## Sheet1
Reference | Section | Parameters | Value
RM17JC00MW | Main | range of product | Zelio Control
RM17JC00MW | Main | product or component type | Modular measurement and control relays
RM17JC00MW | Main | relay type | Current control relay
RM17JC00MW | Main | relay name | RM17JC
RM17JC00MW | Main | relay monitored parameters | Overcurrent detection
RM17JC00MW | Main | time delay | Without
RM17JC00MW | Main | switching capacity in VA | 1250 VA
RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC
RM17JC00MW | Main | maximum power consumption in VA | 3 VA
RM17JC00MW | Main | measurement range | 2...20 A current
RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC
RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM17JC00MW | Complementary | maximum power consumption in W | 1 W
RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal
RM17JC00MW | Complementary | output contacts | 1 C/O
RM17JC00MW | Complementary | nominal output current | 5 A
RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting
RM17JC00MW | Complementary | delay at power up | 0.5 s
RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault)
RM17JC00MW | Complementary | polarity | Yes DC
RM17JC00MW | Complementary | threshold setting | 10...100 %
RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C ¦ 300000 mA non repetitive < 3 s at 25 °C
RM17JC00MW | Complementary | marking | CE : 73/23/EEC ¦ CE : EMC 89/336/EEC
RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17JC00MW | Complementary | insulation | Between supply and measurement
RM17JC00MW | Complementary | operating position | Any position without derating
RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17JC00MW | Complementary | housing material | Self-extinguishing plastic
RM17JC00MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17JC00MW | Complementary | electrical durability | 100000 cycles
RM17JC00MW | Complementary | mechanical durability | 30000000 cycles
RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load
RM17JC00MW | Complementary | contacts material | Cadmium free
RM17JC00MW | Complementary | width | 17.5 mm
RM17JC00MW | Complementary | net weight | 0.13 kg
RM17JC00MW | Environment | immunity to microbreaks | 10 ms
RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17JC00MW | Environment | standards | EN/IEC 60255-6
RM17JC00MW | Environment | product certifications | GL ¦ C-Tick ¦ GOST ¦ UL ¦ CSA
RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C
RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C
RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
RM17JC00MW | Environment | non-dissipating shock wave | 4 kV
RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17JC00MW | Offer Sustainability | Mercury free | Yes
RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes
RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information
RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17JC00MW | Contractual warranty | Warranty | 18 months
RM17TA00 | Main | range of product | Zelio Control
RM17TA00 | Main | product or component type | Modular measurement and control relays
RM17TA00 | Main | relay type | Multifunction control relay
RM17TA00 | Main | product specific application | For 3-phase supply
RM17TA00 | Main | relay name | RM17TA
RM17TA00 | Main | relay monitored parameters | Asymmetry ¦ Phase sequence ¦ Phase failure detection
RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM17TA00 | Main | switching capacity in VA | 1250 VA
RM17TA00 | Main | measurement range | 208...480 V voltage AC
RM17TA00 | Complementary | reset time | 1500 ms time delay
RM17TA00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TA00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TA00 | Complementary | supply voltage limits | 183…528 V AC
RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TA00 | Complementary | output contacts | 1 C/O
RM17TA00 | Complementary | nominal output current | 5 A
RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TA00 | Complementary | hysteresis | 2 %
RM17TA00 | Complementary | delay at power up | 650 ms
RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC ¦ 2...20 % of Un selected ¦ -2...-17 % in the range 220 V AC ¦ -2...-12 % in the range 208 V AC
RM17TA00 | Complementary | voltage range | 208...480 V phase to phase
RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TA00 | Complementary | marking | CE
RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TA00 | Complementary | operating position | Any position without derating
RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TA00 | Complementary | housing material | Self-extinguishing plastic
RM17TA00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TA00 | Complementary | electrical durability | 100000 cycles
RM17TA00 | Complementary | mechanical durability | 30000000 cycles
RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TA00 | Complementary | width | 17.5 mm
RM17TA00 | Complementary | net weight | 0.13 kg
RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TA00 | Environment | standards | EN/IEC 60255-1
RM17TA00 | Environment | product certifications | GOST ¦ CSA ¦ GL ¦ C-Tick ¦ UL
RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TA00 | Offer Sustainability | Mercury free | Yes
RM17TA00 | Offer Sustainability | RoHS exemption information | Yes
RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TA00 | Contractual warranty | Warranty | 18 months
RM17TE00 | Main | range of product | Zelio Control
RM17TE00 | Main | product or component type | Modular measurement and control relays
RM17TE00 | Main | relay type | Multifunction control relay
RM17TE00 | Main | product specific application | For 3-phase supply
RM17TE00 | Main | relay name | RM17TE
RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Asymmetry ¦ Phase sequence ¦ Phase failure detection
RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM17TE00 | Main | switching capacity in VA | 1250 VA
RM17TE00 | Main | measurement range | 208...480 V voltage AC
RM17TE00 | Complementary | reset time | 1500 ms time delay
RM17TE00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TE00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TE00 | Complementary | supply voltage limits | 183…528 V AC
RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TE00 | Complementary | output contacts | 1 C/O
RM17TE00 | Complementary | nominal output current | 5 A
RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TE00 | Complementary | hysteresis | 2 %
RM17TE00 | Complementary | delay at power up | 650 ms
RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC ¦ +2...+17 % in the range 480 V AC ¦ -2...-12 % in the range 208 V AC ¦ 2...20 % of Un selected
RM17TE00 | Complementary | voltage range | 208...480 V phase to phase
RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TE00 | Complementary | marking | CE
RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TE00 | Complementary | operating position | Any position without derating
RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TE00 | Complementary | housing material | Self-extinguishing plastic
RM17TE00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TE00 | Complementary | electrical durability | 100000 cycles
RM17TE00 | Complementary | mechanical durability | 30000000 cycles
RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TE00 | Complementary | width | 17.5 mm
RM17TE00 | Complementary | net weight | 0.13 kg
RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TE00 | Environment | standards | EN/IEC 60255-1
RM17TE00 | Environment | product certifications | GOST ¦ C-Tick ¦ CSA ¦ UL ¦ GL
RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TE00 | Offer Sustainability | Mercury free | Yes
RM17TE00 | Offer Sustainability | RoHS exemption information | Yes
RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TE00 | Contractual warranty | Warranty | 18 months
RM17TG00 | Main | range of product | Zelio Control
RM17TG00 | Main | product or component type | Modular measurement and control relays
RM17TG00 | Main | relay type | Control relay
RM17TG00 | Main | product specific application | For 3-phase supply
RM17TG00 | Main | relay name | RM17TG
RM17TG00 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection (2 or more phase cut)
RM17TG00 | Main | time delay | Without
RM17TG00 | Main | switching capacity in VA | 1250 VA
RM17TG00 | Main | measurement range | 208...480 V voltage AC
RM17TG00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TG00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TG00 | Complementary | supply voltage limits | 183…528 V AC
RM17TG00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TG00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TG00 | Complementary | voltage detection threshold | < 100 V AC
RM17TG00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TG00 | Complementary | output contacts | 1 C/O
RM17TG00 | Complementary | nominal output current | 5 A
RM17TG00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TG00 | Complementary | delay at power up | 650 ms
RM17TG00 | Complementary | voltage range | 183...528 V
RM17TG00 | Complementary | response time | <= 130 ms (in the event of a fault)
RM17TG00 | Complementary | marking | CE
RM17TG00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TG00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TG00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TG00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TG00 | Complementary | operating position | Any position without derating
RM17TG00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TG00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TG00 | Complementary | housing material | Self-extinguishing plastic
RM17TG00 | Complementary | local signalling | LED (yellow) for relay ON
RM17TG00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TG00 | Complementary | electrical durability | 100000 cycles
RM17TG00 | Complementary | mechanical durability | 30000000 cycles
RM17TG00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TG00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TG00 | Complementary | safety reliability data | MTTFd = 924.6 years ¦ B10d = 850000
RM17TG00 | Complementary | width | 17.5 mm
RM17TG00 | Complementary | net weight | 0.13 kg
RM17TG00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TG00 | Environment | standards | EN/IEC 60255-1
RM17TG00 | Environment | product certifications | C-Tick ¦ GL ¦ CSA ¦ UL ¦ GOST
RM17TG00 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TG00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TG00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TG00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TG00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TG00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TG00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TG00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TG00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM17TG00 | Environment | non-dissipating shock wave | 4 kV
RM17TG00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TG00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TG00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TG00 | Offer Sustainability | Mercury free | Yes
RM17TG00 | Offer Sustainability | RoHS exemption information | Yes
RM17TG00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TG00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TG00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TG00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TG00 | Contractual warranty | Warranty | 18 months
RM17TG20 | Main | range of product | Zelio Control
RM17TG20 | Main | product or component type | Modular measurement and control relays
RM17TG20 | Main | relay type | Control relay
RM17TG20 | Main | product specific application | For 3-phase supply
RM17TG20 | Main | relay name | RM17TG
RM17TG20 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection (2 or more phase cut)
RM17TG20 | Main | time delay | Without
RM17TG20 | Main | switching capacity in VA | 1250 VA
RM17TG20 | Main | measurement range | 208...480 V voltage AC
RM17TG20 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TG20 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TG20 | Complementary | supply voltage limits | 183…484 V AC
RM17TG20 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TG20 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TG20 | Complementary | voltage detection threshold | < 100 V AC
RM17TG20 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TG20 | Complementary | output contacts | 2 C/O
RM17TG20 | Complementary | nominal output current | 5 A
RM17TG20 | Complementary | measurement voltage limits | 183…528 V AC
RM17TG20 | Complementary | delay at power up | 650 ms
RM17TG20 | Complementary | voltage range | 183...484 V
RM17TG20 | Complementary | response time | <= 130 ms (in the event of a fault)
RM17TG20 | Complementary | marking | CE
RM17TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TG20 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TG20 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TG20 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TG20 | Complementary | operating position | Any position without derating
RM17TG20 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TG20 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TG20 | Complementary | housing material | Self-extinguishing plastic
RM17TG20 | Complementary | local signalling | LED (yellow) for relay ON
RM17TG20 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TG20 | Complementary | electrical durability | 10000 cycles
RM17TG20 | Complementary | mechanical durability | 30000000 cycles
RM17TG20 | Complementary | operating rate | <= 360 operations/hour full load
RM17TG20 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TG20 | Complementary | safety reliability data | B10d = 850000 ¦ MTTFd = 924.6 years
RM17TG20 | Complementary | width | 17.5 mm
RM17TG20 | Complementary | net weight | 0.13 kg
RM17TG20 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TG20 | Environment | standards | EN/IEC 60255-1
RM17TG20 | Environment | product certifications | GOST ¦ C-Tick ¦ UL ¦ CSA ¦ GL
RM17TG20 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TG20 | Environment | ambient air temperature for storage | -40…70 °C
RM17TG20 | Environment | ambient air temperature for operation | -20…50 °C
RM17TG20 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TG20 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TG20 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TG20 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM17TG20 | Environment | non-dissipating shock wave | 4 kV
RM17TG20 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TG20 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TG20 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TG20 | Offer Sustainability | Mercury free | Yes
RM17TG20 | Offer Sustainability | RoHS exemption information | Yes
RM17TG20 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TG20 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TG20 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TG20 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TG20 | Contractual warranty | Warranty | 18 months
RM17TT00 | Main | range of product | Zelio Control
RM17TT00 | Main | product or component type | Modular measurement and control relays
RM17TT00 | Main | relay type | Multifunction control relay
RM17TT00 | Main | product specific application | For 3-phase supply
RM17TT00 | Main | relay name | RM17TT
RM17TT00 | Main | relay monitored parameters | Phase failure detection ¦ Phase sequence
RM17TT00 | Main | time delay | Without
RM17TT00 | Main | switching capacity in VA | 1250 VA
RM17TT00 | Main | measurement range | 208...480 V voltage AC
RM17TT00 | Complementary | reset time | 1500 ms time delay
RM17TT00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TT00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TT00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TT00 | Complementary | supply voltage limits | 183…528 V AC
RM17TT00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TT00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TT00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TT00 | Complementary | output contacts | 1 C/O
RM17TT00 | Complementary | nominal output current | 5 A
RM17TT00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TT00 | Complementary | hysteresis | 2 %
RM17TT00 | Complementary | delay at power up | 650 ms
RM17TT00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TT00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC ¦ 2...20 % of Un selected ¦ +2...+17 % in the range 480 V AC ¦ -2...-12 % in the range 208 V AC
RM17TT00 | Complementary | voltage range | 208...480 V phase to phase
RM17TT00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TT00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TT00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TT00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TT00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TT00 | Complementary | marking | CE
RM17TT00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TT00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TT00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TT00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TT00 | Complementary | operating position | Any position without derating
RM17TT00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TT00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TT00 | Complementary | housing material | Self-extinguishing plastic
RM17TT00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TT00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TT00 | Complementary | electrical durability | 100000 cycles
RM17TT00 | Complementary | mechanical durability | 30000000 cycles
RM17TT00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TT00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TT00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TT00 | Complementary | width | 17.5 mm
RM17TT00 | Complementary | net weight | 0.13 kg
RM17TT00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TT00 | Environment | standards | EN/IEC 60255-1
RM17TT00 | Environment | product certifications | UL ¦ GL ¦ C-Tick ¦ GOST ¦ CSA
RM17TT00 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TT00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TT00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TT00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TT00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TT00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TT00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TT00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TT00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TT00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TT00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TT00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TT00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TT00 | Offer Sustainability | Mercury free | Yes
RM17TT00 | Offer Sustainability | RoHS exemption information | Yes
RM17TT00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TT00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TT00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TT00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TT00 | Contractual warranty | Warranty | 18 months
RM17TU00 | Main | range of product | Zelio Control
RM17TU00 | Main | product or component type | Modular measurement and control relays
RM17TU00 | Main | relay type | Multifunction control relay
RM17TU00 | Main | product specific application | For 3-phase supply
RM17TU00 | Main | relay name | RM17TU
RM17TU00 | Main | relay monitored parameters | Undervoltage detection ¦ Phase sequence ¦ Phase failure detection
RM17TU00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM17TU00 | Main | switching capacity in VA | 1250 VA
RM17TU00 | Main | measurement range | 208...480 V voltage AC
RM17TU00 | Complementary | reset time | 1500 ms time delay
RM17TU00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TU00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TU00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TU00 | Complementary | supply voltage limits | 183…528 V AC
RM17TU00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TU00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TU00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TU00 | Complementary | output contacts | 1 C/O
RM17TU00 | Complementary | nominal output current | 5 A
RM17TU00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TU00 | Complementary | hysteresis | 2 %
RM17TU00 | Complementary | delay at power up | 650 ms
RM17TU00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TU00 | Complementary | threshold adjustment voltage | -2...-12 % in the range 208 V AC ¦ -2...-17 % in the range 220 V AC ¦ 2...20 % of Un selected ¦ +2...+17 % in the range 480 V AC
RM17TU00 | Complementary | voltage range | 208...480 V phase to phase
RM17TU00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TU00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TU00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TU00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TU00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TU00 | Complementary | marking | CE
RM17TU00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TU00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TU00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TU00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TU00 | Complementary | operating position | Any position without derating
RM17TU00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TU00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TU00 | Complementary | housing material | Self-extinguishing plastic
RM17TU00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TU00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TU00 | Complementary | electrical durability | 100000 cycles
RM17TU00 | Complementary | mechanical durability | 30000000 cycles
RM17TU00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TU00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TU00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TU00 | Complementary | width | 17.5 mm
RM17TU00 | Complementary | net weight | 0.13 kg
RM17TU00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TU00 | Environment | standards | EN/IEC 60255-1
RM17TU00 | Environment | product certifications | GL ¦ GOST ¦ UL ¦ C-Tick ¦ CSA
RM17TU00 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TU00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TU00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TU00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TU00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TU00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TU00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TU00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TU00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TU00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TU00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TU00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TU00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TU00 | Offer Sustainability | Mercury free | Yes
RM17TU00 | Offer Sustainability | RoHS exemption information | Yes
RM17TU00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TU00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TU00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TU00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TU00 | Contractual warranty | Warranty | 18 months
RM17UAS14 | Main | range of product | Zelio Control
RM17UAS14 | Main | product or component type | Modular measurement and control relays
RM17UAS14 | Main | relay type | Voltage control relay
RM17UAS14 | Main | product specific application | For single-phase and DC supply
RM17UAS14 | Main | relay name | RM17UAS
RM17UAS14 | Main | relay monitored parameters | Overvoltage or undervoltage detection ¦ Self-powered
RM17UAS14 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
RM17UAS14 | Main | switching capacity in VA | 1250 VA
RM17UAS14 | Main | minimum switching current | 10 mA at 5 V DC
RM17UAS14 | Main | maximum switching current | 5 A AC/DC
RM17UAS14 | Main | measurement range | 9...15 V voltage DC
RM17UAS14 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UAS14 | Complementary | reset time | 1500 ms time delay
RM17UAS14 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UAS14 | Complementary | [Us] rated supply voltage | 12 V DC +/- 10 %
RM17UAS14 | Complementary | supply voltage limits | 7…20 V DC
RM17UAS14 | Complementary | maximum power consumption in W | 1 W DC
RM17UAS14 | Complementary | immunity to microbreaks | 20 ms at 12 V
RM17UAS14 | Complementary | output contacts | 1 C/O
RM17UAS14 | Complementary | nominal output current | 5 A
RM17UAS14 | Complementary | hysteresis | 5…20 % of threshold setting
RM17UAS14 | Complementary | delay at power up | 1000 ms DC
RM17UAS14 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UAS14 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UAS14 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM17UAS14 | Complementary | polarity | Non reversible polarity on DC supply
RM17UAS14 | Complementary | quality labels | CE
RM17UAS14 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UAS14 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UAS14 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 400 V conforming to IEC 60664-1
RM17UAS14 | Complementary | operating position | Any position without derating
RM17UAS14 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UAS14 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UAS14 | Complementary | housing material | Self-extinguishing plastic
RM17UAS14 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UAS14 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UAS14 | Complementary | electrical durability | 100000 cycles
RM17UAS14 | Complementary | mechanical durability | 30000000 cycles
RM17UAS14 | Complementary | operating rate | <= 360 operations/hour full load
RM17UAS14 | Complementary | width | 17.5 mm
RM17UAS14 | Complementary | net weight | 0.08 kg
RM17UAS14 | Complementary | compatibility code | RM17
RM17UAS14 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UAS14 | Environment | standards | EN/IEC 60255-6
RM17UAS14 | Environment | product certifications | CSA ¦ C-Tick ¦ GL ¦ UL ¦ GOST
RM17UAS14 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17UAS14 | Environment | ambient air temperature for storage | -40…70 °C
RM17UAS14 | Environment | ambient air temperature for operation | -20…50 °C
RM17UAS14 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UAS14 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UAS14 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UAS14 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UAS14 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UAS14 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17UAS14 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17UAS14 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UAS14 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UAS14 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UAS14 | Offer Sustainability | Mercury free | Yes
RM17UAS14 | Offer Sustainability | RoHS exemption information | Yes
RM17UAS14 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UAS14 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UAS14 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UAS14 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UAS14 | Contractual warranty | Warranty | 18 months
RM17UAS15 | Main | range of product | Zelio Control
RM17UAS15 | Main | product or component type | Modular measurement and control relays
RM17UAS15 | Main | relay type | Voltage control relay
RM17UAS15 | Main | product specific application | For single-phase and DC supply
RM17UAS15 | Main | relay name | RM17UAS
RM17UAS15 | Main | relay monitored parameters | Overvoltage or undervoltage detection ¦ Self-powered
RM17UAS15 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
RM17UAS15 | Main | switching capacity in VA | 1250 VA
RM17UAS15 | Main | minimum switching current | 10 mA at 5 V DC
RM17UAS15 | Main | maximum switching current | 5 A AC/DC
RM17UAS15 | Main | power consumption in VA | 0…3 VA AC
RM17UAS15 | Main | measurement range | 65...260 V voltage AC 50/60 Hz ¦ 65...260 V voltage DC
RM17UAS15 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UAS15 | Complementary | reset time | 1500 ms time delay
RM17UAS15 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UAS15 | Complementary | [Us] rated supply voltage | 110...240 V AC/DC 50/60 Hz +/- 10 %
RM17UAS15 | Complementary | supply voltage limits | 50…270 V AC/DC
RM17UAS15 | Complementary | maximum power consumption in W | 1 W DC
RM17UAS15 | Complementary | immunity to microbreaks | 20 ms
RM17UAS15 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17UAS15 | Complementary | output contacts | 1 C/O
RM17UAS15 | Complementary | nominal output current | 5 A
RM17UAS15 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17UAS15 | Complementary | hysteresis | 5…20 % of threshold setting
RM17UAS15 | Complementary | delay at power up | 1000 ms DC ¦ 500 ms AC
RM17UAS15 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UAS15 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UAS15 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM17UAS15 | Complementary | polarity | Non reversible polarity on DC supply
RM17UAS15 | Complementary | quality labels | CE
RM17UAS15 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UAS15 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UAS15 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 400 V conforming to IEC 60664-1
RM17UAS15 | Complementary | operating position | Any position without derating
RM17UAS15 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UAS15 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UAS15 | Complementary | housing material | Self-extinguishing plastic
RM17UAS15 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UAS15 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UAS15 | Complementary | electrical durability | 100000 cycles
RM17UAS15 | Complementary | mechanical durability | 30000000 cycles
RM17UAS15 | Complementary | operating rate | <= 360 operations/hour full load
RM17UAS15 | Complementary | width | 17.5 mm
RM17UAS15 | Complementary | net weight | 0.08 kg
RM17UAS15 | Complementary | compatibility code | RM17
RM17UAS15 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UAS15 | Environment | standards | EN/IEC 60255-6
RM17UAS15 | Environment | product certifications | GL ¦ UL ¦ GOST ¦ CSA ¦ C-Tick
RM17UAS15 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17UAS15 | Environment | ambient air temperature for storage | -40…70 °C
RM17UAS15 | Environment | ambient air temperature for operation | -20…50 °C
RM17UAS15 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UAS15 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UAS15 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UAS15 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UAS15 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UAS15 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17UAS15 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17UAS15 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UAS15 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UAS15 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UAS15 | Offer Sustainability | Mercury free | Yes
RM17UAS15 | Offer Sustainability | RoHS exemption information | Yes
RM17UAS15 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UAS15 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UAS15 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UAS15 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UAS15 | Contractual warranty | Warranty | 18 months
RM17UAS16 | Main | range of product | Zelio Control
RM17UAS16 | Main | product or component type | Modular measurement and control relays
RM17UAS16 | Main | relay type | Voltage control relay
RM17UAS16 | Main | product specific application | For single-phase and DC supply
RM17UAS16 | Main | relay name | RM17UAS
RM17UAS16 | Main | relay monitored parameters | Overvoltage or undervoltage detection ¦ Self-powered
RM17UAS16 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
RM17UAS16 | Main | switching capacity in VA | 1250 VA
RM17UAS16 | Main | minimum switching current | 10 mA at 5 V DC
RM17UAS16 | Main | maximum switching current | 5 A AC/DC
RM17UAS16 | Main | power consumption in VA | 0…3.9 VA AC
RM17UAS16 | Main | measurement range | 20...80 V voltage AC 50/60 Hz ¦ 20...80 V voltage DC
RM17UAS16 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UAS16 | Complementary | reset time | 1500 ms time delay
RM17UAS16 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UAS16 | Complementary | [Us] rated supply voltage | 24...48 V AC/DC 50/60 Hz +/- 10 %
RM17UAS16 | Complementary | supply voltage limits | 15…100 V AC/DC
RM17UAS16 | Complementary | maximum power consumption in W | 1.6 W DC
RM17UAS16 | Complementary | immunity to microbreaks | 20 ms
RM17UAS16 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17UAS16 | Complementary | output contacts | 1 C/O
RM17UAS16 | Complementary | nominal output current | 5 A
RM17UAS16 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17UAS16 | Complementary | hysteresis | 5…20 % of threshold setting
RM17UAS16 | Complementary | delay at power up | 1000 ms DC ¦ 500 ms AC
RM17UAS16 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UAS16 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UAS16 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM17UAS16 | Complementary | polarity | Non reversible polarity on DC supply
RM17UAS16 | Complementary | quality labels | CE
RM17UAS16 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UAS16 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UAS16 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 400 V conforming to IEC 60664-1
RM17UAS16 | Complementary | operating position | Any position without derating
RM17UAS16 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UAS16 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UAS16 | Complementary | housing material | Self-extinguishing plastic
RM17UAS16 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UAS16 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UAS16 | Complementary | electrical durability | 100000 cycles
RM17UAS16 | Complementary | mechanical durability | 30000000 cycles
RM17UAS16 | Complementary | operating rate | <= 360 operations/hour full load
RM17UAS16 | Complementary | width | 17.5 mm
RM17UAS16 | Complementary | net weight | 0.08 kg
RM17UAS16 | Complementary | compatibility code | RM17
RM17UAS16 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UAS16 | Environment | standards | EN/IEC 60255-6
RM17UAS16 | Environment | product certifications | CSA ¦ GL ¦ UL ¦ GOST ¦ C-Tick
RM17UAS16 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17UAS16 | Environment | ambient air temperature for storage | -40…70 °C
RM17UAS16 | Environment | ambient air temperature for operation | -20…50 °C
RM17UAS16 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UAS16 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UAS16 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UAS16 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UAS16 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UAS16 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17UAS16 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17UAS16 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UAS16 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UAS16 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UAS16 | Offer Sustainability | Mercury free | Yes
RM17UAS16 | Offer Sustainability | RoHS exemption information | Yes
RM17UAS16 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UAS16 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UAS16 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UAS16 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UAS16 | Contractual warranty | Warranty | 18 months
RM17UB310 | Main | range of product | Zelio Control
RM17UB310 | Main | product or component type | Modular measurement and control relays
RM17UB310 | Main | relay type | Voltage control relay
RM17UB310 | Main | product specific application | For 3-phase supply
RM17UB310 | Main | relay name | RM17UB3
RM17UB310 | Main | relay monitored parameters | Overvoltage and undervoltage between phases
RM17UB310 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM17UB310 | Main | switching capacity in VA | 1250 VA
RM17UB310 | Main | minimum switching current | 10 mA at 5 V DC
RM17UB310 | Main | maximum switching current | 5 A AC/DC
RM17UB310 | Main | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17UB310 | Main | measurement range | 183...528 V voltage AC
RM17UB310 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UB310 | Complementary | reset time | 1500 ms time delay
RM17UB310 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UB310 | Complementary | [Us] rated supply voltage | 208...480 V AC 50/60 Hz +/- 10 %
RM17UB310 | Complementary | supply voltage limits | 183…528 V AC
RM17UB310 | Complementary | voltage detection threshold | 183 V
RM17UB310 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17UB310 | Complementary | output contacts | 1 C/O
RM17UB310 | Complementary | nominal output current | 5 A
RM17UB310 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17UB310 | Complementary | hysteresis | 2 %
RM17UB310 | Complementary | delay at power up | 650 ms
RM17UB310 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UB310 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UB310 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM17UB310 | Complementary | response time | < 200 ms (in the event of a fault)
RM17UB310 | Complementary | quality labels | CE
RM17UB310 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UB310 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UB310 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17UB310 | Complementary | operating position | Any position without derating
RM17UB310 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UB310 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UB310 | Complementary | housing material | Self-extinguishing plastic
RM17UB310 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UB310 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UB310 | Complementary | electrical durability | 100000 cycles
RM17UB310 | Complementary | mechanical durability | 30000000 cycles
RM17UB310 | Complementary | operating rate | <= 360 operations/hour full load
RM17UB310 | Complementary | safety reliability data | B10d = 470000 ¦ MTTFd = 502.2 years
RM17UB310 | Complementary | width | 17.5 mm
RM17UB310 | Complementary | net weight | 0.08 kg
RM17UB310 | Complementary | functionality | Overvoltage and undervoltage detection
RM17UB310 | Complementary | compatibility code | RM17
RM17UB310 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UB310 | Environment | standards | EN/IEC 60255-1
RM17UB310 | Environment | product certifications | GOST ¦ UL ¦ GL ¦ C-Tick ¦ CSA
RM17UB310 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17UB310 | Environment | ambient air temperature for storage | -40…70 °C
RM17UB310 | Environment | ambient air temperature for operation | -20…50 °C
RM17UB310 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UB310 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UB310 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UB310 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UB310 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UB310 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM17UB310 | Environment | non-dissipating shock wave | 4 kV
RM17UB310 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UB310 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UB310 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UB310 | Offer Sustainability | Mercury free | Yes
RM17UB310 | Offer Sustainability | RoHS exemption information | Yes
RM17UB310 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UB310 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UB310 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UB310 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UB310 | Contractual warranty | Warranty | 18 months
RM17UBE15 | Main | range of product | Zelio Control
RM17UBE15 | Main | product or component type | Modular measurement and control relays
RM17UBE15 | Main | relay type | Voltage control relay
RM17UBE15 | Main | product specific application | For single-phase and DC supply
RM17UBE15 | Main | relay name | RM17UBE
RM17UBE15 | Main | relay monitored parameters | Self-powered ¦ Overvoltage and undervoltage detection
RM17UBE15 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
RM17UBE15 | Main | switching capacity in VA | 1250 VA
RM17UBE15 | Main | minimum switching current | 10 mA at 5 V DC
RM17UBE15 | Main | maximum switching current | 5 A AC/DC
RM17UBE15 | Main | power consumption in VA | 0…3 VA AC
RM17UBE15 | Main | measurement range | 65...260 V voltage AC/DC
RM17UBE15 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UBE15 | Complementary | reset time | 1500 ms time delay
RM17UBE15 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UBE15 | Complementary | [Us] rated supply voltage | 110...240 V AC/DC 50/60 Hz +/- 10 %
RM17UBE15 | Complementary | supply voltage limits | 50…270 V AC/DC
RM17UBE15 | Complementary | maximum power consumption in W | 1 W DC
RM17UBE15 | Complementary | immunity to microbreaks | 20 ms
RM17UBE15 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17UBE15 | Complementary | output contacts | 1 C/O
RM17UBE15 | Complementary | nominal output current | 5 A
RM17UBE15 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17UBE15 | Complementary | hysteresis | 3 % fixed of threshold setting
RM17UBE15 | Complementary | delay at power up | 1000 ms DC ¦ 500 ms AC
RM17UBE15 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UBE15 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UBE15 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM17UBE15 | Complementary | polarity | Non reversible polarity on DC supply
RM17UBE15 | Complementary | quality labels | CE
RM17UBE15 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UBE15 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UBE15 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 400 V conforming to IEC 60664-1
RM17UBE15 | Complementary | operating position | Any position without derating
RM17UBE15 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UBE15 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UBE15 | Complementary | housing material | Self-extinguishing plastic
RM17UBE15 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UBE15 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UBE15 | Complementary | electrical durability | 100000 cycles
RM17UBE15 | Complementary | mechanical durability | 30000000 cycles
RM17UBE15 | Complementary | operating rate | <= 360 operations/hour full load
RM17UBE15 | Complementary | safety reliability data | B10d = 470000 ¦ MTTFd = 502.2 years
RM17UBE15 | Complementary | width | 17.5 mm
RM17UBE15 | Complementary | net weight | 0.08 kg
RM17UBE15 | Complementary | functionality | Overvoltage and undervoltage detection
RM17UBE15 | Complementary | compatibility code | RM17
RM17UBE15 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UBE15 | Environment | standards | EN/IEC 60255-6
RM17UBE15 | Environment | product certifications | UL ¦ GL ¦ GOST ¦ C-Tick ¦ CSA
RM17UBE15 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17UBE15 | Environment | ambient air temperature for storage | -40…70 °C
RM17UBE15 | Environment | ambient air temperature for operation | -20…50 °C
RM17UBE15 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UBE15 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UBE15 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UBE15 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UBE15 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UBE15 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17UBE15 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17UBE15 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UBE15 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UBE15 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UBE15 | Offer Sustainability | Mercury free | Yes
RM17UBE15 | Offer Sustainability | RoHS exemption information | Yes
RM17UBE15 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UBE15 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UBE15 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UBE15 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UBE15 | Contractual warranty | Warranty | 18 months
RM17UBE16 | Main | range of product | Zelio Control
RM17UBE16 | Main | product or component type | Modular measurement and control relays
RM17UBE16 | Main | relay type | Voltage control relay
RM17UBE16 | Main | product specific application | For single-phase and DC supply
RM17UBE16 | Main | relay name | RM17UBE
RM17UBE16 | Main | relay monitored parameters | Self-powered ¦ Overvoltage and undervoltage detection
RM17UBE16 | Main | time delay | Adjustable 0.1...10 s, 0 + 10 % on crossing the threshold
RM17UBE16 | Main | switching capacity in VA | 1250 VA
RM17UBE16 | Main | minimum switching current | 10 mA at 5 V DC
RM17UBE16 | Main | maximum switching current | 5 A AC/DC
RM17UBE16 | Main | power consumption in VA | 0…3.9 VA AC
RM17UBE16 | Main | measurement range | 20...80 V voltage AC 50/60 Hz ¦ 20...80 V voltage DC
RM17UBE16 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17UBE16 | Complementary | reset time | 1500 ms time delay
RM17UBE16 | Complementary | maximum switching voltage | 250 V AC/DC
RM17UBE16 | Complementary | [Us] rated supply voltage | 24...48 V AC/DC 50/60 Hz +/- 10 %
RM17UBE16 | Complementary | supply voltage limits | 15…100 V AC/DC
RM17UBE16 | Complementary | maximum power consumption in W | 1.6 W DC
RM17UBE16 | Complementary | immunity to microbreaks | 20 ms
RM17UBE16 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17UBE16 | Complementary | output contacts | 1 C/O
RM17UBE16 | Complementary | nominal output current | 5 A
RM17UBE16 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17UBE16 | Complementary | hysteresis | 3 % fixed of threshold setting
RM17UBE16 | Complementary | delay at power up | 1000 ms DC ¦ 500 ms AC
RM17UBE16 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17UBE16 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM17UBE16 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM17UBE16 | Complementary | polarity | Non reversible polarity on DC supply
RM17UBE16 | Complementary | quality labels | CE
RM17UBE16 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17UBE16 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17UBE16 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 400 V conforming to IEC 60664-1
RM17UBE16 | Complementary | operating position | Any position without derating
RM17UBE16 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17UBE16 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17UBE16 | Complementary | housing material | Self-extinguishing plastic
RM17UBE16 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17UBE16 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17UBE16 | Complementary | electrical durability | 100000 cycles
RM17UBE16 | Complementary | mechanical durability | 30000000 cycles
RM17UBE16 | Complementary | operating rate | <= 360 operations/hour full load
RM17UBE16 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17UBE16 | Complementary | width | 17.5 mm
RM17UBE16 | Complementary | net weight | 0.08 kg
RM17UBE16 | Complementary | functionality | Overvoltage and undervoltage detection
RM17UBE16 | Complementary | compatibility code | RM17
RM17UBE16 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17UBE16 | Environment | standards | EN/IEC 60255-6
RM17UBE16 | Environment | product certifications | C-Tick ¦ GOST ¦ GL ¦ CSA ¦ UL
RM17UBE16 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17UBE16 | Environment | ambient air temperature for storage | -40…70 °C
RM17UBE16 | Environment | ambient air temperature for operation | -20…50 °C
RM17UBE16 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17UBE16 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17UBE16 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM17UBE16 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17UBE16 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17UBE16 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17UBE16 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17UBE16 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17UBE16 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17UBE16 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17UBE16 | Offer Sustainability | Mercury free | Yes
RM17UBE16 | Offer Sustainability | RoHS exemption information | Yes
RM17UBE16 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17UBE16 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17UBE16 | Offer Sustainability | Circularity Profile | End of Life Information
RM17UBE16 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17UBE16 | Contractual warranty | Warranty | 18 months
RM35ATL0MW | Main | range of product | Zelio Control
RM35ATL0MW | Main | product or component type | Modular measurement and control relays
RM35ATL0MW | Main | relay type | Temperature control relays
RM35ATL0MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
RM35ATL0MW | Main | relay name | RM35AT
RM35ATL0MW | Main | relay monitored parameters | Undertemperature: -1...11°C ¦ Overtemperature: 34...46°C
RM35ATL0MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
RM35ATL0MW | Main | switching capacity in VA | 1250 VA
RM35ATL0MW | Main | minimum switching current | 10 mA at 5 V DC
RM35ATL0MW | Main | maximum power consumption in VA | 3.5 VA AC
RM35ATL0MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35ATL0MW | Complementary | reset time | 8 s
RM35ATL0MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35ATL0MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATL0MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATL0MW | Complementary | supply voltage limits | 20.4…264 V AC ¦ 21.6…264 V DC
RM35ATL0MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35ATL0MW | Complementary | resistance across terminals | 1.33 kOhm at temperature
RM35ATL0MW | Complementary | width | 35 mm
RM35ATL0MW | Complementary | output contacts | 1 C/O
RM35ATL0MW | Complementary | contacts material | Cadmium free
RM35ATL0MW | Complementary | nominal output current | 5 A
RM35ATL0MW | Complementary | delay at power up | 0.2 s
RM35ATL0MW | Complementary | measurement accuracy | +/- 2 °C
RM35ATL0MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) ¦ <= 3.5 s (on disappearance of fault)
RM35ATL0MW | Complementary | temperature probe type | Pt 100 - 3-wire
RM35ATL0MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
RM35ATL0MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35ATL0MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35ATL0MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35ATL0MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35ATL0MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC ¦ - 15 % + 10 % Un AC
RM35ATL0MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35ATL0MW | Complementary | insulation | Galvanic insulation between supply and measurement
RM35ATL0MW | Complementary | operating position | Any position without derating
RM35ATL0MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35ATL0MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35ATL0MW | Complementary | housing material | Self-extinguishing plastic
RM35ATL0MW | Complementary | local signalling | 1 LED green for power ON ¦ 1 LED yellow for correct temperature (high R1) ¦ 1 LED yellow for correct temperature (low R2)
RM35ATL0MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35ATL0MW | Complementary | electrical durability | 100000 cycles
RM35ATL0MW | Complementary | mechanical durability | 30000000 cycles
RM35ATL0MW | Complementary | operating rate | <= 360 operations/hour full load
RM35ATL0MW | Environment | immunity to microbreaks | 10 ms
RM35ATL0MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35ATL0MW | Environment | standards | IEC 60255-6 ¦ NF EN 60255-6
RM35ATL0MW | Environment | product certifications | GOST ¦ GL ¦ C-Tick ¦ UL ¦ CSA
RM35ATL0MW | Environment | ambient air temperature for storage | -40…70 °C
RM35ATL0MW | Environment | ambient air temperature for operation | -20…50 °C
RM35ATL0MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35ATL0MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35ATL0MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35ATL0MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35ATL0MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35ATL0MW | Environment | non-dissipating shock wave | 4 kV
RM35ATL0MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35ATL0MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35ATL0MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35ATL0MW | Offer Sustainability | Mercury free | Yes
RM35ATL0MW | Offer Sustainability | RoHS exemption information | Yes
RM35ATL0MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35ATL0MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35ATL0MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35ATL0MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35ATL0MW | Contractual warranty | Warranty | 18 months
RM35ATR5MW | Main | range of product | Zelio Control
RM35ATR5MW | Main | product or component type | Modular measurement and control relays
RM35ATR5MW | Main | relay type | Temperature control relays
RM35ATR5MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
RM35ATR5MW | Main | relay name | RM35AT
RM35ATR5MW | Main | relay monitored parameters | Overtemperature: 34...46°C ¦ Undertemperature: -1...11°C
RM35ATR5MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
RM35ATR5MW | Main | switching capacity in VA | 1250 VA
RM35ATR5MW | Main | minimum switching current | 10 mA at 5 V DC
RM35ATR5MW | Main | maximum power consumption in VA | 3.5 VA AC
RM35ATR5MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35ATR5MW | Complementary | reset time | 8 s
RM35ATR5MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35ATR5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATR5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATR5MW | Complementary | supply voltage limits | 20.4…264 V AC ¦ 21.6…264 V DC
RM35ATR5MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35ATR5MW | Complementary | resistance across terminals | 1.33 kOhm at temperature
RM35ATR5MW | Complementary | width | 35 mm
RM35ATR5MW | Complementary | output contacts | 2 NO
RM35ATR5MW | Complementary | contacts material | Cadmium free
RM35ATR5MW | Complementary | nominal output current | 5 A
RM35ATR5MW | Complementary | delay at power up | 0.2 s
RM35ATR5MW | Complementary | measurement accuracy | +/- 2 °C
RM35ATR5MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) ¦ <= 3.5 s (on disappearance of fault)
RM35ATR5MW | Complementary | temperature probe type | Pt 100 - 3-wire
RM35ATR5MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
RM35ATR5MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35ATR5MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35ATR5MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35ATR5MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35ATR5MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC ¦ - 15 % + 10 % Un AC
RM35ATR5MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35ATR5MW | Complementary | insulation | Galvanic insulation between supply and measurement
RM35ATR5MW | Complementary | operating position | Any position without derating
RM35ATR5MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35ATR5MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35ATR5MW | Complementary | housing material | Self-extinguishing plastic
RM35ATR5MW | Complementary | local signalling | 1 LED green for power ON ¦ 1 LED yellow for correct temperature (high R1) ¦ 1 LED yellow for correct temperature (low R2)
RM35ATR5MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35ATR5MW | Complementary | electrical durability | 100000 cycles
RM35ATR5MW | Complementary | mechanical durability | 30000000 cycles
RM35ATR5MW | Complementary | operating rate | <= 360 operations/hour full load
RM35ATR5MW | Environment | immunity to microbreaks | 10 ms
RM35ATR5MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35ATR5MW | Environment | standards | IEC 60255-6 ¦ NF EN 60255-6
RM35ATR5MW | Environment | product certifications | GL ¦ GOST ¦ C-Tick ¦ CSA ¦ UL
RM35ATR5MW | Environment | ambient air temperature for storage | -40…70 °C
RM35ATR5MW | Environment | ambient air temperature for operation | -20…50 °C
RM35ATR5MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35ATR5MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35ATR5MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35ATR5MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35ATR5MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35ATR5MW | Environment | non-dissipating shock wave | 4 kV
RM35ATR5MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35ATR5MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35ATR5MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35ATR5MW | Offer Sustainability | Mercury free | Yes
RM35ATR5MW | Offer Sustainability | RoHS exemption information | Yes
RM35ATR5MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35ATR5MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35ATR5MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35ATR5MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35ATR5MW | Contractual warranty | Warranty | 18 months
RM35ATW5MW | Main | range of product | Zelio Control
RM35ATW5MW | Main | product or component type | Modular measurement and control relays
RM35ATW5MW | Main | relay type | Temperature control relays
RM35ATW5MW | Main | product specific application | For elevator machine rooms and 3-phase supplies
RM35ATW5MW | Main | relay name | RM35AT
RM35ATW5MW | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection ¦ Undertemperature: -1...11°C ¦ Overtemperature: 34...46°C
RM35ATW5MW | Main | time delay range | 0.1...10 s adjustable delay (tolerance: 0...10 % of the full scale value)
RM35ATW5MW | Main | switching capacity in VA | 1250 VA
RM35ATW5MW | Main | minimum switching current | 10 mA at 5 V DC
RM35ATW5MW | Main | maximum power consumption in VA | 3.5 VA AC
RM35ATW5MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35ATW5MW | Complementary | reset time | 8 s
RM35ATW5MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35ATW5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATW5MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RM35ATW5MW | Complementary | supply voltage limits | 20.4…264 V AC ¦ 21.6…264 V DC
RM35ATW5MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35ATW5MW | Complementary | resistance across terminals | 600 kOhm at 3-phase ¦ 1.33 kOhm at temperature
RM35ATW5MW | Complementary | width | 35 mm
RM35ATW5MW | Complementary | output contacts | 2 NO
RM35ATW5MW | Complementary | contacts material | Cadmium free
RM35ATW5MW | Complementary | nominal output current | 5 A
RM35ATW5MW | Complementary | delay at power up | 0.2 s
RM35ATW5MW | Complementary | measurement accuracy | +/- 2 °C
RM35ATW5MW | Complementary | response time | <= 3.5 s + Tt (in case of temperature fault) ¦ 500 ms (in case of 3-phase fault) ¦ 500 ms (on disappearance of fault)
RM35ATW5MW | Complementary | temperature probe type | Pt 100 - 3-wire
RM35ATW5MW | Complementary | installed device | Pt 100 probe cable length <= 10 m
RM35ATW5MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35ATW5MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35ATW5MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35ATW5MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35ATW5MW | Complementary | operating voltage tolerance | - 10 % + 10 % Un DC ¦ - 15 % + 10 % Un AC
RM35ATW5MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35ATW5MW | Complementary | operating position | Any position without derating
RM35ATW5MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35ATW5MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35ATW5MW | Complementary | housing material | Self-extinguishing plastic
RM35ATW5MW | Complementary | local signalling | 1 LED green for power ON ¦ 1 LED yellow for correct temperature (high R1)/(low R2) ¦ 1 LED yellow for phases of relay
RM35ATW5MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35ATW5MW | Complementary | electrical durability | 100000 cycles
RM35ATW5MW | Complementary | mechanical durability | 30000000 cycles
RM35ATW5MW | Complementary | operating rate | <= 360 operations/hour full load
RM35ATW5MW | Environment | immunity to microbreaks | 10 ms
RM35ATW5MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35ATW5MW | Environment | standards | NF EN 60255-6 ¦ IEC 60255-6
RM35ATW5MW | Environment | product certifications | GL ¦ UL ¦ C-Tick ¦ CSA ¦ GOST
RM35ATW5MW | Environment | ambient air temperature for storage | -40…70 °C
RM35ATW5MW | Environment | ambient air temperature for operation | -20…50 °C
RM35ATW5MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35ATW5MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35ATW5MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35ATW5MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35ATW5MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35ATW5MW | Environment | non-dissipating shock wave | 4 kV
RM35ATW5MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35ATW5MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35ATW5MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35ATW5MW | Offer Sustainability | Mercury free | Yes
RM35ATW5MW | Offer Sustainability | RoHS exemption information | Yes
RM35ATW5MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35ATW5MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35ATW5MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35ATW5MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35ATW5MW | Contractual warranty | Warranty | 18 months
RM35BA10 | Main | range of product | Zelio Control
RM35BA10 | Main | product or component type | Modular measurement and control relays
RM35BA10 | Main | relay type | Pump control relays
RM35BA10 | Main | product specific application | For 3-phase and single-phase pump
RM35BA10 | Main | relay name | RM35BA
RM35BA10 | Main | relay monitored parameters | Overcurrent and undercurrent control ¦ Phase sequence on 3-phase supply ¦ Phase failure on 3-phase supply
RM35BA10 | Main | time delay type | Adjustable 1...60 s, +/- 10 % Ti on energisation ¦ Fixed 0.3 s reset on terminal Y2 ¦ Adjustable 0.1...10 s, +/- 10 % Tt on crossing the threshold
RM35BA10 | Main | switching capacity in VA | 1250 VA
RM35BA10 | Main | minimum switching current | 10 mA at 5 V DC
RM35BA10 | Main | maximum switching current | 5 A AC/DC
RM35BA10 | Main | maximum power consumption in VA | 5 VA AC
RM35BA10 | Main | measurement range | 1...10 A AC
RM35BA10 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35BA10 | Complementary | reset time | 2000 ms
RM35BA10 | Complementary | maximum switching voltage | 250 V AC/DC
RM35BA10 | Complementary | [Un] rated nominal voltage | 208...480 V AC 3 phases ¦ 230 V AC single phase
RM35BA10 | Complementary | [Un] rated nominal voltage | 208...480 V AC 3 phases ¦ 230 V AC 1 phase
RM35BA10 | Complementary | supply voltage limits | 183…528 V AC
RM35BA10 | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35BA10 | Complementary | resistance across terminals | 0.01 Ohm at E1-L2 terminals
RM35BA10 | Complementary | width | 35 mm
RM35BA10 | Complementary | output contacts | 1 C/O
RM35BA10 | Complementary | nominal output current | 5 A
RM35BA10 | Complementary | maximum measuring cycle | 140 ms as true rms value
RM35BA10 | Complementary | delay at power up | 0.5 s
RM35BA10 | Complementary | hysteresis | 5 % of threshold
RM35BA10 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35BA10 | Complementary | repeat accuracy | +/- 1 % for input and measurement circuit ¦ +/- 1 % for time delay
RM35BA10 | Complementary | measurement error | 1 % by volt over the whole range ¦ +/- 0.05 %/°C
RM35BA10 | Complementary | response time | < 300 ms (in the event of a fault)
RM35BA10 | Complementary | overload input current | 11 A permanent at 25 °C E1-L2 terminals ¦ 50 A non repetitive < 1 s at 25 °C E1-L2 terminals
RM35BA10 | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35BA10 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35BA10 | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to 60664-1
RM35BA10 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35BA10 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35BA10 | Complementary | operating position | Any position
RM35BA10 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35BA10 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35BA10 | Complementary | housing material | Self-extinguishing plastic
RM35BA10 | Complementary | status LED | 1 LED green for power ON ¦ 1 LED yellow for fault ¦ 1 LED yellow for relay ON
RM35BA10 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35BA10 | Complementary | electrical durability | 100000 cycles
RM35BA10 | Complementary | mechanical durability | 30000000 cycles
RM35BA10 | Complementary | operating rate | <= 360 operations/hour full load
RM35BA10 | Environment | immunity to microbreaks | 500 ms
RM35BA10 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35BA10 | Environment | standards | EN/IEC 60255-6
RM35BA10 | Environment | product certifications | C-Tick ¦ CSA ¦ GOST ¦ UL ¦ GL
RM35BA10 | Environment | ambient air temperature for storage | -40…70 °C
RM35BA10 | Environment | ambient air temperature for operation | -20…50 °C
RM35BA10 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35BA10 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35BA10 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35BA10 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35BA10 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35BA10 | Environment | dielectric strength | 2 kV AC 50 Hz (shock wave 4 kV)
RM35BA10 | Offer Sustainability | Sustainable offer status | Green Premium product
RM35BA10 | Offer Sustainability | REACh Regulation | REACh Declaration
RM35BA10 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35BA10 | Offer Sustainability | Mercury free | Yes
RM35BA10 | Offer Sustainability | RoHS exemption information | Yes
RM35BA10 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35BA10 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35BA10 | Offer Sustainability | Circularity Profile | End of Life Information
RM35BA10 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35BA10 | Contractual warranty | Warranty | 18 months
RM35HZ21FM | Main | range of product | Zelio Control
RM35HZ21FM | Main | product or component type | Modular measurement and control relays
RM35HZ21FM | Main | relay type | Frequency control relays
RM35HZ21FM | Main | relay name | RM35HZ21FM
RM35HZ21FM | Main | relay monitored parameters | Overfrequency and underfrequency 50 or 60 Hz
RM35HZ21FM | Main | time delay type | Adjustable 0.1...10 s, +/- 10 % on crossing the threshold
RM35HZ21FM | Main | switching capacity in VA | 1250 VA
RM35HZ21FM | Main | minimum switching current | 10 mA at 5 V DC
RM35HZ21FM | Main | maximum power consumption in VA | 6 VA AC
RM35HZ21FM | Main | measurement range | 40...70 Hz frequency
RM35HZ21FM | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35HZ21FM | Complementary | reset time | 2000 ms time delay
RM35HZ21FM | Complementary | maximum switching voltage | 250 V AC/DC
RM35HZ21FM | Complementary | [Us] rated supply voltage | 120...277 V AC
RM35HZ21FM | Complementary | [Us] rated supply voltage | 120...277 V AC
RM35HZ21FM | Complementary | supply voltage limits | 102…308 V AC
RM35HZ21FM | Complementary | control circuit frequency | 40...70 Hz
RM35HZ21FM | Complementary | width | 35 mm
RM35HZ21FM | Complementary | output contacts | 1 C/O + 1 C/O
RM35HZ21FM | Complementary | contacts material | Cadmium free
RM35HZ21FM | Complementary | nominal output current | 5 A
RM35HZ21FM | Complementary | maximum input frequency | 70 Hz
RM35HZ21FM | Complementary | maximum measuring cycle | 200 ms measurement cycle as true rms value
RM35HZ21FM | Complementary | delay at power up | 0.5 s
RM35HZ21FM | Complementary | hysteresis | 0.3 % fixed
RM35HZ21FM | Complementary | measurement accuracy | +/- 10 % of the full scale value in input ¦ +/- 10 % of the full scale value in time delay
RM35HZ21FM | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 0.5 % for time delay
RM35HZ21FM | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < +/- 1 % over the whole range with voltage variation
RM35HZ21FM | Complementary | threshold setting | -2...10 Hz ¦ -10...2 Hz
RM35HZ21FM | Complementary | marking | CE : 73/23/EEC ¦ CE : EMC 89/336/EEC
RM35HZ21FM | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35HZ21FM | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35HZ21FM | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35HZ21FM | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35HZ21FM | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35HZ21FM | Complementary | insulation | No galvanic insulation between supply and measurement
RM35HZ21FM | Complementary | operating position | Any position without derating
RM35HZ21FM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35HZ21FM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35HZ21FM | Complementary | housing material | Self-extinguishing plastic
RM35HZ21FM | Complementary | local signalling | 1 LED green for power ON ¦ 1 LED yellow for correct frequency (high R1) ¦ 1 LED yellow for correct frequency (low R2)
RM35HZ21FM | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35HZ21FM | Complementary | electrical durability | 100000 cycles
RM35HZ21FM | Complementary | mechanical durability | 30000000 cycles
RM35HZ21FM | Complementary | operating rate | <= 360 operations/hour full load
RM35HZ21FM | Environment | immunity to microbreaks | 10 ms
RM35HZ21FM | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35HZ21FM | Environment | standards | IEC 60255-6 ¦ NF EN 60255-6
RM35HZ21FM | Environment | product certifications | GL ¦ UL ¦ CSA ¦ C-Tick ¦ GOST
RM35HZ21FM | Environment | ambient air temperature for storage | -40…70 °C
RM35HZ21FM | Environment | ambient air temperature for operation | -20…50 °C
RM35HZ21FM | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35HZ21FM | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35HZ21FM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35HZ21FM | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35HZ21FM | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35HZ21FM | Environment | dielectric test voltage | 2 kV AC 50 Hz
RM35HZ21FM | Environment | non-dissipating shock wave | 4 kV
RM35HZ21FM | Offer Sustainability | Sustainable offer status | Green Premium product
RM35HZ21FM | Offer Sustainability | REACh Regulation | REACh Declaration
RM35HZ21FM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35HZ21FM | Offer Sustainability | Mercury free | Yes
RM35HZ21FM | Offer Sustainability | RoHS exemption information | Yes
RM35HZ21FM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35HZ21FM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35HZ21FM | Offer Sustainability | Circularity Profile | End of Life Information
RM35HZ21FM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35HZ21FM | Contractual warranty | Warranty | 18 months
RM35JA31MW | Main | range of product | Zelio Control
RM35JA31MW | Main | product or component type | Modular measurement and control relays
RM35JA31MW | Main | relay type | Current control relay
RM35JA31MW | Main | relay name | RM35JA
RM35JA31MW | Main | relay monitored parameters | Overcurrent or undercurrent in window mode ¦ Overcurrent or undercurrent detection
RM35JA31MW | Main | time delay | Adjustable 1...20 s, 0 + 10 % on energisation Ti ¦ Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold Tt
RM35JA31MW | Main | switching capacity in VA | 1250 VA
RM35JA31MW | Main | minimum switching current | 10 mA at 5 V DC
RM35JA31MW | Main | maximum switching current | 5 A AC
RM35JA31MW | Main | maximum power consumption in VA | 3.5 VA AC
RM35JA31MW | Main | measurement range | 10...100 mA E2-M terminals ¦ 2...20 mA E1-M terminals ¦ 2...500 mA current ¦ 50...500 mA E3-M terminals
RM35JA31MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35JA31MW | Complementary | reset time | 1500 ms time delay
RM35JA31MW | Complementary | maximum switching voltage | 250 V AC
RM35JA31MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35JA31MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35JA31MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35JA31MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35JA31MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
RM35JA31MW | Complementary | resistance across terminals | 1 Ohm at E2-M terminals ¦ 5 Ohm at E1-M terminals ¦ 0.2 Ohm at E3-M terminals
RM35JA31MW | Complementary | output contacts | 2 C/O
RM35JA31MW | Complementary | nominal output current | 5 A
RM35JA31MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM35JA31MW | Complementary | hysteresis | 5…50 % of threshold setting
RM35JA31MW | Complementary | delay at power up | 0.3 s
RM35JA31MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35JA31MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35JA31MW | Complementary | measurement error | 0.05 %/°C with temperature variation ¦ 1 by volt over the whole range with voltage variation
RM35JA31MW | Complementary | polarity | No DC
RM35JA31MW | Complementary | threshold setting | 10...100 %
RM35JA31MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35JA31MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35JA31MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35JA31MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35JA31MW | Complementary | operating position | Any position without derating
RM35JA31MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35JA31MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35JA31MW | Complementary | housing material | Self-extinguishing plastic
RM35JA31MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35JA31MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35JA31MW | Complementary | electrical durability | 100000 cycles
RM35JA31MW | Complementary | mechanical durability | 30000000 cycles
RM35JA31MW | Complementary | operating rate | <= 360 operations/hour full load
RM35JA31MW | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM35JA31MW | Complementary | contacts material | Cadmium free
RM35JA31MW | Complementary | width | 35 mm
RM35JA31MW | Complementary | net weight | 0.13 kg
RM35JA31MW | Environment | immunity to microbreaks | 50 ms
RM35JA31MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35JA31MW | Environment | standards | EN/IEC 60255-6
RM35JA31MW | Environment | product certifications | GL ¦ CSA ¦ GOST ¦ UL ¦ C-Tick
RM35JA31MW | Environment | ambient air temperature for storage | -40…70 °C
RM35JA31MW | Environment | ambient air temperature for operation | -20…50 °C
RM35JA31MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35JA31MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35JA31MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35JA31MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35JA31MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35JA31MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35JA31MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM35JA31MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35JA31MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35JA31MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35JA31MW | Offer Sustainability | Mercury free | Yes
RM35JA31MW | Offer Sustainability | RoHS exemption information | Yes
RM35JA31MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35JA31MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35JA31MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35JA31MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35JA31MW | Contractual warranty | Warranty | 18 months
RM35JA32MW | Main | range of product | Zelio Control
RM35JA32MW | Main | product or component type | Modular measurement and control relays
RM35JA32MW | Main | relay type | Current control relay
RM35JA32MW | Main | relay name | RM35JA
RM35JA32MW | Main | relay monitored parameters | Overcurrent or undercurrent detection
RM35JA32MW | Main | time delay | Adjustable 1...20 s, 0 + 10 % on energisation Ti ¦ Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold Tt
RM35JA32MW | Main | switching capacity in VA | 1250 VA
RM35JA32MW | Main | minimum switching current | 10 mA at 5 V DC
RM35JA32MW | Main | maximum switching current | 5 A AC/DC
RM35JA32MW | Main | maximum power consumption in VA | 3.5 VA AC
RM35JA32MW | Main | measurement range | 0.15...1.5 A E1-M terminals ¦ 0.5...5 A E2-M terminals ¦ 1.5...15 A E3-M terminals ¦ 150 mA...15 A current
RM35JA32MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35JA32MW | Complementary | reset time | 1500 ms time delay
RM35JA32MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35JA32MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35JA32MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35JA32MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35JA32MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35JA32MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
RM35JA32MW | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals ¦ 0.015 Ohm at E2-M terminals ¦ 0.05 Ohm at E1-M terminals
RM35JA32MW | Complementary | output contacts | 2 C/O
RM35JA32MW | Complementary | nominal output current | 5 A
RM35JA32MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM35JA32MW | Complementary | hysteresis | 5…50 % of threshold setting
RM35JA32MW | Complementary | delay at power up | 0.3 s
RM35JA32MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35JA32MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35JA32MW | Complementary | measurement error | 0.05 %/°C with temperature variation ¦ 1 by volt over the whole range with voltage variation
RM35JA32MW | Complementary | polarity | No DC
RM35JA32MW | Complementary | threshold setting | 10...100 %
RM35JA32MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35JA32MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35JA32MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35JA32MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35JA32MW | Complementary | operating position | Any position without derating
RM35JA32MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35JA32MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35JA32MW | Complementary | housing material | Self-extinguishing plastic
RM35JA32MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35JA32MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35JA32MW | Complementary | electrical durability | 100000 cycles
RM35JA32MW | Complementary | mechanical durability | 30000000 cycles
RM35JA32MW | Complementary | operating rate | <= 360 operations/hour full load
RM35JA32MW | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM35JA32MW | Complementary | contacts material | Cadmium free
RM35JA32MW | Complementary | width | 35 mm
RM35JA32MW | Complementary | net weight | 0.13 kg
RM35JA32MW | Environment | immunity to microbreaks | 50 ms
RM35JA32MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35JA32MW | Environment | standards | EN/IEC 60255-6
RM35JA32MW | Environment | product certifications | GL ¦ UL ¦ GOST ¦ C-Tick ¦ CSA
RM35JA32MW | Environment | ambient air temperature for storage | -40…70 °C
RM35JA32MW | Environment | ambient air temperature for operation | -20…50 °C
RM35JA32MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35JA32MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35JA32MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35JA32MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35JA32MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35JA32MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35JA32MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM35JA32MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35JA32MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35JA32MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35JA32MW | Offer Sustainability | Mercury free | Yes
RM35JA32MW | Offer Sustainability | RoHS exemption information | Yes
RM35JA32MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35JA32MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35JA32MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35JA32MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35JA32MW | Contractual warranty | Warranty | 18 months
RM35LM33MW | Main | range of product | Zelio Control
RM35LM33MW | Main | product or component type | Modular measurement and control relays
RM35LM33MW | Main | relay type | Level control relay
RM35LM33MW | Main | relay name | RM35L
RM35LM33MW | Main | relay monitored parameters | Detection by resistive probes
RM35LM33MW | Main | time delay | Adjustable 0.1...5 s, +/- 10 %
RM35LM33MW | Main | switching capacity in VA | 1250 VA
RM35LM33MW | Main | minimum switching current | 10 mA at 5 V DC
RM35LM33MW | Main | maximum switching current | 5 A AC/DC
RM35LM33MW | Main | power consumption | 5 VA AC
RM35LM33MW | Main | measurement range | 250 Ohm...1 MOhm
RM35LM33MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35LM33MW | Complementary | reset time | 1750 ms
RM35LM33MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35LM33MW | Complementary | [Un] rated nominal voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35LM33MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35LM33MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35LM33MW | Complementary | power consumption | 1.5 W DC
RM35LM33MW | Complementary | output contacts | 2 C/O
RM35LM33MW | Complementary | nominal output current | 5 A
RM35LM33MW | Complementary | delay at power up | 0.6 s
RM35LM33MW | Complementary | measurement accuracy | +/- 10 % of the full scale value ¦ +/- 20 % for the HS range
RM35LM33MW | Complementary | repeat accuracy | +/- 2 % for time delay
RM35LM33MW | Complementary | measurement error | 0.5 %/°C with temperature variation
RM35LM33MW | Complementary | maximum cable distance between devices | 100 m
RM35LM33MW | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) ¦ 5...100 kOhm St (Standard Sensitivity) ¦ 50...1000 kOhm HS (High Sensitivity)
RM35LM33MW | Complementary | sensitivity adjustment | 5…100 %
RM35LM33MW | Complementary | maximum supply current for sensors | 1 mA
RM35LM33MW | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable ¦ 2.2 nF at St (Standard Sensitivity) for probe cable ¦ 4.7 nF at LS (Low Sensitivity)
RM35LM33MW | Complementary | marking | CE : 73/23/EEC ¦ CE : EMC 89/336/EEC
RM35LM33MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35LM33MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35LM33MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35LM33MW | Complementary | operating position | Any position without derating
RM35LM33MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end
RM35LM33MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35LM33MW | Complementary | housing material | Self-extinguishing plastic
RM35LM33MW | Complementary | local signalling | LED (yellow) for relay ON ¦ LED (green) for power ON ¦ LED (yellow) for timer ON
RM35LM33MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35LM33MW | Complementary | electrical durability | 100000 cycles
RM35LM33MW | Complementary | mechanical durability | 30000000 cycles
RM35LM33MW | Complementary | operating rate | <= 360 operations/hour full load
RM35LM33MW | Complementary | safety reliability data | B10d = 170000 ¦ MTTFd = 182.6 years
RM35LM33MW | Complementary | width | 35 mm
RM35LM33MW | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM35LM33MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35LM33MW | Environment | standards | EN/IEC 60255-6
RM35LM33MW | Environment | product certifications | CSA ¦ GL ¦ UL ¦ C-Tick ¦ GOST
RM35LM33MW | Environment | ambient air temperature for storage | -40…70 °C
RM35LM33MW | Environment | ambient air temperature for operation | -20…50 °C
RM35LM33MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35LM33MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35LM33MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35LM33MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35LM33MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35LM33MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35LM33MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35LM33MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35LM33MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35LM33MW | Offer Sustainability | Mercury free | Yes
RM35LM33MW | Offer Sustainability | RoHS exemption information | Yes
RM35LM33MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35LM33MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35LM33MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35LM33MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35LM33MW | Contractual warranty | Warranty | 18 months
RM35LV14MW | Main | range of product | Zelio Control
RM35LV14MW | Main | product or component type | Modular measurement and control relays
RM35LV14MW | Main | relay type | Level control relay
RM35LV14MW | Main | relay name | RM35L
RM35LV14MW | Main | relay monitored parameters | Detection by discrete sensors
RM35LV14MW | Main | time delay | Adjustable 0.1...5 s, +/- 10 %
RM35LV14MW | Main | switching capacity in VA | 1250 VA
RM35LV14MW | Main | minimum switching current | 10 mA at 5 V DC
RM35LV14MW | Main | maximum switching current | 5 A AC/DC
RM35LV14MW | Main | power consumption | 5 VA AC
RM35LV14MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35LV14MW | Complementary | reset time | 1000 ms ¦ 4000 ms
RM35LV14MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35LV14MW | Complementary | [Un] rated nominal voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35LV14MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35LV14MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35LV14MW | Complementary | power consumption | 1.5 W DC
RM35LV14MW | Complementary | output contacts | 1 C/O
RM35LV14MW | Complementary | nominal output current | 5 A
RM35LV14MW | Complementary | delay at power up | 0.5 s
RM35LV14MW | Complementary | measurement accuracy | +/- 10 % of the full scale value ¦ +/- 20 % for the HS range
RM35LV14MW | Complementary | repeat accuracy | +/- 2 % for time delay
RM35LV14MW | Complementary | measurement error | 0.5 %/°C with temperature variation
RM35LV14MW | Complementary | maximum cable distance between devices | 100 m
RM35LV14MW | Complementary | sensitivity adjustment | 5…100 %
RM35LV14MW | Complementary | maximum supply current for sensors | 40 mA
RM35LV14MW | Complementary | cable capacitance | 10 nF for probe cable
RM35LV14MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35LV14MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35LV14MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35LV14MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35LV14MW | Complementary | operating position | Any position without derating
RM35LV14MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end
RM35LV14MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35LV14MW | Complementary | housing material | Self-extinguishing plastic
RM35LV14MW | Complementary | local signalling | LED (yellow) for relay ON ¦ LED (green) for power ON ¦ LED (yellow) for timer ON
RM35LV14MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35LV14MW | Complementary | electrical durability | 100000 cycles
RM35LV14MW | Complementary | mechanical durability | 30000000 cycles
RM35LV14MW | Complementary | operating rate | <= 360 operations/hour full load
RM35LV14MW | Complementary | safety reliability data | B10d = 170000 ¦ MTTFd = 182.6 years
RM35LV14MW | Complementary | width | 35 mm
RM35LV14MW | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM35LV14MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35LV14MW | Environment | standards | EN/IEC 60255-6
RM35LV14MW | Environment | product certifications | GOST ¦ CSA ¦ UL ¦ GL ¦ C-Tick
RM35LV14MW | Environment | ambient air temperature for storage | -40…70 °C
RM35LV14MW | Environment | ambient air temperature for operation | -20…50 °C
RM35LV14MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35LV14MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35LV14MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35LV14MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35LV14MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35LV14MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35LV14MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35LV14MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35LV14MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35LV14MW | Offer Sustainability | Mercury free | Yes
RM35LV14MW | Offer Sustainability | RoHS exemption information | Yes
RM35LV14MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35LV14MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35LV14MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35LV14MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35LV14MW | Contractual warranty | Warranty | 18 months
RM35S0MW | Main | range of product | Zelio Control
RM35S0MW | Main | product or component type | Modular measurement and control relays
RM35S0MW | Main | relay type | Speed control relays
RM35S0MW | Main | relay name | RM35S
RM35S0MW | Main | relay monitored parameters | Overspeed ¦ Underspeed
RM35S0MW | Main | time delay range | 0.6...60 s adjustable on energisation delay (tolerance: 0...10 % of the full scale value)
RM35S0MW | Main | switching capacity in VA | 1250 VA
RM35S0MW | Main | minimum switching current | 10 mA at 5 V DC
RM35S0MW | Main | [Us] rated supply voltage | 24...240 V AC/DC
RM35S0MW | Main | maximum power consumption in VA | 5 VA AC
RM35S0MW | Main | measurement range | 0.05...0.5 s ¦ 0.5...5 min ¦ 1...10 min ¦ 1...10 s ¦ 0.5...5 s ¦ 0.1...1 s ¦ 0.1...1 min
RM35S0MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35S0MW | Complementary | rest time in memory mode | 50 ms contact S2 in memory mode on time delay ¦ 1 s supply Un in memory mode on time delay
RM35S0MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35S0MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35S0MW | Complementary | maximum power consumption in W | 3 W DC
RM35S0MW | Complementary | width | 35 mm
RM35S0MW | Complementary | output contacts | 1 C/O
RM35S0MW | Complementary | contacts material | Cadmium free
RM35S0MW | Complementary | nominal output current | 5 A
RM35S0MW | Complementary | delay at power up | 0.05 s
RM35S0MW | Complementary | hysteresis | 5 % of threshold
RM35S0MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35S0MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 0.5 % for time delay
RM35S0MW | Complementary | measurement error | +/- 0.1 %/°C with temperature variation ¦ < +/- 1 % over the whole range with voltage variation
RM35S0MW | Complementary | input frequency | 0.0017…20 Hz
RM35S0MW | Complementary | response time | 15 ms max (on crossing the threshold)
RM35S0MW | Complementary | polarity | Reversible polarity on DC supply
RM35S0MW | Complementary | threshold setting | 10...100 %
RM35S0MW | Complementary | supply voltage for sensor | 11.5...12.5 V
RM35S0MW | Complementary | maximum supply current for sensors | 40 mA for < 24 V AC at 25 °C ¦ 40 mA for < 24 V DC at 25 °C ¦ 50 mA for 24...240 V AC ¦ 50 mA for 24...240 V DC
RM35S0MW | Complementary | impulse duration | >= 5 ms high state ¦ >= 5 ms low state
RM35S0MW | Complementary | input compatibility | 3-wire sensor (E1) PNP or NPN, 12 V, 50 mA ¦ NAMUR sensor (E2), 12 V, 1.5 kOhm ¦ Voltage input (E1), 0...30 V, 9.5 kOhm, high state >= 4.5 V low state <= 1 V ¦ Volt-free contact input (E1), 12 V, 9.5 kOhm
RM35S0MW | Complementary | marking | CE : EMC 89/336/EEC ¦ CE : 73/23/EEC
RM35S0MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35S0MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35S0MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1
RM35S0MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35S0MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35S0MW | Complementary | operating position | Any position without derating
RM35S0MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35S0MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35S0MW | Complementary | housing material | Self-extinguishing plastic
RM35S0MW | Complementary | status LED | 1 LED green for power ON ¦ 1 LED yellow for inhibit ¦ 1 LED yellow for relay (R)
RM35S0MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35S0MW | Complementary | electrical durability | 100000 cycles
RM35S0MW | Complementary | mechanical durability | 30000000 cycles
RM35S0MW | Complementary | operating rate | <= 360 operations/hour full load
RM35S0MW | Environment | immunity to microbreaks | 50 ms
RM35S0MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35S0MW | Environment | standards | NF EN 60255-6 ¦ IEC 60255-6
RM35S0MW | Environment | product certifications | C-Tick ¦ GOST ¦ UL ¦ GL ¦ CSA
RM35S0MW | Environment | ambient air temperature for storage | -40…70 °C
RM35S0MW | Environment | ambient air temperature for operation | -20…50 °C
RM35S0MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35S0MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60068-2-6/IEC 60255-21-1
RM35S0MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35S0MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35S0MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35S0MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
RM35S0MW | Environment | non-dissipating shock wave | 4 kV
RM35S0MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35S0MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35S0MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35S0MW | Offer Sustainability | Mercury free | Yes
RM35S0MW | Offer Sustainability | RoHS exemption information | Yes
RM35S0MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35S0MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35S0MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35S0MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35S0MW | Contractual warranty | Warranty | 18 months
RM35TF30 | Main | range of product | Zelio Control
RM35TF30 | Main | product or component type | Modular measurement and control relays
RM35TF30 | Main | relay type | Multifunction control relay
RM35TF30 | Main | product specific application | For 3-phase supply
RM35TF30 | Main | relay name | RM35TF
RM35TF30 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Phase sequence ¦ Phase failure detection ¦ Asymmetry
RM35TF30 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM35TF30 | Main | switching capacity in VA | 1250 VA
RM35TF30 | Main | measurement range | 208...480 V voltage AC
RM35TF30 | Complementary | reset time | 1500 ms at 480 V
RM35TF30 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM35TF30 | Complementary | minimum switching current | 10 mA at 5 V DC
RM35TF30 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM35TF30 | Complementary | supply voltage limits | 194…528 V AC, 3 phases
RM35TF30 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM35TF30 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM35TF30 | Complementary | voltage detection threshold | < 194 V
RM35TF30 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM35TF30 | Complementary | output contacts | 2 C/O
RM35TF30 | Complementary | nominal output current | 5 A
RM35TF30 | Complementary | measurement voltage limits | 176…528 V AC
RM35TF30 | Complementary | hysteresis | 2 %
RM35TF30 | Complementary | delay at power up | 650 ms
RM35TF30 | Complementary | maximum measuring cycle | 140 ms measurement cycle as true rms value
RM35TF30 | Complementary | threshold adjustment voltage | -20...-2 % in the range 380...480 V AC ¦ 2...20 % of Un selected ¦ -12...-2 % in the range 220 V AC ¦ +2...+20 % in the range 220...440 V AC ¦ +2...+10 % in the range 480 V AC
RM35TF30 | Complementary | voltage range | 220...480 V phase to phase
RM35TF30 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM35TF30 | Complementary | repeat accuracy | 0.3 % for time delay ¦ 0.5 % for input and measurement circuit
RM35TF30 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35TF30 | Complementary | response time | < 200 ms (in the event of a fault)
RM35TF30 | Complementary | marking | CE
RM35TF30 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35TF30 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM35TF30 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35TF30 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35TF30 | Complementary | operating position | Any position without derating
RM35TF30 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35TF30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35TF30 | Complementary | housing material | Self-extinguishing plastic
RM35TF30 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON ¦ LED (yellow) for fault
RM35TF30 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35TF30 | Complementary | electrical durability | 100000 cycles
RM35TF30 | Complementary | mechanical durability | 30000000 cycles
RM35TF30 | Complementary | operating rate | <= 360 operations/hour full load
RM35TF30 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35TF30 | Complementary | safety reliability data | MTTFd = 399.5 years ¦ B10d = 360000
RM35TF30 | Complementary | width | 35 mm
RM35TF30 | Complementary | net weight | 0.13 kg
RM35TF30 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM35TF30 | Environment | standards | EN/IEC 60255-1
RM35TF30 | Environment | product certifications | GL ¦ UL ¦ CSA ¦ GOST ¦ C-Tick
RM35TF30 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM35TF30 | Environment | ambient air temperature for storage | -40…70 °C
RM35TF30 | Environment | ambient air temperature for operation | -20…50 °C
RM35TF30 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35TF30 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35TF30 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35TF30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35TF30 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35TF30 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35TF30 | Environment | non-dissipating shock wave | 4 kV
RM35TF30 | Offer Sustainability | Sustainable offer status | Green Premium product
RM35TF30 | Offer Sustainability | REACh Regulation | REACh Declaration
RM35TF30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35TF30 | Offer Sustainability | Mercury free | Yes
RM35TF30 | Offer Sustainability | RoHS exemption information | Yes
RM35TF30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35TF30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35TF30 | Offer Sustainability | Circularity Profile | End of Life Information
RM35TF30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35TF30 | Contractual warranty | Warranty | 18 months
RM35TF30SP01 | Main | range of product | Zelio Control
RM35TF30SP01 | Main | product or component type | Modular measurement and control relays
RM35TF30SP01 | Main | relay type | Multifunction control relay
RM35TF30SP01 | Main | product specific application | For 3-phase supply
RM35TF30SP01 | Main | relay name | RM35TF
RM35TF30SP01 | Main | relay monitored parameters | Phase sequence ¦ Asymmetry ¦ Undervoltage and overvoltage in window mode ¦ Phase failure detection
RM35TF30SP01 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM35TF30SP01 | Main | switching capacity in VA | 1250 VA
RM35TF30SP01 | Main | measurement range | 194...528 V AC
RM35TF30SP01 | Complementary | reset time | 1500 ms at 480 V
RM35TF30SP01 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM35TF30SP01 | Complementary | minimum switching current | 10 mA at 5 V DC
RM35TF30SP01 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM35TF30SP01 | Complementary | supply voltage limits | 194…528 V AC, 3 phases
RM35TF30SP01 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM35TF30SP01 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM35TF30SP01 | Complementary | voltage detection threshold | < 194 V
RM35TF30SP01 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM35TF30SP01 | Complementary | output contacts | 2 C/O
RM35TF30SP01 | Complementary | nominal output current | 5 A
RM35TF30SP01 | Complementary | hysteresis | 2 %
RM35TF30SP01 | Complementary | delay at power up | 650 ms
RM35TF30SP01 | Complementary | maximum measuring cycle | 140 ms measurement cycle as true rms value
RM35TF30SP01 | Complementary | threshold adjustment voltage | 2...20 % of Un selected ¦ -12...-2 % in the range 220 V AC ¦ +2...+10 % in the range 480 V AC ¦ -20...-2 % in the range 380...480 V AC ¦ +2...+20 % in the range 220...440 V AC
RM35TF30SP01 | Complementary | voltage range | 220...480 V phase to phase
RM35TF30SP01 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM35TF30SP01 | Complementary | repeat accuracy | 0.3 % for time delay ¦ 0.5 % for input and measurement circuit
RM35TF30SP01 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35TF30SP01 | Complementary | response time | < 200 ms (in the event of a fault)
RM35TF30SP01 | Complementary | marking | CE
RM35TF30SP01 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35TF30SP01 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM35TF30SP01 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35TF30SP01 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35TF30SP01 | Complementary | operating position | Any position without derating
RM35TF30SP01 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35TF30SP01 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35TF30SP01 | Complementary | housing material | Self-extinguishing plastic
RM35TF30SP01 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON ¦ LED (yellow) for fault
RM35TF30SP01 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35TF30SP01 | Complementary | electrical durability | 100000 cycles
RM35TF30SP01 | Complementary | mechanical durability | 30000000 cycles
RM35TF30SP01 | Complementary | operating rate | <= 360 operations/hour full load
RM35TF30SP01 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35TF30SP01 | Complementary | safety reliability data | B10d = 360000 ¦ MTTFd = 399.5 years
RM35TF30SP01 | Complementary | width | 35 mm
RM35TF30SP01 | Complementary | net weight | 0.13 kg
RM35TF30SP01 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM35TF30SP01 | Environment | standards | EN/IEC 60255-1
RM35TF30SP01 | Environment | product certifications | CSA ¦ C-Tick ¦ GL ¦ GOST ¦ UL
RM35TF30SP01 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM35TF30SP01 | Environment | ambient air temperature for storage | -40…70 °C
RM35TF30SP01 | Environment | ambient air temperature for operation | -20…50 °C
RM35TF30SP01 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35TF30SP01 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35TF30SP01 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35TF30SP01 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35TF30SP01 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35TF30SP01 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35TF30SP01 | Environment | non-dissipating shock wave | 4 kV
RM35TF30SP01 | Offer Sustainability | Sustainable offer status | Green Premium product
RM35TF30SP01 | Offer Sustainability | REACh Regulation | REACh Declaration
RM35TF30SP01 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35TF30SP01 | Offer Sustainability | Mercury free | Yes
RM35TF30SP01 | Offer Sustainability | RoHS exemption information | Yes
RM35TF30SP01 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35TF30SP01 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35TF30SP01 | Offer Sustainability | Circularity Profile | End of Life Information
RM35TF30SP01 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35TM250MW | Main | range of product | Zelio Control
RM35TM250MW | Main | product or component type | Modular measurement and control relays
RM35TM250MW | Main | relay type | Motor temperature control relay
RM35TM250MW | Main | product specific application | For 3-phase supply
RM35TM250MW | Main | relay name | RM35TM
RM35TM250MW | Main | relay monitored parameters | Phase failure detection ¦ Phase sequence ¦ Test/reset button ¦ Motor temperature via PTC probe ¦ Selection (with or without memory)
RM35TM250MW | Main | time delay | Fixed 0.3 s
RM35TM250MW | Main | switching capacity in VA | 1250 VA
RM35TM250MW | Main | measurement range | 208...480 V voltage AC ¦ 0...20 Ohm short-circuit detection
RM35TM250MW | Complementary | reset time | 10000 ms output
RM35TM250MW | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM35TM250MW | Complementary | minimum switching current | 10 mA at 5 V DC
RM35TM250MW | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM35TM250MW | Complementary | supply voltage limits | 20.4…264 V AC ¦ 20.4…264 V DC
RM35TM250MW | Complementary | power consumption in VA | 0…4 VA at 24...240 V AC
RM35TM250MW | Complementary | power consumption | 0.5 W DC
RM35TM250MW | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM35TM250MW | Complementary | resistance across terminals | 602 mOhm
RM35TM250MW | Complementary | output contacts | 2 NO
RM35TM250MW | Complementary | nominal output current | 5 A
RM35TM250MW | Complementary | measurement voltage limits | 176…528 V AC
RM35TM250MW | Complementary | delay at power up | 500 ms
RM35TM250MW | Complementary | voltage range | 176...528 V
RM35TM250MW | Complementary | response time | > 50 ms (input Y1 (contact Y1-T1) and push-button)
RM35TM250MW | Complementary | [Uc] control circuit voltage | <= 3.6 V of temperature control circuit (T1-T2 terminals open)
RM35TM250MW | Complementary | short-circuit current | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited)
RM35TM250MW | Complementary | maximum resistance | 1500 Ohm for temperature sensor at 20 °C
RM35TM250MW | Complementary | tripping threshold | 3100 Ohm +/- 10 % for temperature control circuit
RM35TM250MW | Complementary | reset threshold | 1650 Ohm +/- 10 % for temperature control circuit
RM35TM250MW | Complementary | marking | CE
RM35TM250MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35TM250MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35TM250MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35TM250MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35TM250MW | Complementary | operating position | Any position without derating
RM35TM250MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35TM250MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35TM250MW | Complementary | housing material | Self-extinguishing plastic
RM35TM250MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for phase of relay (R2) ¦ LED (yellow) for temperature of relay (R1)
RM35TM250MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35TM250MW | Complementary | electrical durability | 10000 cycles
RM35TM250MW | Complementary | mechanical durability | 30000000 cycles
RM35TM250MW | Complementary | operating rate | <= 360 operations/hour full load
RM35TM250MW | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35TM250MW | Complementary | width | 35 mm
RM35TM250MW | Complementary | net weight | 0.13 kg
RM35TM250MW | Environment | immunity to microbreaks | 20 ms at 20.4 V
RM35TM250MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM35TM250MW | Environment | standards | EN/IEC 60255-6 ¦ IEC 60034-11-2
RM35TM250MW | Environment | product certifications | CSA ¦ C-Tick ¦ GOST ¦ UL ¦ GL
RM35TM250MW | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35TM250MW | Environment | ambient air temperature for storage | -40…70 °C
RM35TM250MW | Environment | ambient air temperature for operation | -20…50 °C
RM35TM250MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35TM250MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35TM250MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35TM250MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35TM250MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35TM250MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35TM250MW | Environment | non-dissipating shock wave | 4 kV
RM35TM250MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35TM250MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35TM250MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35TM250MW | Offer Sustainability | Mercury free | Yes
RM35TM250MW | Offer Sustainability | RoHS exemption information | Yes
RM35TM250MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35TM250MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35TM250MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35TM250MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35TM250MW | Contractual warranty | Warranty | 18 months
RM35TM50MW | Main | range of product | Zelio Control
RM35TM50MW | Main | product or component type | Modular measurement and control relays
RM35TM50MW | Main | relay type | Motor temperature control relay
RM35TM50MW | Main | product specific application | For 3-phase supply
RM35TM50MW | Main | relay name | RM35TM
RM35TM50MW | Main | relay monitored parameters | Phase sequence ¦ Motor temperature via PTC probe ¦ Phase failure detection
RM35TM50MW | Main | time delay | Fixed 0.3 s
RM35TM50MW | Main | switching capacity in VA | 1250 VA
RM35TM50MW | Main | measurement range | 208...480 V voltage AC ¦ 0...20 Ohm short-circuit detection
RM35TM50MW | Complementary | reset time | 10000 ms output
RM35TM50MW | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM35TM50MW | Complementary | minimum switching current | 10 mA at 5 V DC
RM35TM50MW | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM35TM50MW | Complementary | supply voltage limits | 20.4…264 V AC ¦ 20.4…264 V DC
RM35TM50MW | Complementary | power consumption in VA | 0…4 VA at 24...240 V AC
RM35TM50MW | Complementary | power consumption | 0.5 W DC
RM35TM50MW | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM35TM50MW | Complementary | resistance across terminals | 602 mOhm
RM35TM50MW | Complementary | output contacts | 2 NO
RM35TM50MW | Complementary | nominal output current | 5 A
RM35TM50MW | Complementary | measurement voltage limits | 176…528 V AC
RM35TM50MW | Complementary | delay at power up | 500 ms
RM35TM50MW | Complementary | voltage range | 176...528 V
RM35TM50MW | Complementary | response time | > 50 ms (input Y1 (contact Y1-T1) and push-button)
RM35TM50MW | Complementary | [Uc] control circuit voltage | <= 3.6 V of temperature control circuit (T1-T2 terminals open)
RM35TM50MW | Complementary | short-circuit current | 0.007 A temperature sensing circuit (T1-T2 terminals short circuited)
RM35TM50MW | Complementary | maximum resistance | 1500 Ohm for temperature sensor at 20 °C
RM35TM50MW | Complementary | tripping threshold | 3100 Ohm +/- 10 % for temperature control circuit
RM35TM50MW | Complementary | reset threshold | 1650 Ohm +/- 10 % for temperature control circuit
RM35TM50MW | Complementary | marking | CE
RM35TM50MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35TM50MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35TM50MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35TM50MW | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM35TM50MW | Complementary | operating position | Any position without derating
RM35TM50MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35TM50MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35TM50MW | Complementary | housing material | Self-extinguishing plastic
RM35TM50MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for phase of relay (R2) ¦ LED (yellow) for temperature of relay (R1)
RM35TM50MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35TM50MW | Complementary | electrical durability | 10000 cycles
RM35TM50MW | Complementary | mechanical durability | 30000000 cycles
RM35TM50MW | Complementary | operating rate | <= 360 operations/hour full load
RM35TM50MW | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM35TM50MW | Complementary | width | 35 mm
RM35TM50MW | Complementary | net weight | 0.13 kg
RM35TM50MW | Environment | immunity to microbreaks | 20 ms at 20.4 V
RM35TM50MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM35TM50MW | Environment | standards | EN/IEC 60255-6 ¦ IEC 60034-11-2
RM35TM50MW | Environment | product certifications | GL ¦ UL ¦ GOST ¦ C-Tick ¦ CSA
RM35TM50MW | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35TM50MW | Environment | ambient air temperature for storage | -40…70 °C
RM35TM50MW | Environment | ambient air temperature for operation | -20…50 °C
RM35TM50MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35TM50MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35TM50MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM35TM50MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35TM50MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35TM50MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35TM50MW | Environment | non-dissipating shock wave | 4 kV
RM35TM50MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35TM50MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35TM50MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35TM50MW | Offer Sustainability | Mercury free | Yes
RM35TM50MW | Offer Sustainability | RoHS exemption information | Yes
RM35TM50MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35TM50MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35TM50MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35TM50MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35TM50MW | Contractual warranty | Warranty | 18 months
RM35UA11MW | Main | range of product | Zelio Control
RM35UA11MW | Main | product or component type | Modular measurement and control relays
RM35UA11MW | Main | relay type | Multifunction voltage control relay
RM35UA11MW | Main | relay name | RM35UA
RM35UA11MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
RM35UA11MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM35UA11MW | Main | switching capacity in VA | 1250 VA
RM35UA11MW | Main | minimum switching current | 10 mA at 5 V DC
RM35UA11MW | Main | maximum switching current | 5 A AC/DC
RM35UA11MW | Main | power consumption in VA | 0…3.5 VA AC
RM35UA11MW | Main | measurement range | 0.05...5 V voltage
RM35UA11MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35UA11MW | Complementary | reset time | 1500 ms time delay
RM35UA11MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35UA11MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35UA11MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35UA11MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35UA11MW | Complementary | immunity to microbreaks | 10 ms
RM35UA11MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
RM35UA11MW | Complementary | resistance across terminals | 30 mOhm at E2-M terminals ¦ 5 mOhm at E1-M terminals ¦ 50 mOhm at E3-M terminals
RM35UA11MW | Complementary | output contacts | 2 C/O
RM35UA11MW | Complementary | nominal output current | 5 A
RM35UA11MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM35UA11MW | Complementary | hysteresis | 5…50 % of threshold setting
RM35UA11MW | Complementary | delay at power up | 600 ms
RM35UA11MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35UA11MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35UA11MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM35UA11MW | Complementary | polarity | Non reversible polarity on DC supply
RM35UA11MW | Complementary | sensitivity scale | 0.05...0.5 V E1-M terminals ¦ 0.3...3 V E2-M terminals ¦ 0.5...5 V E3-M terminals
RM35UA11MW | Complementary | threshold setting | 10...100 %
RM35UA11MW | Complementary | quality labels | CE
RM35UA11MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35UA11MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35UA11MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 600 V conforming to IEC 60664-1
RM35UA11MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35UA11MW | Complementary | operating position | Any position without derating
RM35UA11MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35UA11MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35UA11MW | Complementary | housing material | Self-extinguishing plastic
RM35UA11MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35UA11MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35UA11MW | Complementary | electrical durability | 100000 cycles
RM35UA11MW | Complementary | mechanical durability | 30000000 cycles
RM35UA11MW | Complementary | operating rate | <= 360 operations/hour full load
RM35UA11MW | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM35UA11MW | Complementary | width | 35 mm
RM35UA11MW | Complementary | net weight | 0.08 kg
RM35UA11MW | Complementary | compatibility code | RM3
RM35UA11MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35UA11MW | Environment | standards | EN/IEC 60255-6
RM35UA11MW | Environment | product certifications | GOST ¦ CSA ¦ GL ¦ UL ¦ C-Tick
RM35UA11MW | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35UA11MW | Environment | ambient air temperature for storage | -40…70 °C
RM35UA11MW | Environment | ambient air temperature for operation | -20…50 °C
RM35UA11MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35UA11MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35UA11MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM35UA11MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35UA11MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35UA11MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35UA11MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM35UA11MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35UA11MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35UA11MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35UA11MW | Offer Sustainability | Mercury free | Yes
RM35UA11MW | Offer Sustainability | RoHS exemption information | Yes
RM35UA11MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35UA11MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35UA11MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35UA11MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35UA11MW | Contractual warranty | Warranty | 18 months
RM35UA12MW | Main | range of product | Zelio Control
RM35UA12MW | Main | product or component type | Modular measurement and control relays
RM35UA12MW | Main | relay type | Multifunction voltage control relay
RM35UA12MW | Main | relay name | RM35UA
RM35UA12MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
RM35UA12MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM35UA12MW | Main | switching capacity in VA | 1250 VA
RM35UA12MW | Main | minimum switching current | 10 mA at 5 V DC
RM35UA12MW | Main | maximum switching current | 5 A AC/DC
RM35UA12MW | Main | power consumption in VA | 0…3.5 VA AC
RM35UA12MW | Main | measurement range | 1...100 V voltage
RM35UA12MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35UA12MW | Complementary | reset time | 1500 ms time delay
RM35UA12MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35UA12MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35UA12MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35UA12MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35UA12MW | Complementary | immunity to microbreaks | 10 ms
RM35UA12MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
RM35UA12MW | Complementary | resistance across terminals | 110 mOhm at E2-M terminals ¦ 22 mOhm at E1-M terminals ¦ 220 mOhm at E3-M terminals
RM35UA12MW | Complementary | output contacts | 2 C/O
RM35UA12MW | Complementary | nominal output current | 5 A
RM35UA12MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM35UA12MW | Complementary | hysteresis | 5…50 % of threshold setting
RM35UA12MW | Complementary | delay at power up | 600 ms
RM35UA12MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35UA12MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35UA12MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM35UA12MW | Complementary | polarity | Non reversible polarity on DC supply
RM35UA12MW | Complementary | sensitivity scale | 1...10 V E1-M terminals ¦ 10...100 V E3-M terminals ¦ 5...50 V E2-M terminals
RM35UA12MW | Complementary | threshold setting | 10...100 %
RM35UA12MW | Complementary | quality labels | CE
RM35UA12MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35UA12MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35UA12MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 600 V conforming to IEC 60664-1
RM35UA12MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35UA12MW | Complementary | operating position | Any position without derating
RM35UA12MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35UA12MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35UA12MW | Complementary | housing material | Self-extinguishing plastic
RM35UA12MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35UA12MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35UA12MW | Complementary | electrical durability | 100000 cycles
RM35UA12MW | Complementary | mechanical durability | 30000000 cycles
RM35UA12MW | Complementary | operating rate | <= 360 operations/hour full load
RM35UA12MW | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM35UA12MW | Complementary | width | 35 mm
RM35UA12MW | Complementary | net weight | 0.08 kg
RM35UA12MW | Complementary | compatibility code | RM3
RM35UA12MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35UA12MW | Environment | standards | EN/IEC 60255-6
RM35UA12MW | Environment | product certifications | GOST ¦ C-Tick ¦ UL ¦ GL ¦ CSA
RM35UA12MW | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35UA12MW | Environment | ambient air temperature for storage | -40…70 °C
RM35UA12MW | Environment | ambient air temperature for operation | -20…50 °C
RM35UA12MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35UA12MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35UA12MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM35UA12MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35UA12MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35UA12MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35UA12MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM35UA12MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35UA12MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35UA12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35UA12MW | Offer Sustainability | Mercury free | Yes
RM35UA12MW | Offer Sustainability | RoHS exemption information | Yes
RM35UA12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35UA12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35UA12MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35UA12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35UA12MW | Contractual warranty | Warranty | 18 months
RM35UA13MW | Main | range of product | Zelio Control
RM35UA13MW | Main | product or component type | Modular measurement and control relays
RM35UA13MW | Main | relay type | Multifunction voltage control relay
RM35UA13MW | Main | relay name | RM35UA
RM35UA13MW | Main | relay monitored parameters | Overvoltage or undervoltage detection
RM35UA13MW | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM35UA13MW | Main | switching capacity in VA | 1250 VA
RM35UA13MW | Main | minimum switching current | 10 mA at 5 V DC
RM35UA13MW | Main | maximum switching current | 5 A AC/DC
RM35UA13MW | Main | power consumption in VA | 0…3.5 VA AC
RM35UA13MW | Main | measurement range | 15...600 V voltage
RM35UA13MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35UA13MW | Complementary | reset time | 1500 ms time delay
RM35UA13MW | Complementary | maximum switching voltage | 250 V AC/DC
RM35UA13MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35UA13MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35UA13MW | Complementary | maximum power consumption in W | 0.6 W DC
RM35UA13MW | Complementary | immunity to microbreaks | 10 ms
RM35UA13MW | Complementary | control circuit frequency | 40...70 Hz +/- 10 %
RM35UA13MW | Complementary | resistance across terminals | 150 mOhm at E1-M terminals ¦ 300 mOhm at E2-M terminals ¦ 600 mOhm at E3-M terminals
RM35UA13MW | Complementary | output contacts | 2 C/O
RM35UA13MW | Complementary | nominal output current | 5 A
RM35UA13MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM35UA13MW | Complementary | hysteresis | 5…50 % of threshold setting
RM35UA13MW | Complementary | delay at power up | 600 ms
RM35UA13MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35UA13MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35UA13MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM35UA13MW | Complementary | polarity | Non reversible polarity on DC supply
RM35UA13MW | Complementary | sensitivity scale | 15...150 V E1-M terminals ¦ 30...300 V E2-M terminals ¦ 60...600 V E3-M terminals
RM35UA13MW | Complementary | threshold setting | 10...100 %
RM35UA13MW | Complementary | quality labels | CE
RM35UA13MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35UA13MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60664-1 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC between supply and relay output conforming to IEC 60664-1 ¦ > 500 MOhm at 500 V DC between measurement and relay output conforming to IEC 60255-5 ¦ > 1 MOhm at 500 V DC between supply and measurement conforming to IEC 60664-1
RM35UA13MW | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60664-1 ¦ 600 V conforming to IEC 60664-1
RM35UA13MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM35UA13MW | Complementary | operating position | Any position without derating
RM35UA13MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35UA13MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35UA13MW | Complementary | housing material | Self-extinguishing plastic
RM35UA13MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35UA13MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35UA13MW | Complementary | electrical durability | 100000 cycles
RM35UA13MW | Complementary | mechanical durability | 30000000 cycles
RM35UA13MW | Complementary | operating rate | <= 360 operations/hour full load
RM35UA13MW | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM35UA13MW | Complementary | width | 35 mm
RM35UA13MW | Complementary | net weight | 0.08 kg
RM35UA13MW | Complementary | compatibility code | RM3
RM35UA13MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35UA13MW | Environment | standards | EN/IEC 60255-6
RM35UA13MW | Environment | product certifications | GOST ¦ UL ¦ GL ¦ C-Tick ¦ CSA
RM35UA13MW | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35UA13MW | Environment | ambient air temperature for storage | -40…70 °C
RM35UA13MW | Environment | ambient air temperature for operation | -20…50 °C
RM35UA13MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35UA13MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35UA13MW | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM35UA13MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35UA13MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35UA13MW | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM35UA13MW | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM35UA13MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM35UA13MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM35UA13MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35UA13MW | Offer Sustainability | Mercury free | Yes
RM35UA13MW | Offer Sustainability | RoHS exemption information | Yes
RM35UA13MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35UA13MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35UA13MW | Offer Sustainability | Circularity Profile | End of Life Information
RM35UA13MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35UA13MW | Contractual warranty | Warranty | 18 months
RM35UB330 | Main | range of product | Zelio Control
RM35UB330 | Main | product or component type | Modular measurement and control relays
RM35UB330 | Main | relay type | Voltage control relay
RM35UB330 | Main | product specific application | For 3-phase supply
RM35UB330 | Main | relay name | RM35UB3
RM35UB330 | Main | relay monitored parameters | Overvoltage and undervoltage between phases
RM35UB330 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM35UB330 | Main | switching capacity in VA | 1250 VA
RM35UB330 | Main | minimum switching current | 10 mA at 5 V DC
RM35UB330 | Main | maximum switching current | 5 A AC/DC
RM35UB330 | Main | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM35UB330 | Main | measurement range | 194...528 V voltage AC 50/60 Hz
RM35UB330 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35UB330 | Complementary | reset time | 1500 ms time delay
RM35UB330 | Complementary | maximum switching voltage | 250 V AC/DC
RM35UB330 | Complementary | [Us] rated supply voltage | 220...480 V AC 50/60 Hz +/- 10 %
RM35UB330 | Complementary | supply voltage limits | 194…528 V AC
RM35UB330 | Complementary | voltage detection threshold | 194 V
RM35UB330 | Complementary | control circuit frequency | 50...60 Hz +/- 15 %
RM35UB330 | Complementary | output contacts | 1 C/O + 1 C/O, 1 per threshold
RM35UB330 | Complementary | nominal output current | 5 A
RM35UB330 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM35UB330 | Complementary | hysteresis | 2 %
RM35UB330 | Complementary | delay at power up | 650 ms
RM35UB330 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35UB330 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM35UB330 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35UB330 | Complementary | response time | < 200 ms (in the event of a fault)
RM35UB330 | Complementary | quality labels | CE
RM35UB330 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35UB330 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM35UB330 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35UB330 | Complementary | operating position | Any position without derating
RM35UB330 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35UB330 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35UB330 | Complementary | housing material | Self-extinguishing plastic
RM35UB330 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35UB330 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35UB330 | Complementary | electrical durability | 10000 cycles
RM35UB330 | Complementary | mechanical durability | 30000000 cycles
RM35UB330 | Complementary | operating rate | <= 360 operations/hour full load
RM35UB330 | Complementary | safety reliability data | B10d = 300000 ¦ MTTFd = 319.6 years
RM35UB330 | Complementary | width | 35 mm
RM35UB330 | Complementary | net weight | 0.08 kg
RM35UB330 | Complementary | functionality | Overvoltage and undervoltage detection
RM35UB330 | Complementary | compatibility code | RM3
RM35UB330 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35UB330 | Environment | standards | EN/IEC 60255-1
RM35UB330 | Environment | product certifications | C-Tick ¦ GOST ¦ CSA ¦ GL ¦ UL
RM35UB330 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35UB330 | Environment | ambient air temperature for storage | -40…70 °C
RM35UB330 | Environment | ambient air temperature for operation | -20…50 °C
RM35UB330 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35UB330 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35UB330 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM35UB330 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35UB330 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35UB330 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35UB330 | Environment | non-dissipating shock wave | 4 kV
RM35UB330 | Offer Sustainability | Sustainable offer status | Green Premium product
RM35UB330 | Offer Sustainability | REACh Regulation | REACh Declaration
RM35UB330 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35UB330 | Offer Sustainability | Mercury free | Yes
RM35UB330 | Offer Sustainability | RoHS exemption information | Yes
RM35UB330 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35UB330 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35UB330 | Offer Sustainability | Circularity Profile | End of Life Information
RM35UB330 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35UB330 | Contractual warranty | Warranty | 18 months
RM35UB3N30 | Main | range of product | Zelio Control
RM35UB3N30 | Main | product or component type | Modular measurement and control relays
RM35UB3N30 | Main | relay type | Voltage control relay
RM35UB3N30 | Main | product specific application | For 3-phase supply
RM35UB3N30 | Main | relay name | RM35UB3
RM35UB3N30 | Main | relay monitored parameters | Absence of neutral ¦ Overvoltage and undervoltage between phases ¦ Overvoltage and undervoltage between neutral
RM35UB3N30 | Main | time delay | Adjustable 0.3...30 s, 0 + 10 % on crossing the threshold
RM35UB3N30 | Main | switching capacity in VA | 1250 VA
RM35UB3N30 | Main | minimum switching current | 10 mA at 5 V DC
RM35UB3N30 | Main | maximum switching current | 5 A AC/DC
RM35UB3N30 | Main | power consumption in VA | 0…3.9 VA AC
RM35UB3N30 | Main | measurement range | 114...329 V voltage AC 50/60 Hz
RM35UB3N30 | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM35UB3N30 | Complementary | reset time | 1500 ms time delay
RM35UB3N30 | Complementary | maximum switching voltage | 250 V AC/DC
RM35UB3N30 | Complementary | [Us] rated supply voltage | 120...277 V AC 50/60 Hz +/- 10 %
RM35UB3N30 | Complementary | supply voltage limits | 114…329 V AC
RM35UB3N30 | Complementary | voltage detection threshold | 114 V
RM35UB3N30 | Complementary | control circuit frequency | 50...60 Hz +/- 15 %
RM35UB3N30 | Complementary | output contacts | 1 C/O + 1 C/O, 1 per threshold
RM35UB3N30 | Complementary | nominal output current | 5 A
RM35UB3N30 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM35UB3N30 | Complementary | hysteresis | 2 %
RM35UB3N30 | Complementary | delay at power up | 650 ms
RM35UB3N30 | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM35UB3N30 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 1 % for time delay
RM35UB3N30 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35UB3N30 | Complementary | response time | < 200 ms (in the event of a fault)
RM35UB3N30 | Complementary | quality labels | CE
RM35UB3N30 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM35UB3N30 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM35UB3N30 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM35UB3N30 | Complementary | operating position | Any position without derating
RM35UB3N30 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...2 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM35UB3N30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35UB3N30 | Complementary | housing material | Self-extinguishing plastic
RM35UB3N30 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM35UB3N30 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM35UB3N30 | Complementary | electrical durability | 10000 cycles
RM35UB3N30 | Complementary | mechanical durability | 30000000 cycles
RM35UB3N30 | Complementary | operating rate | <= 360 operations/hour full load
RM35UB3N30 | Complementary | safety reliability data | B10d = 470000 ¦ MTTFd = 502.2 years
RM35UB3N30 | Complementary | width | 35 mm
RM35UB3N30 | Complementary | net weight | 0.08 kg
RM35UB3N30 | Complementary | functionality | Overvoltage and undervoltage detection
RM35UB3N30 | Complementary | compatibility code | RM3
RM35UB3N30 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM35UB3N30 | Environment | standards | EN/IEC 60255-1
RM35UB3N30 | Environment | product certifications | UL ¦ C-Tick ¦ GL ¦ CSA ¦ GOST
RM35UB3N30 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM35UB3N30 | Environment | ambient air temperature for storage | -40…70 °C
RM35UB3N30 | Environment | ambient air temperature for operation | -20…50 °C
RM35UB3N30 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM35UB3N30 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM35UB3N30 | Environment | shock resistance | 5 gn conforming to IEC 60068-2-27
RM35UB3N30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM35UB3N30 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM35UB3N30 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM35UB3N30 | Environment | non-dissipating shock wave | 4 kV
RM35UB3N30 | Offer Sustainability | Sustainable offer status | Green Premium product
RM35UB3N30 | Offer Sustainability | REACh Regulation | REACh Declaration
RM35UB3N30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35UB3N30 | Offer Sustainability | Mercury free | Yes
RM35UB3N30 | Offer Sustainability | RoHS exemption information | Yes
RM35UB3N30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35UB3N30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35UB3N30 | Offer Sustainability | Circularity Profile | End of Life Information
RM35UB3N30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35UB3N30 | Contractual warranty | Warranty | 18 months
RM22JA21MR | Main | range of product | Zelio Control
RM22JA21MR | Main | product or component type | Modular measurement and control relays
RM22JA21MR | Main | relay type | Current control relay
RM22JA21MR | Main | relay name | RM22JA
RM22JA21MR | Main | relay monitored parameters | Overcurrent detection
RM22JA21MR | Main | time delay type | Without
RM22JA21MR | Main | switching capacity in VA | 2000 VA
RM22JA21MR | Main | measurement range | 4...40 mA E1-M terminals ¦ 20...200 mA E2-M terminals ¦ 100...1000 mA E3-M terminals ¦ 4 mA...1 A current AC/DC 50/60 Hz
RM22JA21MR | Complementary | reset time | 1500 ms at maximum voltage
RM22JA21MR | Complementary | maximum switching voltage | 250 V AC
RM22JA21MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22JA21MR | Complementary | maximum switching current | 8 A AC
RM22JA21MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM22JA21MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22JA21MR | Complementary | operating limits | - 15 % + 10 % Un
RM22JA21MR | Complementary | power consumption in VA | 3.5 VA AC
RM22JA21MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22JA21MR | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22JA21MR | Complementary | resistance across terminals | 2.5 Ohm at E1-M terminals ¦ 0.5 Ohm at E2-M terminals ¦ 0.1 Ohm at E3-M terminals
RM22JA21MR | Complementary | output contacts | 2 C/O
RM22JA21MR | Complementary | nominal output current | 8 A
RM22JA21MR | Complementary | internal input resistance | 0.1 Ohm ¦ 2.5 Ohm ¦ 0.5 Ohm
RM22JA21MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22JA21MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22JA21MR | Complementary | setting accuracy of time delay | 10 %
RM22JA21MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22JA21MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
RM22JA21MR | Complementary | run-up delay at power-up | 0.3 s
RM22JA21MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22JA21MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 0.2 % for time delay
RM22JA21MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22JA21MR | Complementary | response time | <= 500 ms
RM22JA21MR | Complementary | threshold setting | 10...100 %
RM22JA21MR | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22JA21MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22JA21MR | Complementary | insulation | Between supply and measurement
RM22JA21MR | Complementary | mounting position | Any position
RM22JA21MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22JA21MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22JA21MR | Complementary | housing material | Self-extinguishing plastic
RM22JA21MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22JA21MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22JA21MR | Complementary | electrical durability | 100000 cycles
RM22JA21MR | Complementary | mechanical durability | 10000000 cycles
RM22JA21MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22JA21MR | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM22JA21MR | Complementary | contacts material | Cadmium free
RM22JA21MR | Complementary | width | 22.5 mm
RM22JA21MR | Complementary | net weight | 0.11 kg
RM22JA21MR | Environment | immunity to microbreaks | 50 ms
RM22JA21MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22JA21MR | Environment | standards | EN/IEC 60255-1
RM22JA21MR | Environment | product certifications | EAC ¦ CSA ¦ China RoHS ¦ CE ¦ RCM ¦ CCC ¦ UL ¦ GL
RM22JA21MR | Environment | ambient air temperature for storage | -40…70 °C
RM22JA21MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22JA21MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22JA21MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22JA21MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22JA21MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22JA21MR | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22JA21MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22JA21MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22JA21MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22JA21MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22JA21MR | Offer Sustainability | Mercury free | Yes
RM22JA21MR | Offer Sustainability | RoHS exemption information | Yes
RM22JA21MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22JA21MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22JA21MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22JA21MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22JA31MR | Main | range of product | Zelio Control
RM22JA31MR | Main | product or component type | Modular measurement and control relays
RM22JA31MR | Main | relay type | Current control relay
RM22JA31MR | Main | relay name | RM22JA
RM22JA31MR | Main | relay monitored parameters | Overcurrent or undercurrent detection ¦ Overcurrent or undercurrent in window mode
RM22JA31MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22JA31MR | Main | switching capacity in VA | 2000 VA
RM22JA31MR | Main | measurement range | 4...40 mA E1-M terminals ¦ 20...200 mA E2-M terminals ¦ 100...1000 mA E3-M terminals ¦ 4 mA...1 A current AC/DC 50/60 Hz
RM22JA31MR | Complementary | reset time | 1500 ms at maximum voltage
RM22JA31MR | Complementary | maximum switching voltage | 250 V AC
RM22JA31MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22JA31MR | Complementary | maximum switching current | 8 A AC
RM22JA31MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM22JA31MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22JA31MR | Complementary | operating limits | - 15 % + 10 % Un
RM22JA31MR | Complementary | power consumption in VA | 3.5 VA AC
RM22JA31MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22JA31MR | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22JA31MR | Complementary | resistance across terminals | 2.5 Ohm at E1-M terminals ¦ 0.5 Ohm at E2-M terminals ¦ 0.1 Ohm at E3-M terminals
RM22JA31MR | Complementary | output contacts | 2 C/O
RM22JA31MR | Complementary | nominal output current | 8 A
RM22JA31MR | Complementary | internal input resistance | 0.5 Ohm ¦ 2.5 Ohm ¦ 0.1 Ohm
RM22JA31MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22JA31MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22JA31MR | Complementary | setting accuracy of time delay | 10 P
RM22JA31MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22JA31MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection ¦ 3 % fixed of full scale for window mode
RM22JA31MR | Complementary | run-up delay at power-up | 0.3 s
RM22JA31MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22JA31MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 0.2 % for time delay
RM22JA31MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22JA31MR | Complementary | response time | <= 500 ms
RM22JA31MR | Complementary | threshold setting | 10...100 %
RM22JA31MR | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22JA31MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22JA31MR | Complementary | insulation | Between supply and measurement
RM22JA31MR | Complementary | mounting position | Any position
RM22JA31MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22JA31MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22JA31MR | Complementary | housing material | Self-extinguishing plastic
RM22JA31MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22JA31MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22JA31MR | Complementary | electrical durability | 100000 cycles
RM22JA31MR | Complementary | mechanical durability | 10000000 cycles
RM22JA31MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22JA31MR | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM22JA31MR | Complementary | contacts material | Cadmium free
RM22JA31MR | Complementary | width | 22.5 mm
RM22JA31MR | Complementary | net weight | 0.11 kg
RM22JA31MR | Environment | immunity to microbreaks | 50 ms
RM22JA31MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22JA31MR | Environment | standards | EN/IEC 60255-1
RM22JA31MR | Environment | product certifications | CSA ¦ CE ¦ EAC ¦ CCC ¦ GL ¦ RCM ¦ China RoHS ¦ UL
RM22JA31MR | Environment | ambient air temperature for storage | -40…70 °C
RM22JA31MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22JA31MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22JA31MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22JA31MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22JA31MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22JA31MR | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22JA31MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22JA31MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22JA31MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22JA31MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22JA31MR | Offer Sustainability | Mercury free | Yes
RM22JA31MR | Offer Sustainability | RoHS exemption information | Yes
RM22JA31MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22JA31MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22JA31MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22JA31MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22LA32MR | Main | range of product | Zelio Control
RM22LA32MR | Main | product or component type | Modular measurement and control relays
RM22LA32MR | Main | relay type | Level control relay
RM22LA32MR | Main | relay name | RM22L
RM22LA32MR | Main | relay monitored parameters | Detection by resistive probes
RM22LA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22LA32MR | Main | switching capacity in VA | 2000 VA
RM22LA32MR | Main | measurement range | 250 Ohm...1 MOhm
RM22LA32MR | Complementary | reset time | 1750 ms
RM22LA32MR | Complementary | maximum switching voltage | 250 V AC
RM22LA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22LA32MR | Complementary | maximum switching current | 8 A AC
RM22LA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22LA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22LA32MR | Complementary | operating limits | - 15 % + 10 % Un
RM22LA32MR | Complementary | power consumption in VA | 5 VA AC
RM22LA32MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22LA32MR | Complementary | output contacts | 2 C/O
RM22LA32MR | Complementary | nominal output current | 8 A
RM22LA32MR | Complementary | run-up delay at power-up | 2.5 s ¦ 0.6 s
RM22LA32MR | Complementary | maximum electrode voltage | 12 V AC
RM22LA32MR | Complementary | maximum electrode current | 1 mA
RM22LA32MR | Complementary | repeat accuracy | +/- 2 % for time delay
RM22LA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22LA32MR | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) ¦ 5...100 kOhm St (Standard Sensitivity) ¦ 50...1000 kOhm HS (High Sensitivity)
RM22LA32MR | Complementary | sensitivity adjustment | 5…100 %
RM22LA32MR | Complementary | maximum supply current for sensors | 1 mA
RM22LA32MR | Complementary | maximum cable distance between devices | 1000 m between probe and delay
RM22LA32MR | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable ¦ 2.2 nF at St (Standard Sensitivity) for probe cable ¦ 4.7 nF at LS (Low Sensitivity) for probe cable
RM22LA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22LA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22LA32MR | Complementary | insulation | Between supply and measurement
RM22LA32MR | Complementary | mounting position | Any position
RM22LA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22LA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22LA32MR | Complementary | housing material | Self-extinguishing plastic
RM22LA32MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22LA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22LA32MR | Complementary | electrical durability | 100000 cycles
RM22LA32MR | Complementary | mechanical durability | 10000000 cycles
RM22LA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22LA32MR | Complementary | safety reliability data | MTTFd = 182.6 years ¦ B10d = 170000
RM22LA32MR | Complementary | contacts material | Cadmium free
RM22LA32MR | Complementary | width | 22.5 mm
RM22LA32MR | Complementary | net weight | 0.11 kg
RM22LA32MR | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM22LA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22LA32MR | Environment | standards | EN/IEC 60255-1
RM22LA32MR | Environment | product certifications | China RoHS ¦ UL ¦ RCM ¦ CSA ¦ GL ¦ CCC ¦ CE ¦ EAC
RM22LA32MR | Environment | ambient air temperature for storage | -40…70 °C
RM22LA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22LA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22LA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22LA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22LA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22LA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22LA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22LA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22LA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22LA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22LA32MR | Offer Sustainability | Mercury free | Yes
RM22LA32MR | Offer Sustainability | RoHS exemption information | Yes
RM22LA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22LA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22LA32MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22LA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22LA32MT | Main | range of product | Zelio Control
RM22LA32MT | Main | product or component type | Modular measurement and control relays
RM22LA32MT | Main | relay type | Level control relay
RM22LA32MT | Main | relay name | RM22L
RM22LA32MT | Main | relay monitored parameters | Detection by resistive probes
RM22LA32MT | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22LA32MT | Main | switching capacity in VA | 2000 VA
RM22LA32MT | Main | measurement range | 250 Ohm...1 MOhm
RM22LA32MT | Complementary | reset time | 1750 ms
RM22LA32MT | Complementary | maximum switching voltage | 250 V AC
RM22LA32MT | Complementary | minimum switching current | 10 mA at 5 V DC
RM22LA32MT | Complementary | maximum switching current | 8 A AC
RM22LA32MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
RM22LA32MT | Complementary | supply voltage limits | 323…456.5 V AC
RM22LA32MT | Complementary | operating limits | - 15 % + 10 % Un
RM22LA32MT | Complementary | power consumption in VA | 8 VA AC
RM22LA32MT | Complementary | output contacts | 2 C/O
RM22LA32MT | Complementary | nominal output current | 8 A
RM22LA32MT | Complementary | run-up delay at power-up | 2.5 s ¦ 0.6 s
RM22LA32MT | Complementary | maximum electrode voltage | 12 V AC
RM22LA32MT | Complementary | maximum electrode current | 1 mA
RM22LA32MT | Complementary | repeat accuracy | +/- 2 % for time delay
RM22LA32MT | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22LA32MT | Complementary | sensitivity scale | 0.25...5 kOhm LS (Low Sensitivity) ¦ 5...100 kOhm St (Standard Sensitivity) ¦ 50...1000 kOhm HS (High Sensitivity)
RM22LA32MT | Complementary | sensitivity adjustment | 5…100 %
RM22LA32MT | Complementary | maximum supply current for sensors | 1 mA
RM22LA32MT | Complementary | maximum cable distance between devices | 1000 m between probe and delay
RM22LA32MT | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable ¦ 2.2 nF at St (Standard Sensitivity) for probe cable ¦ 4.7 nF at LS (Low Sensitivity) for probe cable
RM22LA32MT | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22LA32MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22LA32MT | Complementary | insulation | Between supply and measurement
RM22LA32MT | Complementary | mounting position | Any position
RM22LA32MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22LA32MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22LA32MT | Complementary | housing material | Self-extinguishing plastic
RM22LA32MT | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22LA32MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22LA32MT | Complementary | electrical durability | 100000 cycles
RM22LA32MT | Complementary | mechanical durability | 10000000 cycles
RM22LA32MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22LA32MT | Complementary | safety reliability data | MTTFd = 182.6 years ¦ B10d = 170000
RM22LA32MT | Complementary | contacts material | Cadmium free
RM22LA32MT | Complementary | width | 22.5 mm
RM22LA32MT | Complementary | net weight | 0.11 kg
RM22LA32MT | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM22LA32MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22LA32MT | Environment | standards | EN/IEC 60255-1
RM22LA32MT | Environment | product certifications | GL ¦ UL ¦ CCC ¦ EAC ¦ RCM ¦ CE ¦ CSA ¦ China RoHS
RM22LA32MT | Environment | ambient air temperature for storage | -40…70 °C
RM22LA32MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22LA32MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22LA32MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22LA32MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22LA32MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22LA32MT | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22LA32MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22LA32MT | Offer Sustainability | Sustainable offer status | Green Premium product
RM22LA32MT | Offer Sustainability | REACh Regulation | REACh Declaration
RM22LA32MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22LA32MT | Offer Sustainability | Mercury free | Yes
RM22LA32MT | Offer Sustainability | RoHS exemption information | Yes
RM22LA32MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22LA32MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22LA32MT | Offer Sustainability | Circularity Profile | End of Life Information
RM22LA32MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22LG11MR | Main | range of product | Zelio Control
RM22LG11MR | Main | product or component type | Modular measurement and control relays
RM22LG11MR | Main | relay type | Level control relay
RM22LG11MR | Main | relay name | RM22L
RM22LG11MR | Main | relay monitored parameters | Detection by resistive probes
RM22LG11MR | Main | time delay type | Without
RM22LG11MR | Main | switching capacity in VA | 2000 VA
RM22LG11MR | Main | measurement range | 5...100 kOhm
RM22LG11MR | Complementary | reset time | 1750 ms
RM22LG11MR | Complementary | maximum switching voltage | 250 V AC
RM22LG11MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22LG11MR | Complementary | maximum switching current | 8 A AC
RM22LG11MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22LG11MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22LG11MR | Complementary | operating limits | - 15 % + 10 % Un
RM22LG11MR | Complementary | power consumption in VA | 5 VA AC
RM22LG11MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22LG11MR | Complementary | output contacts | 2 C/O
RM22LG11MR | Complementary | nominal output current | 8 A
RM22LG11MR | Complementary | run-up delay at power-up | 0.6 s
RM22LG11MR | Complementary | maximum electrode voltage | 12 V AC
RM22LG11MR | Complementary | maximum electrode current | 1 mA
RM22LG11MR | Complementary | repeat accuracy | +/- 2 % for time delay
RM22LG11MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22LG11MR | Complementary | sensitivity scale | 5...100 kOhm St (Standard Sensitivity)
RM22LG11MR | Complementary | sensitivity adjustment | 5…100 %
RM22LG11MR | Complementary | maximum supply current for sensors | 1 mA
RM22LG11MR | Complementary | maximum cable distance between devices | 1000 m between probe and delay
RM22LG11MR | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable ¦ 2.2 nF at St (Standard Sensitivity) for probe cable ¦ 4.7 nF at LS (Low Sensitivity) for probe cable
RM22LG11MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22LG11MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22LG11MR | Complementary | insulation | Between supply and measurement
RM22LG11MR | Complementary | mounting position | Any position
RM22LG11MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22LG11MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22LG11MR | Complementary | housing material | Self-extinguishing plastic
RM22LG11MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22LG11MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22LG11MR | Complementary | electrical durability | 100000 cycles
RM22LG11MR | Complementary | mechanical durability | 10000000 cycles
RM22LG11MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22LG11MR | Complementary | safety reliability data | B10d = 120000 ¦ MTTFd = 125.5 years
RM22LG11MR | Complementary | contacts material | Cadmium free
RM22LG11MR | Complementary | width | 22.5 mm
RM22LG11MR | Complementary | net weight | 0.1 kg
RM22LG11MR | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM22LG11MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22LG11MR | Environment | standards | EN/IEC 60255-1
RM22LG11MR | Environment | product certifications | GL ¦ RCM ¦ CCC ¦ CSA ¦ UL ¦ China RoHS ¦ EAC ¦ CE
RM22LG11MR | Environment | ambient air temperature for storage | -40…70 °C
RM22LG11MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22LG11MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22LG11MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22LG11MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22LG11MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22LG11MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22LG11MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22LG11MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22LG11MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22LG11MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22LG11MR | Offer Sustainability | Mercury free | Yes
RM22LG11MR | Offer Sustainability | RoHS exemption information | Yes
RM22LG11MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22LG11MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22LG11MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22LG11MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22LG11MT | Main | range of product | Zelio Control
RM22LG11MT | Main | product or component type | Modular measurement and control relays
RM22LG11MT | Main | relay type | Level control relay
RM22LG11MT | Main | relay name | RM22L
RM22LG11MT | Main | relay monitored parameters | Detection by resistive probes
RM22LG11MT | Main | time delay type | Without
RM22LG11MT | Main | switching capacity in VA | 2000 VA
RM22LG11MT | Main | measurement range | 5...100 kOhm
RM22LG11MT | Complementary | reset time | 1750 ms
RM22LG11MT | Complementary | maximum switching voltage | 250 V AC
RM22LG11MT | Complementary | minimum switching current | 10 mA at 5 V DC
RM22LG11MT | Complementary | maximum switching current | 8 A AC
RM22LG11MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
RM22LG11MT | Complementary | supply voltage limits | 323…456.5 V AC
RM22LG11MT | Complementary | operating limits | - 15 % + 10 % Un
RM22LG11MT | Complementary | power consumption in VA | 8 VA AC
RM22LG11MT | Complementary | output contacts | 2 C/O
RM22LG11MT | Complementary | nominal output current | 8 A
RM22LG11MT | Complementary | run-up delay at power-up | 0.6 s
RM22LG11MT | Complementary | maximum electrode voltage | 12 V AC
RM22LG11MT | Complementary | maximum electrode current | 1 mA
RM22LG11MT | Complementary | repeat accuracy | +/- 2 % for time delay
RM22LG11MT | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22LG11MT | Complementary | sensitivity scale | 5...100 kOhm St (Standard Sensitivity)
RM22LG11MT | Complementary | sensitivity adjustment | 5…100 %
RM22LG11MT | Complementary | maximum supply current for sensors | 1 mA
RM22LG11MT | Complementary | maximum cable distance between devices | 1000 m between probe and delay
RM22LG11MT | Complementary | cable capacitance | 1 nF at HS (High Sensitivity) for probe cable ¦ 2.2 nF at St (Standard Sensitivity) for probe cable ¦ 4.7 nF at LS (Low Sensitivity) for probe cable
RM22LG11MT | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22LG11MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22LG11MT | Complementary | insulation | Between supply and measurement
RM22LG11MT | Complementary | mounting position | Any position
RM22LG11MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22LG11MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22LG11MT | Complementary | housing material | Self-extinguishing plastic
RM22LG11MT | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22LG11MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22LG11MT | Complementary | electrical durability | 100000 cycles
RM22LG11MT | Complementary | mechanical durability | 10000000 cycles
RM22LG11MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22LG11MT | Complementary | safety reliability data | MTTFd = 125.5 years ¦ B10d = 120000
RM22LG11MT | Complementary | contacts material | Cadmium free
RM22LG11MT | Complementary | width | 22.5 mm
RM22LG11MT | Complementary | net weight | 0.1 kg
RM22LG11MT | Environment | immunity to microbreaks | 100 ms DC ¦ 90 ms AC
RM22LG11MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22LG11MT | Environment | standards | EN/IEC 60255-1
RM22LG11MT | Environment | product certifications | CSA ¦ GL ¦ RCM ¦ UL ¦ China RoHS ¦ EAC ¦ CE ¦ CCC
RM22LG11MT | Environment | ambient air temperature for storage | -40…70 °C
RM22LG11MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22LG11MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22LG11MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22LG11MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22LG11MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22LG11MT | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22LG11MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22LG11MT | Offer Sustainability | Sustainable offer status | Green Premium product
RM22LG11MT | Offer Sustainability | REACh Regulation | REACh Declaration
RM22LG11MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22LG11MT | Offer Sustainability | Mercury free | Yes
RM22LG11MT | Offer Sustainability | RoHS exemption information | Yes
RM22LG11MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22LG11MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22LG11MT | Offer Sustainability | Circularity Profile | End of Life Information
RM22LG11MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TA31 | Main | range of product | Zelio Control
RM22TA31 | Main | product or component type | Modular measurement and control relays
RM22TA31 | Main | relay type | Control relay
RM22TA31 | Main | network number of phases | 3 phases
RM22TA31 | Main | relay name | RM22TA
RM22TA31 | Main | relay monitored parameters | Asymmetry ¦ Phase failure detection ¦ Phase sequence
RM22TA31 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22TA31 | Main | switching capacity in VA | 2000 VA
RM22TA31 | Main | measurement range | 200...240 V voltage AC
RM22TA31 | Complementary | reset time | 1500 ms at maximum voltage
RM22TA31 | Complementary | maximum switching voltage | 250 V AC
RM22TA31 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TA31 | Complementary | maximum switching current | 8 A AC
RM22TA31 | Complementary | [Us] rated supply voltage | 200...240 V AC
RM22TA31 | Complementary | supply voltage limits | 160…288 V AC
RM22TA31 | Complementary | operating limits | - 20 % + 20 % Un
RM22TA31 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
RM22TA31 | Complementary | voltage detection threshold | < 100 V AC
RM22TA31 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TA31 | Complementary | output contacts | 2 C/O
RM22TA31 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TA31 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TA31 | Complementary | setting accuracy of time delay | 10 %
RM22TA31 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TA31 | Complementary | hysteresis | 2 % fixed of selectable
RM22TA31 | Complementary | run-up delay at power-up | 650 ms
RM22TA31 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TA31 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TA31 | Complementary | voltage range | 200...240 V phase to phase
RM22TA31 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM22TA31 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 3 % for time delay
RM22TA31 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TA31 | Complementary | response time | <= 300 ms
RM22TA31 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TA31 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TA31 | Complementary | mounting position | Any position
RM22TA31 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TA31 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TA31 | Complementary | housing material | Self-extinguishing plastic
RM22TA31 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TA31 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TA31 | Complementary | electrical durability | 100000 cycles
RM22TA31 | Complementary | mechanical durability | 10000000 cycles
RM22TA31 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TA31 | Complementary | safety reliability data | MTTFd = 388.1 years ¦ B10d = 350000
RM22TA31 | Complementary | contacts material | Cadmium free
RM22TA31 | Complementary | width | 22.5 mm
RM22TA31 | Complementary | net weight | 0.09 kg
RM22TA31 | Environment | immunity to microbreaks | 10 ms
RM22TA31 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TA31 | Environment | standards | EN/IEC 60255-1
RM22TA31 | Environment | product certifications | GL ¦ EAC ¦ China RoHS ¦ UL ¦ CSA ¦ RCM ¦ CCC ¦ CE
RM22TA31 | Environment | ambient air temperature for storage | -40…70 °C
RM22TA31 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TA31 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TA31 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TA31 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TA31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TA31 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TA31 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TA31 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TA31 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TA31 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TA31 | Offer Sustainability | Mercury free | Yes
RM22TA31 | Offer Sustainability | RoHS exemption information | Yes
RM22TA31 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TA31 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TA31 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TA31 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TA33 | Main | range of product | Zelio Control
RM22TA33 | Main | product or component type | Modular measurement and control relays
RM22TA33 | Main | relay type | Control relay
RM22TA33 | Main | network number of phases | 3 phases
RM22TA33 | Main | relay name | RM22TA
RM22TA33 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection ¦ Asymmetry
RM22TA33 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22TA33 | Main | switching capacity in VA | 2000 VA
RM22TA33 | Main | measurement range | 380...480 V voltage AC
RM22TA33 | Complementary | reset time | 1500 ms at maximum voltage
RM22TA33 | Complementary | maximum switching voltage | 250 V AC
RM22TA33 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TA33 | Complementary | maximum switching current | 8 A AC
RM22TA33 | Complementary | [Us] rated supply voltage | 380...480 V AC
RM22TA33 | Complementary | supply voltage limits | 304…576 V AC
RM22TA33 | Complementary | operating limits | - 20 % + 20 % Un
RM22TA33 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
RM22TA33 | Complementary | voltage detection threshold | < 100 V AC
RM22TA33 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TA33 | Complementary | output contacts | 2 C/O
RM22TA33 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TA33 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TA33 | Complementary | setting accuracy of time delay | 10 %
RM22TA33 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TA33 | Complementary | hysteresis | 2 % fixed of selectable
RM22TA33 | Complementary | run-up delay at power-up | 650 ms
RM22TA33 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TA33 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TA33 | Complementary | voltage range | 380...480 V phase to phase
RM22TA33 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM22TA33 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 3 % for time delay
RM22TA33 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TA33 | Complementary | response time | <= 300 ms
RM22TA33 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TA33 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TA33 | Complementary | mounting position | Any position
RM22TA33 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TA33 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TA33 | Complementary | housing material | Self-extinguishing plastic
RM22TA33 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TA33 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TA33 | Complementary | electrical durability | 100000 cycles
RM22TA33 | Complementary | mechanical durability | 10000000 cycles
RM22TA33 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TA33 | Complementary | safety reliability data | MTTFd = 388.1 years ¦ B10d = 350000
RM22TA33 | Complementary | contacts material | Cadmium free
RM22TA33 | Complementary | width | 22.5 mm
RM22TA33 | Complementary | net weight | 0.09 kg
RM22TA33 | Environment | immunity to microbreaks | 10 ms
RM22TA33 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TA33 | Environment | standards | EN/IEC 60255-1
RM22TA33 | Environment | product certifications | GL ¦ EAC ¦ CCC ¦ CE ¦ CSA ¦ China RoHS ¦ UL ¦ RCM
RM22TA33 | Environment | ambient air temperature for storage | -40…70 °C
RM22TA33 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TA33 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TA33 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TA33 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TA33 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TA33 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TA33 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TA33 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TA33 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TA33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TA33 | Offer Sustainability | Mercury free | Yes
RM22TA33 | Offer Sustainability | RoHS exemption information | Yes
RM22TA33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TA33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TA33 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TA33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TG20 | Main | range of product | Zelio Control
RM22TG20 | Main | product or component type | Modular measurement and control relays
RM22TG20 | Main | relay type | Control relay
RM22TG20 | Main | network number of phases | 3 phases
RM22TG20 | Main | relay name | RM22TG
RM22TG20 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection (2 or more phase cut)
RM22TG20 | Main | time delay type | Without
RM22TG20 | Main | switching capacity in VA | 2000 VA
RM22TG20 | Main | measurement range | 183...528 V voltage AC
RM22TG20 | Complementary | reset time | 1500 ms at maximum voltage
RM22TG20 | Complementary | maximum switching voltage | 250 V AC
RM22TG20 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TG20 | Complementary | maximum switching current | 8 A AC
RM22TG20 | Complementary | [Us] rated supply voltage | 208...480 V AC
RM22TG20 | Complementary | supply voltage limits | 183…528 V AC
RM22TG20 | Complementary | operating limits | 183...528 V AC
RM22TG20 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
RM22TG20 | Complementary | voltage detection threshold | < 100 V AC
RM22TG20 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TG20 | Complementary | output contacts | 2 C/O
RM22TG20 | Complementary | run-up delay at power-up | 650 ms
RM22TG20 | Complementary | response time | <= 200 ms
RM22TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TG20 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TG20 | Complementary | mounting position | Any position
RM22TG20 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TG20 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TG20 | Complementary | housing material | Self-extinguishing plastic
RM22TG20 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TG20 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TG20 | Complementary | electrical durability | 100000 cycles
RM22TG20 | Complementary | mechanical durability | 10000000 cycles
RM22TG20 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TG20 | Complementary | safety reliability data | MTTFd = 924.6 years ¦ B10d = 850000
RM22TG20 | Complementary | contacts material | Cadmium free
RM22TG20 | Complementary | width | 22.5 mm
RM22TG20 | Complementary | net weight | 0.09 kg
RM22TG20 | Environment | immunity to microbreaks | 10 ms
RM22TG20 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TG20 | Environment | standards | EN/IEC 60255-1
RM22TG20 | Environment | product certifications | CE ¦ EAC ¦ China RoHS ¦ RCM ¦ GL ¦ CSA ¦ UL ¦ CCC
RM22TG20 | Environment | ambient air temperature for storage | -40…70 °C
RM22TG20 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TG20 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TG20 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TG20 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TG20 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TG20 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TG20 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TG20 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TG20 | Offer Sustainability | Mercury free | Yes
RM22TG20 | Offer Sustainability | RoHS exemption information | Yes
RM22TG20 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TG20 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TG20 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TG20 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TR31 | Main | range of product | Zelio Control
RM22TR31 | Main | product or component type | Modular measurement and control relays
RM22TR31 | Main | relay type | Control relay
RM22TR31 | Main | network number of phases | 3 phases
RM22TR31 | Main | relay name | RM22TR
RM22TR31 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection ¦ Overvoltage and undervoltage detection
RM22TR31 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22TR31 | Main | switching capacity in VA | 2000 VA
RM22TR31 | Main | measurement range | 200...240 V voltage AC
RM22TR31 | Complementary | reset time | 1500 ms at maximum voltage
RM22TR31 | Complementary | maximum switching voltage | 250 V AC
RM22TR31 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TR31 | Complementary | maximum switching current | 8 A AC
RM22TR31 | Complementary | [Us] rated supply voltage | 200...240 V AC
RM22TR31 | Complementary | supply voltage limits | 160…288 V AC
RM22TR31 | Complementary | operating limits | - 20 % + 20 % Un
RM22TR31 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
RM22TR31 | Complementary | voltage detection threshold | < 100 V AC
RM22TR31 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TR31 | Complementary | output contacts | 2 C/O
RM22TR31 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TR31 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TR31 | Complementary | setting accuracy of time delay | 10 %
RM22TR31 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TR31 | Complementary | hysteresis | 2 % fixed of selectable
RM22TR31 | Complementary | run-up delay at power-up | 650 ms
RM22TR31 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TR31 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TR31 | Complementary | voltage range | 200...240 V phase to phase
RM22TR31 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 3 % for time delay
RM22TR31 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TR31 | Complementary | response time | <= 300 ms
RM22TR31 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TR31 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TR31 | Complementary | mounting position | Any position
RM22TR31 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TR31 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TR31 | Complementary | housing material | Self-extinguishing plastic
RM22TR31 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TR31 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TR31 | Complementary | electrical durability | 100000 cycles
RM22TR31 | Complementary | mechanical durability | 10000000 cycles
RM22TR31 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TR31 | Complementary | safety reliability data | MTTFd = 388.1 years ¦ B10d = 350000
RM22TR31 | Complementary | contacts material | Cadmium free
RM22TR31 | Complementary | width | 22.5 mm
RM22TR31 | Complementary | net weight | 0.09 kg
RM22TR31 | Environment | immunity to microbreaks | 10 ms
RM22TR31 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TR31 | Environment | standards | EN/IEC 60255-1
RM22TR31 | Environment | product certifications | CSA ¦ CCC ¦ EAC ¦ China RoHS ¦ RCM ¦ CE ¦ GL ¦ UL
RM22TR31 | Environment | ambient air temperature for storage | -40…70 °C
RM22TR31 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TR31 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TR31 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TR31 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TR31 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TR31 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TR31 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TR31 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TR31 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TR31 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TR31 | Offer Sustainability | Mercury free | Yes
RM22TR31 | Offer Sustainability | RoHS exemption information | Yes
RM22TR31 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TR31 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TR31 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TR31 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TR33 | Main | range of product | Zelio Control
RM22TR33 | Main | product or component type | Modular measurement and control relays
RM22TR33 | Main | relay type | Control relay
RM22TR33 | Main | network number of phases | 3 phases
RM22TR33 | Main | relay name | RM22TR
RM22TR33 | Main | relay monitored parameters | Overvoltage and undervoltage detection ¦ Phase sequence ¦ Phase failure detection
RM22TR33 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22TR33 | Main | switching capacity in VA | 2000 VA
RM22TR33 | Main | measurement range | 380...480 V voltage AC
RM22TR33 | Complementary | reset time | 1500 ms at maximum voltage
RM22TR33 | Complementary | maximum switching voltage | 250 V AC
RM22TR33 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TR33 | Complementary | maximum switching current | 8 A AC
RM22TR33 | Complementary | [Us] rated supply voltage | 380...480 V AC
RM22TR33 | Complementary | supply voltage limits | 304…576 V AC
RM22TR33 | Complementary | operating limits | - 20 % + 20 % Un
RM22TR33 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
RM22TR33 | Complementary | voltage detection threshold | < 100 V AC
RM22TR33 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TR33 | Complementary | output contacts | 2 C/O
RM22TR33 | Complementary | nominal output current | 8 A
RM22TR33 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TR33 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TR33 | Complementary | setting accuracy of time delay | 10 P
RM22TR33 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TR33 | Complementary | hysteresis | 2 % fixed of selectable
RM22TR33 | Complementary | run-up delay at power-up | 650 ms
RM22TR33 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TR33 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TR33 | Complementary | voltage range | 380...480 V phase to phase
RM22TR33 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 3 % for time delay
RM22TR33 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TR33 | Complementary | response time | <= 300 ms
RM22TR33 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TR33 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TR33 | Complementary | mounting position | Any position
RM22TR33 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TR33 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TR33 | Complementary | housing material | Self-extinguishing plastic
RM22TR33 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TR33 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TR33 | Complementary | electrical durability | 100000 cycles
RM22TR33 | Complementary | mechanical durability | 10000000 cycles
RM22TR33 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TR33 | Complementary | safety reliability data | MTTFd = 388.1 years ¦ B10d = 350000
RM22TR33 | Complementary | contacts material | Cadmium free
RM22TR33 | Complementary | width | 22.5 mm
RM22TR33 | Complementary | net weight | 0.09 kg
RM22TR33 | Environment | immunity to microbreaks | 10 ms
RM22TR33 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TR33 | Environment | standards | EN/IEC 60255-1
RM22TR33 | Environment | product certifications | GL ¦ China RoHS ¦ CSA ¦ RCM ¦ CE ¦ EAC ¦ CCC ¦ UL
RM22TR33 | Environment | ambient air temperature for storage | -40…70 °C
RM22TR33 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TR33 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TR33 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TR33 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TR33 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TR33 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TR33 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TR33 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TR33 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TR33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TR33 | Offer Sustainability | Mercury free | Yes
RM22TR33 | Offer Sustainability | RoHS exemption information | Yes
RM22TR33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TR33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TR33 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TR33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TU21 | Main | range of product | Zelio Control
RM22TU21 | Main | product or component type | Modular measurement and control relays
RM22TU21 | Main | relay type | Control relay
RM22TU21 | Main | network number of phases | 3 phases
RM22TU21 | Main | relay name | RM22TR
RM22TU21 | Main | relay monitored parameters | Undervoltage detection ¦ Phase sequence ¦ Phase failure detection
RM22TU21 | Main | time delay type | Without
RM22TU21 | Main | switching capacity in VA | 2000 VA
RM22TU21 | Main | measurement range | 200...240 V voltage AC
RM22TU21 | Complementary | reset time | 1500 ms at maximum voltage
RM22TU21 | Complementary | maximum switching voltage | 250 V AC
RM22TU21 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TU21 | Complementary | maximum switching current | 8 A AC
RM22TU21 | Complementary | [Us] rated supply voltage | 200...240 V AC
RM22TU21 | Complementary | supply voltage limits | 160…288 V AC
RM22TU21 | Complementary | operating limits | - 20 % + 20 % Un
RM22TU21 | Complementary | power consumption in VA | 10 VA at 240 V AC 60 Hz
RM22TU21 | Complementary | voltage detection threshold | < 100 V AC
RM22TU21 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TU21 | Complementary | output contacts | 2 C/O
RM22TU21 | Complementary | nominal output current | 8 A
RM22TU21 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TU21 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TU21 | Complementary | setting accuracy of time delay | 10 %
RM22TU21 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TU21 | Complementary | hysteresis | 2 % fixed of selectable
RM22TU21 | Complementary | run-up delay at power-up | 650 ms
RM22TU21 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TU21 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TU21 | Complementary | voltage range | 200...240 V phase to phase
RM22TU21 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM22TU21 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TU21 | Complementary | response time | <= 300 ms
RM22TU21 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TU21 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TU21 | Complementary | mounting position | Any position
RM22TU21 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TU21 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TU21 | Complementary | housing material | Self-extinguishing plastic
RM22TU21 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TU21 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TU21 | Complementary | electrical durability | 100000 cycles
RM22TU21 | Complementary | mechanical durability | 10000000 cycles
RM22TU21 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TU21 | Complementary | safety reliability data | B10d = 350000 ¦ MTTFd = 388.1 years
RM22TU21 | Complementary | contacts material | Cadmium free
RM22TU21 | Complementary | width | 22.5 mm
RM22TU21 | Complementary | net weight | 0.09 kg
RM22TU21 | Environment | immunity to microbreaks | 10 ms
RM22TU21 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TU21 | Environment | standards | EN/IEC 60255-1
RM22TU21 | Environment | product certifications | RCM ¦ CE ¦ China RoHS ¦ CSA ¦ GL ¦ CCC ¦ UL ¦ EAC
RM22TU21 | Environment | ambient air temperature for storage | -40…70 °C
RM22TU21 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TU21 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TU21 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TU21 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TU21 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TU21 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TU21 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TU21 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TU21 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TU21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TU21 | Offer Sustainability | Mercury free | Yes
RM22TU21 | Offer Sustainability | RoHS exemption information | Yes
RM22TU21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TU21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TU21 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TU21 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22TU23 | Main | range of product | Zelio Control
RM22TU23 | Main | product or component type | Modular measurement and control relays
RM22TU23 | Main | relay type | Control relay
RM22TU23 | Main | network number of phases | 3 phases
RM22TU23 | Main | relay name | RM22TR
RM22TU23 | Main | relay monitored parameters | Undervoltage detection ¦ Phase sequence ¦ Phase failure detection
RM22TU23 | Main | time delay type | Without
RM22TU23 | Main | switching capacity in VA | 2000 VA
RM22TU23 | Main | measurement range | 380...480 V voltage AC
RM22TU23 | Complementary | reset time | 1500 ms at maximum voltage
RM22TU23 | Complementary | maximum switching voltage | 250 V AC
RM22TU23 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22TU23 | Complementary | maximum switching current | 8 A AC
RM22TU23 | Complementary | [Us] rated supply voltage | 380...480 V AC
RM22TU23 | Complementary | supply voltage limits | 304…576 V AC
RM22TU23 | Complementary | operating limits | - 20 % + 20 % Un
RM22TU23 | Complementary | power consumption in VA | 15 VA at 480 V AC 60 Hz
RM22TU23 | Complementary | voltage detection threshold | < 100 V AC
RM22TU23 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22TU23 | Complementary | output contacts | 2 C/O
RM22TU23 | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM22TU23 | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TU23 | Complementary | setting accuracy of time delay | 10 %
RM22TU23 | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM22TU23 | Complementary | hysteresis | 2 % fixed of selectable
RM22TU23 | Complementary | run-up delay at power-up | 650 ms
RM22TU23 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM22TU23 | Complementary | threshold adjustment voltage | 2...20 % of Un selected
RM22TU23 | Complementary | voltage range | 380...480 V phase to phase
RM22TU23 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM22TU23 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ < 0.05 %/°C with temperature variation
RM22TU23 | Complementary | response time | <= 300 ms
RM22TU23 | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM22TU23 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22TU23 | Complementary | mounting position | Any position
RM22TU23 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22TU23 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22TU23 | Complementary | housing material | Self-extinguishing plastic
RM22TU23 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22TU23 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22TU23 | Complementary | electrical durability | 100000 cycles
RM22TU23 | Complementary | mechanical durability | 10000000 cycles
RM22TU23 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22TU23 | Complementary | safety reliability data | MTTFd = 388.1 years ¦ B10d = 350000
RM22TU23 | Complementary | contacts material | Cadmium free
RM22TU23 | Complementary | width | 22.5 mm
RM22TU23 | Complementary | net weight | 0.09 kg
RM22TU23 | Environment | immunity to microbreaks | 10 ms
RM22TU23 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22TU23 | Environment | standards | EN/IEC 60255-1
RM22TU23 | Environment | product certifications | CSA ¦ RCM ¦ UL ¦ GL ¦ China RoHS ¦ CE ¦ CCC ¦ EAC
RM22TU23 | Environment | ambient air temperature for storage | -40…70 °C
RM22TU23 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22TU23 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22TU23 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22TU23 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22TU23 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22TU23 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM22TU23 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22TU23 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22TU23 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22TU23 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22TU23 | Offer Sustainability | Mercury free | Yes
RM22TU23 | Offer Sustainability | RoHS exemption information | Yes
RM22TU23 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22TU23 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22TU23 | Offer Sustainability | Circularity Profile | End of Life Information
RM22TU23 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA21MR | Main | range of product | Zelio Control
RM22UA21MR | Main | product or component type | Modular measurement and control relays
RM22UA21MR | Main | relay type | Voltage control relay
RM22UA21MR | Main | network number of phases | 1 phase
RM22UA21MR | Main | supply circuit type | DC
RM22UA21MR | Main | relay name | RM22UA
RM22UA21MR | Main | relay monitored parameters | Overvoltage detection
RM22UA21MR | Main | time delay type | Without
RM22UA21MR | Main | switching capacity in VA | 2000 VA
RM22UA21MR | Main | measurement range | 50 mV...5 V voltage AC/DC 50/60 Hz
RM22UA21MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA21MR | Complementary | maximum switching voltage | 250 V AC
RM22UA21MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA21MR | Complementary | maximum switching current | 8 A AC
RM22UA21MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA21MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA21MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA21MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA21MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA21MR | Complementary | resistance across terminals | 30 kOhm at E2-M terminals ¦ 5 kOhm at E1-M terminals ¦ 50 kOhm at E3-M terminals
RM22UA21MR | Complementary | output contacts | 2 C/O
RM22UA21MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
RM22UA21MR | Complementary | run-up delay at power-up | 600 ms
RM22UA21MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA21MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM22UA21MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA21MR | Complementary | response time | <= 500 ms
RM22UA21MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA21MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA21MR | Complementary | insulation | Between supply and measurement
RM22UA21MR | Complementary | mounting position | Any position
RM22UA21MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA21MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA21MR | Complementary | housing material | Self-extinguishing plastic
RM22UA21MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA21MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA21MR | Complementary | electrical durability | 100000 cycles
RM22UA21MR | Complementary | mechanical durability | 10000000 cycles
RM22UA21MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA21MR | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM22UA21MR | Complementary | contacts material | Cadmium free
RM22UA21MR | Complementary | width | 22.5 mm
RM22UA21MR | Complementary | net weight | 0.11 kg
RM22UA21MR | Environment | immunity to microbreaks | 10 ms
RM22UA21MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA21MR | Environment | standards | EN/IEC 60255-1
RM22UA21MR | Environment | product certifications | UL ¦ China RoHS ¦ EAC ¦ CSA ¦ GL ¦ CCC ¦ RCM ¦ CE
RM22UA21MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA21MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA21MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA21MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA21MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA21MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA21MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA21MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA21MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA21MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA21MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA21MR | Offer Sustainability | Mercury free | Yes
RM22UA21MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA21MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA21MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA21MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA21MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA22MR | Main | range of product | Zelio Control
RM22UA22MR | Main | product or component type | Modular measurement and control relays
RM22UA22MR | Main | relay type | Voltage control relay
RM22UA22MR | Main | network number of phases | 1 phase
RM22UA22MR | Main | supply circuit type | DC
RM22UA22MR | Main | relay name | RM22UA
RM22UA22MR | Main | relay monitored parameters | Overvoltage detection
RM22UA22MR | Main | time delay type | Without
RM22UA22MR | Main | switching capacity in VA | 2000 VA
RM22UA22MR | Main | measurement range | 1...100 V voltage AC/DC 50/60 Hz
RM22UA22MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA22MR | Complementary | maximum switching voltage | 250 V AC
RM22UA22MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA22MR | Complementary | maximum switching current | 8 A AC
RM22UA22MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA22MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA22MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA22MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA22MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA22MR | Complementary | resistance across terminals | 110 kOhm at E2-M terminals ¦ 22 kOhm at E1-M terminals ¦ 220 kOhm at E3-M terminals
RM22UA22MR | Complementary | output contacts | 2 C/O
RM22UA22MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
RM22UA22MR | Complementary | run-up delay at power-up | 600 ms
RM22UA22MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA22MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM22UA22MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA22MR | Complementary | response time | <= 500 ms
RM22UA22MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA22MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA22MR | Complementary | insulation | Between supply and measurement
RM22UA22MR | Complementary | mounting position | Any position
RM22UA22MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA22MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA22MR | Complementary | housing material | Self-extinguishing plastic
RM22UA22MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA22MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA22MR | Complementary | electrical durability | 100000 cycles
RM22UA22MR | Complementary | mechanical durability | 10000000 cycles
RM22UA22MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA22MR | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM22UA22MR | Complementary | contacts material | Cadmium free
RM22UA22MR | Complementary | width | 22.5 mm
RM22UA22MR | Complementary | net weight | 0.11 kg
RM22UA22MR | Environment | immunity to microbreaks | 10 ms
RM22UA22MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA22MR | Environment | standards | EN/IEC 60255-1
RM22UA22MR | Environment | product certifications | CE ¦ China RoHS ¦ CCC ¦ EAC ¦ CSA ¦ RCM ¦ UL ¦ GL
RM22UA22MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA22MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA22MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA22MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA22MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA22MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA22MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA22MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA22MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA22MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA22MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA22MR | Offer Sustainability | Mercury free | Yes
RM22UA22MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA22MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA22MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA22MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA22MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA23MR | Main | range of product | Zelio Control
RM22UA23MR | Main | product or component type | Modular measurement and control relays
RM22UA23MR | Main | relay type | Voltage control relay
RM22UA23MR | Main | network number of phases | 1 phase
RM22UA23MR | Main | supply circuit type | DC
RM22UA23MR | Main | relay name | RM22UA
RM22UA23MR | Main | relay monitored parameters | Overvoltage detection
RM22UA23MR | Main | time delay type | Without
RM22UA23MR | Main | switching capacity in VA | 2000 VA
RM22UA23MR | Main | measurement range | 15...500 V voltage AC/DC 50/60 Hz
RM22UA23MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA23MR | Complementary | maximum switching voltage | 250 V AC
RM22UA23MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA23MR | Complementary | maximum switching current | 8 A AC
RM22UA23MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA23MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA23MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA23MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA23MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA23MR | Complementary | resistance across terminals | 150 kOhm at E2-M terminals ¦ 300 kOhm at E1-M terminals ¦ 500 kOhm at E3-M terminals
RM22UA23MR | Complementary | output contacts | 2 C/O
RM22UA23MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting
RM22UA23MR | Complementary | run-up delay at power-up | 600 ms
RM22UA23MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA23MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM22UA23MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA23MR | Complementary | response time | <= 500 ms
RM22UA23MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA23MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA23MR | Complementary | insulation | Between supply and measurement
RM22UA23MR | Complementary | mounting position | Any position
RM22UA23MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA23MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA23MR | Complementary | housing material | Self-extinguishing plastic
RM22UA23MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA23MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA23MR | Complementary | electrical durability | 100000 cycles
RM22UA23MR | Complementary | mechanical durability | 10000000 cycles
RM22UA23MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA23MR | Complementary | safety reliability data | MTTFd = 308.2 years ¦ B10d = 290000
RM22UA23MR | Complementary | contacts material | Cadmium free
RM22UA23MR | Complementary | width | 22.5 mm
RM22UA23MR | Complementary | net weight | 0.11 kg
RM22UA23MR | Environment | immunity to microbreaks | 10 ms
RM22UA23MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA23MR | Environment | standards | EN/IEC 60255-1
RM22UA23MR | Environment | product certifications | CE ¦ China RoHS ¦ CCC ¦ GL ¦ RCM ¦ UL ¦ EAC ¦ CSA
RM22UA23MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA23MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA23MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA23MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA23MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA23MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA23MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA23MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA23MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA23MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA23MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA23MR | Offer Sustainability | Mercury free | Yes
RM22UA23MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA23MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA23MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA23MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA23MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA31MR | Main | range of product | Zelio Control
RM22UA31MR | Main | product or component type | Modular measurement and control relays
RM22UA31MR | Main | relay type | Voltage control relay
RM22UA31MR | Main | network number of phases | 1 phase
RM22UA31MR | Main | supply circuit type | DC
RM22UA31MR | Main | relay name | RM22UA
RM22UA31MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Overvoltage or undervoltage detection
RM22UA31MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22UA31MR | Main | switching capacity in VA | 2000 VA
RM22UA31MR | Main | measurement range | 50 mV...5 V voltage AC/DC 50/60 Hz
RM22UA31MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA31MR | Complementary | maximum switching voltage | 250 V AC
RM22UA31MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA31MR | Complementary | maximum switching current | 8 A AC
RM22UA31MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA31MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA31MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA31MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA31MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA31MR | Complementary | resistance across terminals | 30 kOhm at E2-M terminals ¦ 5 kOhm at E1-M terminals ¦ 50 kOhm at E3-M terminals
RM22UA31MR | Complementary | output contacts | 2 C/O
RM22UA31MR | Complementary | nominal output current | 8 A
RM22UA31MR | Complementary | hysteresis | 3 % fixed of full scale for window mode ¦ 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
RM22UA31MR | Complementary | run-up delay at power-up | 600 ms
RM22UA31MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA31MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM22UA31MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA31MR | Complementary | response time | <= 500 ms
RM22UA31MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA31MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA31MR | Complementary | insulation | Between supply and measurement
RM22UA31MR | Complementary | mounting position | Any position
RM22UA31MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA31MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA31MR | Complementary | housing material | Self-extinguishing plastic
RM22UA31MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA31MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA31MR | Complementary | electrical durability | 100000 cycles
RM22UA31MR | Complementary | mechanical durability | 10000000 cycles
RM22UA31MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA31MR | Complementary | safety reliability data | MTTFd = 308.2 years ¦ B10d = 290000
RM22UA31MR | Complementary | contacts material | Cadmium free
RM22UA31MR | Complementary | width | 22.5 mm
RM22UA31MR | Complementary | net weight | 0.11 kg
RM22UA31MR | Environment | immunity to microbreaks | 10 ms
RM22UA31MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA31MR | Environment | standards | EN/IEC 60255-1
RM22UA31MR | Environment | product certifications | CE ¦ CSA ¦ RCM ¦ GL ¦ China RoHS ¦ CCC ¦ EAC ¦ UL
RM22UA31MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA31MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA31MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA31MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA31MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA31MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA31MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA31MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA31MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA31MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA31MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA31MR | Offer Sustainability | Mercury free | Yes
RM22UA31MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA31MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA31MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA31MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA31MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA32MR | Main | range of product | Zelio Control
RM22UA32MR | Main | product or component type | Modular measurement and control relays
RM22UA32MR | Main | relay type | Voltage control relay
RM22UA32MR | Main | network number of phases | 1 phase
RM22UA32MR | Main | supply circuit type | DC
RM22UA32MR | Main | relay name | RM22UA
RM22UA32MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Overvoltage or undervoltage detection
RM22UA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22UA32MR | Main | switching capacity in VA | 2000 VA
RM22UA32MR | Main | measurement range | 1...100 V voltage AC/DC 50/60 Hz
RM22UA32MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA32MR | Complementary | maximum switching voltage | 250 V AC
RM22UA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA32MR | Complementary | maximum switching current | 8 A AC
RM22UA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA32MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA32MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA32MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA32MR | Complementary | resistance across terminals | 110 kOhm at E2-M terminals ¦ 22 kOhm at E1-M terminals ¦ 220 kOhm at E3-M terminals
RM22UA32MR | Complementary | output contacts | 2 C/O
RM22UA32MR | Complementary | nominal output current | 8 A
RM22UA32MR | Complementary | hysteresis | 3 % fixed of full scale for window mode ¦ 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
RM22UA32MR | Complementary | run-up delay at power-up | 600 ms
RM22UA32MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA32MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM22UA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA32MR | Complementary | response time | <= 500 ms
RM22UA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA32MR | Complementary | insulation | Between supply and measurement
RM22UA32MR | Complementary | mounting position | Any position
RM22UA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA32MR | Complementary | housing material | Self-extinguishing plastic
RM22UA32MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA32MR | Complementary | electrical durability | 100000 cycles
RM22UA32MR | Complementary | mechanical durability | 10000000 cycles
RM22UA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA32MR | Complementary | safety reliability data | B10d = 290000 ¦ MTTFd = 308.2 years
RM22UA32MR | Complementary | contacts material | Cadmium free
RM22UA32MR | Complementary | width | 22.5 mm
RM22UA32MR | Complementary | net weight | 0.11 kg
RM22UA32MR | Environment | immunity to microbreaks | 10 ms
RM22UA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA32MR | Environment | standards | EN/IEC 60255-1
RM22UA32MR | Environment | product certifications | GL ¦ UL ¦ CCC ¦ EAC ¦ CE ¦ China RoHS ¦ RCM ¦ CSA
RM22UA32MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA32MR | Offer Sustainability | Mercury free | Yes
RM22UA32MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA32MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UA33MR | Main | range of product | Zelio Control
RM22UA33MR | Main | product or component type | Modular measurement and control relays
RM22UA33MR | Main | relay type | Voltage control relay
RM22UA33MR | Main | network number of phases | 1 phase
RM22UA33MR | Main | supply circuit type | DC
RM22UA33MR | Main | relay name | RM22UA
RM22UA33MR | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Overvoltage or undervoltage detection
RM22UA33MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22UA33MR | Main | switching capacity in VA | 2000 VA
RM22UA33MR | Main | measurement range | 15...500 V voltage AC/DC 50/60 Hz
RM22UA33MR | Complementary | reset time | 1500 ms at maximum voltage
RM22UA33MR | Complementary | maximum switching voltage | 250 V AC
RM22UA33MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UA33MR | Complementary | maximum switching current | 8 A AC
RM22UA33MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RM22UA33MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM22UA33MR | Complementary | power consumption in VA | 3.5 VA AC
RM22UA33MR | Complementary | maximum power consumption in W | 1.5 W DC
RM22UA33MR | Complementary | supply voltage frequency | 40...70 Hz +/- 10 %
RM22UA33MR | Complementary | resistance across terminals | 150 kOhm at E2-M terminals ¦ 300 kOhm at E1-M terminals ¦ 500 kOhm at E3-M terminals
RM22UA33MR | Complementary | output contacts | 2 C/O
RM22UA33MR | Complementary | nominal output current | 8 A
RM22UA33MR | Complementary | hysteresis | 3 % fixed of full scale for window mode ¦ 5…50 % adjustable of threshold setting for overvoltage or undervoltage detection
RM22UA33MR | Complementary | run-up delay at power-up | 600 ms
RM22UA33MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM22UA33MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM22UA33MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM22UA33MR | Complementary | response time | <= 500 ms
RM22UA33MR | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UA33MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UA33MR | Complementary | insulation | Between supply and measurement
RM22UA33MR | Complementary | mounting position | Any position
RM22UA33MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UA33MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UA33MR | Complementary | housing material | Self-extinguishing plastic
RM22UA33MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UA33MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UA33MR | Complementary | electrical durability | 100000 cycles
RM22UA33MR | Complementary | mechanical durability | 10000000 cycles
RM22UA33MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UA33MR | Complementary | safety reliability data | MTTFd = 308.2 years ¦ B10d = 290000
RM22UA33MR | Complementary | contacts material | Cadmium free
RM22UA33MR | Complementary | width | 22.5 mm
RM22UA33MR | Complementary | net weight | 0.11 kg
RM22UA33MR | Environment | immunity to microbreaks | 10 ms
RM22UA33MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UA33MR | Environment | standards | EN/IEC 60255-1
RM22UA33MR | Environment | product certifications | RCM ¦ UL ¦ China RoHS ¦ EAC ¦ CSA ¦ CE ¦ GL ¦ CCC
RM22UA33MR | Environment | ambient air temperature for storage | -40…70 °C
RM22UA33MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UA33MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UA33MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UA33MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UA33MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UA33MR | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UA33MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UA33MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UA33MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UA33MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UA33MR | Offer Sustainability | Mercury free | Yes
RM22UA33MR | Offer Sustainability | RoHS exemption information | Yes
RM22UA33MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UA33MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UA33MR | Offer Sustainability | Circularity Profile | End of Life Information
RM22UA33MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM22UB34 | Main | range of product | Zelio Control
RM22UB34 | Main | product or component type | Modular measurement and control relays
RM22UB34 | Main | relay type | Voltage control relay
RM22UB34 | Main | network number of phases | 1 phase
RM22UB34 | Main | supply circuit type | DC
RM22UB34 | Main | relay name | RM22UA
RM22UB34 | Main | relay monitored parameters | Overvoltage and undervoltage detection
RM22UB34 | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM22UB34 | Main | switching capacity in VA | 2000 VA
RM22UB34 | Main | measurement range | 80...300 V voltage AC/DC 50/60 Hz
RM22UB34 | Complementary | reset time | 1500 ms at maximum voltage
RM22UB34 | Complementary | maximum switching voltage | 250 V AC
RM22UB34 | Complementary | minimum switching current | 10 mA at 5 V DC
RM22UB34 | Complementary | maximum switching current | 8 A AC
RM22UB34 | Complementary | [Us] rated supply voltage | 110...240 V AC 50/60 Hz
RM22UB34 | Complementary | supply voltage limits | 60…280 V AC
RM22UB34 | Complementary | power consumption in VA | 5 VA AC
RM22UB34 | Complementary | maximum power consumption in W | 2 W DC
RM22UB34 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RM22UB34 | Complementary | output contacts | 2 C/O
RM22UB34 | Complementary | nominal output current | 8 A
RM22UB34 | Complementary | hysteresis | 5…50 % adjustable of threshold setting
RM22UB34 | Complementary | run-up delay at power-up | 600 ms
RM22UB34 | Complementary | maximum measuring cycle | 250 ms measurement cycle as true rms value
RM22UB34 | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM22UB34 | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.2 %/°C with temperature variation
RM22UB34 | Complementary | response time | <= 500 ms
RM22UB34 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM22UB34 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM22UB34 | Complementary | mounting position | Any position
RM22UB34 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM22UB34 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM22UB34 | Complementary | housing material | Self-extinguishing plastic
RM22UB34 | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM22UB34 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM22UB34 | Complementary | electrical durability | 100000 cycles
RM22UB34 | Complementary | mechanical durability | 10000000 cycles
RM22UB34 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM22UB34 | Complementary | safety reliability data | MTTFd = 433.7 years ¦ B10d = 400000
RM22UB34 | Complementary | contacts material | Cadmium free
RM22UB34 | Complementary | width | 22.5 mm
RM22UB34 | Complementary | net weight | 0.09 kg
RM22UB34 | Environment | immunity to microbreaks | 20 ms
RM22UB34 | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22
RM22UB34 | Environment | standards | EN/IEC 60255-1
RM22UB34 | Environment | product certifications | CCC ¦ China RoHS ¦ CE ¦ CSA ¦ EAC ¦ UL ¦ GL ¦ RCM
RM22UB34 | Environment | ambient air temperature for storage | -40…70 °C
RM22UB34 | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM22UB34 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM22UB34 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM22UB34 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM22UB34 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RM22UB34 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM22UB34 | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM22UB34 | Offer Sustainability | Sustainable offer status | Green Premium product
RM22UB34 | Offer Sustainability | REACh Regulation | REACh Declaration
RM22UB34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM22UB34 | Offer Sustainability | Mercury free | Yes
RM22UB34 | Offer Sustainability | RoHS exemption information | Yes
RM22UB34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM22UB34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM22UB34 | Offer Sustainability | Circularity Profile | End of Life Information
RM22UB34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35JA32MR | Main | range of product | Zelio Control
RM35JA32MR | Main | product or component type | Modular measurement and control relays
RM35JA32MR | Main | relay type | Current control relay
RM35JA32MR | Main | relay name | RM35JA
RM35JA32MR | Main | relay monitored parameters | Overcurrent or undercurrent in window mode ¦ Overcurrent or undercurrent detection
RM35JA32MR | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM35JA32MR | Main | switching capacity in VA | 2000 VA
RM35JA32MR | Main | measurement range | 0.15...1.5 A E1-M terminals ¦ 0.5...5 A E2-M terminals ¦ 1.5...15 A E3-M terminals ¦ 150 mA...15 A current AC/DC 50/60 Hz
RM35JA32MR | Complementary | reset time | 1500 ms at maximum voltage
RM35JA32MR | Complementary | maximum switching voltage | 250 V AC
RM35JA32MR | Complementary | minimum switching current | 10 mA at 5 V DC
RM35JA32MR | Complementary | maximum switching current | 8 A AC
RM35JA32MR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM35JA32MR | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM35JA32MR | Complementary | operating limits | - 15 % + 10 % Un
RM35JA32MR | Complementary | power consumption in VA | 3.5 VA AC
RM35JA32MR | Complementary | maximum power consumption in W | 1.5 W DC
RM35JA32MR | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals ¦ 0.015 Ohm at E2-M terminals ¦ 0.05 Ohm at E1-M terminals
RM35JA32MR | Complementary | output contacts | 2 C/O
RM35JA32MR | Complementary | nominal output current | 8 A
RM35JA32MR | Complementary | internal input resistance | 0.015 Ohm ¦ 0.005 Ohm ¦ 0.05 Ohm
RM35JA32MR | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale
RM35JA32MR | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM35JA32MR | Complementary | setting accuracy of time delay | 10 P
RM35JA32MR | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM35JA32MR | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection ¦ 3 % fixed of full scale for window mode
RM35JA32MR | Complementary | run-up delay at power-up | 0.3 s
RM35JA32MR | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM35JA32MR | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35JA32MR | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35JA32MR | Complementary | response time | <= 500 ms (on crossing the threshold)
RM35JA32MR | Complementary | threshold setting | 10...100 %
RM35JA32MR | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM35JA32MR | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM35JA32MR | Complementary | insulation | Between supply and measurement
RM35JA32MR | Complementary | mounting position | Any position
RM35JA32MR | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM35JA32MR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35JA32MR | Complementary | housing material | Self-extinguishing plastic
RM35JA32MR | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM35JA32MR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM35JA32MR | Complementary | electrical durability | 100000 cycles
RM35JA32MR | Complementary | mechanical durability | 10000000 cycles
RM35JA32MR | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM35JA32MR | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM35JA32MR | Complementary | contacts material | Cadmium free
RM35JA32MR | Complementary | width | 35 mm
RM35JA32MR | Complementary | net weight | 0.12 kg
RM35JA32MR | Environment | immunity to microbreaks | 50 ms
RM35JA32MR | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22 ¦ Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3
RM35JA32MR | Environment | standards | EN/IEC 60255-1
RM35JA32MR | Environment | product certifications | CE ¦ GL ¦ CCC ¦ EAC ¦ RCM ¦ China RoHS ¦ UL ¦ CSA
RM35JA32MR | Environment | ambient air temperature for storage | -40…70 °C
RM35JA32MR | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM35JA32MR | Environment | environmental characteristic | 3K3 C
RM35JA32MR | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM35JA32MR | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM35JA32MR | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM35JA32MR | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529 ¦ IP30 (housing) conforming to IEC 60529
RM35JA32MR | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM35JA32MR | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM35JA32MR | Offer Sustainability | Sustainable offer status | Green Premium product
RM35JA32MR | Offer Sustainability | REACh Regulation | REACh Declaration
RM35JA32MR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35JA32MR | Offer Sustainability | Mercury free | Yes
RM35JA32MR | Offer Sustainability | RoHS exemption information | Yes
RM35JA32MR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35JA32MR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35JA32MR | Offer Sustainability | Circularity Profile | End of Life Information
RM35JA32MR | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM35JA32MT | Main | range of product | Zelio Control
RM35JA32MT | Main | product or component type | Modular measurement and control relays
RM35JA32MT | Main | relay type | Current control relay
RM35JA32MT | Main | relay name | RM35JA
RM35JA32MT | Main | relay monitored parameters | Overcurrent or undercurrent detection ¦ Overcurrent or undercurrent in window mode
RM35JA32MT | Main | time delay type | Adjustable 0.1...30 s, +/- 10 % of the full scale value on crossing the threshold Tt
RM35JA32MT | Main | switching capacity in VA | 2000 VA
RM35JA32MT | Main | measurement range | 0.15...1.5 A E1-M terminals ¦ 0.5...5 A E2-M terminals ¦ 1.5...15 A E3-M terminals ¦ 150 mA...15 A current AC/DC 50/60 Hz
RM35JA32MT | Complementary | reset time | 1500 ms at maximum voltage
RM35JA32MT | Complementary | maximum switching voltage | 250 V AC
RM35JA32MT | Complementary | minimum switching current | 10 mA at 5 V DC
RM35JA32MT | Complementary | maximum switching current | 8 A AC
RM35JA32MT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz +/- 10 %
RM35JA32MT | Complementary | supply voltage limits | 323…456.5 V AC
RM35JA32MT | Complementary | operating limits | - 15 % + 10 % Un
RM35JA32MT | Complementary | power consumption in VA | 8 VA AC
RM35JA32MT | Complementary | resistance across terminals | 0.005 Ohm at E3-M terminals ¦ 0.015 Ohm at E2-M terminals ¦ 0.05 Ohm at E1-M terminals
RM35JA32MT | Complementary | output contacts | 2 C/O
RM35JA32MT | Complementary | nominal output current | 8 A
RM35JA32MT | Complementary | internal input resistance | 0.005 Ohm ¦ 0.015 Ohm ¦ 0.05 Ohm
RM35JA32MT | Complementary | setting accuracy of the switching threshold | +/- 10 % of the full scale for 1.5 A ¦ +/- 10 % of the full scale for 5 A ¦ +/- 20 % of the full scale for 15 A
RM35JA32MT | Complementary | switching threshold drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM35JA32MT | Complementary | setting accuracy of time delay | 10 %
RM35JA32MT | Complementary | time delay drift | <= 0.05 % per degree centigrade depending permissible ambient air temperature ¦ <= 1 % within the supply voltage range
RM35JA32MT | Complementary | hysteresis | 5…50 % adjustable of threshold setting for overcurrent or undercurrent detection ¦ 3 % fixed of full scale for window mode
RM35JA32MT | Complementary | run-up delay at power-up | 0.3 s
RM35JA32MT | Complementary | maximum measuring cycle | 100 ms measurement cycle as true rms value
RM35JA32MT | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit ¦ +/- 2 % for time delay
RM35JA32MT | Complementary | measurement error | < 1 % over the whole range with voltage variation ¦ 0.05 %/°C with temperature variation
RM35JA32MT | Complementary | response time | <= 500 ms (on crossing the threshold)
RM35JA32MT | Complementary | threshold setting | 10...100 %
RM35JA32MT | Complementary | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RM35JA32MT | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RM35JA32MT | Complementary | insulation | Between supply and measurement
RM35JA32MT | Complementary | mounting position | Any position
RM35JA32MT | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end
RM35JA32MT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM35JA32MT | Complementary | housing material | Self-extinguishing plastic
RM35JA32MT | Complementary | status LED | LED (yellow)relay ON: ¦ LED (green)power ON:
RM35JA32MT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RM35JA32MT | Complementary | electrical durability | 100000 cycles
RM35JA32MT | Complementary | mechanical durability | 10000000 cycles
RM35JA32MT | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RM35JA32MT | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RM35JA32MT | Complementary | contacts material | Cadmium free
RM35JA32MT | Complementary | width | 35 mm
RM35JA32MT | Complementary | net weight | 0.12 kg
RM35JA32MT | Environment | immunity to microbreaks | 50 ms
RM35JA32MT | Environment | electromagnetic compatibility | Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test - test level: 4 kV level 4 (direct) conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test - test level: 2 kV level 4 (capacitive coupling) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22 ¦ Emission standard for residential, commercial and light-industrial environments (except radiated emission) conforming to EN/IEC 61000-6-3
RM35JA32MT | Environment | standards | EN/IEC 60255-1
RM35JA32MT | Environment | product certifications | CCC ¦ EAC ¦ CSA ¦ China RoHS ¦ RCM ¦ UL ¦ GL ¦ CE
RM35JA32MT | Environment | ambient air temperature for storage | -40…70 °C
RM35JA32MT | Environment | ambient air temperature for operation | -20…50 °C at 60 Hz ¦ -20…60 °C at 50 Hz AC/DC
RM35JA32MT | Environment | environmental characteristic | 3K3 C
RM35JA32MT | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RM35JA32MT | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RM35JA32MT | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RM35JA32MT | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529 ¦ IP30 (housing) conforming to IEC 60529
RM35JA32MT | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RM35JA32MT | Environment | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RM35JA32MT | Offer Sustainability | Sustainable offer status | Green Premium product
RM35JA32MT | Offer Sustainability | REACh Regulation | REACh Declaration
RM35JA32MT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM35JA32MT | Offer Sustainability | Mercury free | Yes
RM35JA32MT | Offer Sustainability | RoHS exemption information | Yes
RM35JA32MT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM35JA32MT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM35JA32MT | Offer Sustainability | Circularity Profile | End of Life Information
RM35JA32MT | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMNF22TB30 | Main | range of product | Zelio Control
RMNF22TB30 | Main | product or component type | Monitoring relay
RMNF22TB30 | Main | relay type | Control relay
RMNF22TB30 | Main | network number of phases | 3 phases
RMNF22TB30 | Main | relay name | RMNF22
RMNF22TB30 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection ¦ Overvoltage detection ¦ Undervoltage detection ¦ Overfrequency and underfrequency ¦ Asymmetry
RMNF22TB30 | Main | Supported OS | Android
RMNF22TB30 | Main | software version | V4.4 and above
RMNF22TB30 | Main | App for product | Zelio NFC (downloadable from Google Play store)
RMNF22TB30 | Main | product compatibility | NFC enabled mobile device
RMNF22TB30 | Main | time delay type | On-delay 0.1 s...60 min ¦ Off-delay 0.1 s...60 min
RMNF22TB30 | Main | switching capacity in VA | 2000 VA
RMNF22TB30 | Complementary | NFC operating frequency | 13.56 MHz
RMNF22TB30 | Complementary | Maximum RF power transmitted | 0.0002 mW
RMNF22TB30 | Complementary | reset time | 1500 ms at maximum voltage
RMNF22TB30 | Complementary | maximum switching voltage | 250 V AC
RMNF22TB30 | Complementary | minimum switching current | 100 mA at 6 V
RMNF22TB30 | Complementary | maximum switching current | 8 A AC
RMNF22TB30 | Complementary | [Us] rated supply voltage | 208...480 V AC line to line ¦ 120...277 V AC line to neutral
RMNF22TB30 | Complementary | supply voltage limits | 166.4…576 V AC line to line ¦ 96…332.4 V AC line to neutral
RMNF22TB30 | Complementary | power consumption in VA | 4 VA at 480 V AC 60 Hz
RMNF22TB30 | Complementary | on-load factor | 100 %
RMNF22TB30 | Complementary | supply voltage frequency | 50...60 Hz +/- 10 %
RMNF22TB30 | Complementary | output contacts | 2 C/O
RMNF22TB30 | Complementary | setting accuracy of the switching threshold | +/- (1.5 % + 1 V)
RMNF22TB30 | Complementary | setting accuracy of time delay | +/- 3 % for 10 s...60 min time delay range ¦ +/- 300 ms for 0...10 s time delay range
RMNF22TB30 | Complementary | hysteresis | 3 % of fixed for phase failure detection
RMNF22TB30 | Complementary | alarm threshold | 166...576 V adjustable overvoltage and undervoltage detection (line to line) ¦ 96...332 V adjustable overvoltage and undervoltage detection (line to neutral) ¦ 5...150 V adjustable asymmetry ¦ 45...66 Hz adjustable overfrequency or underfrequency
RMNF22TB30 | Complementary | Run-up delay at power-up max | 650 ms
RMNF22TB30 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RMNF22TB30 | Complementary | repeat accuracy | +/- 0.5 % for input circuit ¦ +/- 3 % for time delay
RMNF22TB30 | Complementary | setting accuracy of the switching threshold | +/- (1.5 % + 1 V)
RMNF22TB30 | Complementary | measurement error | < 0.05 %/Hz with frequency variation ¦ < 0.05 %/°C with temperature variation
RMNF22TB30 | Complementary | response time | <= 300 ms
RMNF22TB30 | Complementary | insulation resistance | > 100 MOhm at 500 V DC conforming to IEC 60255-27
RMNF22TB30 | Complementary | [Ui] rated insulation voltage | 400 V
RMNF22TB30 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV during 1.2/50 µs
RMNF22TB30 | Complementary | dielectric test voltage | 2.5 kV, 1 min AC 50 Hz conforming to IEC 60255-27
RMNF22TB30 | Complementary | mounting position | Any position
RMNF22TB30 | Complementary | connections - terminals | Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 1.5 mm² (AWG 20...AWG 16) flexible with cable end ¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 1 x 0.5...1 x 2.5 mm² (AWG 20...AWG 14) flexible with cable end
RMNF22TB30 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 ¦ 0.60…0.99 N.m conforming to IEC 60947-1
RMNF22TB30 | Complementary | housing material | Self-extinguishing plastic
RMNF22TB30 | Complementary | local signalling | LED Un: (steady), green for power ON ¦ LED R1: (steady), amber for relay energised ¦ LED R1: (blinking), amber for timing in progress ¦ LED R2: (steady), amber for relay energised ¦ LED R2: (blinking), amber for timing in progress ¦ LED PL: (steady), red for alarm phase failure triggered ¦ LED PS: (blinking), red for alarm phase sequence failure triggered ¦ LED UV: (steady), red for alarm undervoltage failure triggered ¦ LED OV: (blinking), red for alarm overvoltage failure triggered ¦ LED UF: (steady), red for alarm underfrequency failure triggered ¦ LED OF: (blinking), red for alarm overfrequency failure triggered ¦ LED ASYM: (steady), red for alarm asymmentry failure triggered
RMNF22TB30 | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RMNF22TB30 | Complementary | electrical durability | 100000 cycles
RMNF22TB30 | Complementary | mechanical durability | 10000000 cycles
RMNF22TB30 | Complementary | utilisation category | AC-15 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ AC-1 conforming to IEC 60947-4-1 ¦ DC-1 conforming to IEC 60947-4-1
RMNF22TB30 | Complementary | [Ith] conventional free air thermal current | 8 A
RMNF22TB30 | Complementary | contacts material | Cadmium free
RMNF22TB30 | Complementary | width | 22.5 mm
RMNF22TB30 | Complementary | height | 90 mm
RMNF22TB30 | Complementary | depth | 99 mm
RMNF22TB30 | Complementary | net weight | 0.125 kg
RMNF22TB30 | Environment | immunity to microbreaks | 10 ms
RMNF22TB30 | Environment | electromagnetic compatibility | Voltage dips and interruptions immunity test - test level: 70 % (25/30 cycles) conforming to IEC 61000-4-11 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Conducted and radiated emissions class B group 1 conforming to CISPR 11 ¦ Conducted and radiated emissions class B conforming to CISPR 22 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 conforming to IEC 61000-4-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2 ¦ 1 MHz damped oscillating wave - test level: 2.5 kV CM, 1 kV DM criteria B conforming to IEC 61000-4-18 ¦ Voltage dips and interruptions immunity test - test level: 0 % (0.5...25 cycles) conforming to IEC 61000-4-11 ¦ Magnetic field at power frequency - test level: 30 A/m (continuous)-300 A/m (1-3 s) level 4 conforming to IEC 61000-4-8 ¦ Surge immunity test - test level: 2 kV level 4 (differential mode) conforming to IEC 61000-4-5 ¦ Immunity for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-1 ¦ Voltage dips and interruptions immunity test - test level: 40 % (10/12 cycles) conforming to IEC 61000-4-11 ¦ Voltage interruptions - test level: 0 % criteria C (250/300 cycles) conforming to IEC 61000-4-29 ¦ Electrical fast transient/burst immunity test - test level: 4 kV criteria B (direct) conforming to IEC 61000-4-4 ¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Surge immunity test - test level: 4 kV level 4 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Conducted RF disturbances level 3 conforming to IEC 61000-4-6
RMNF22TB30 | Environment | standards | EN/IEC 60255-1
RMNF22TB30 | Environment | product certifications | CE ¦ UL ¦ CSA ¦ CCC ¦ EAC ¦ RCM
RMNF22TB30 | Environment | directives | 2014/30/EU - electromagnetic compatibility ¦ 2014/35/EU - low voltage directive ¦ 2014/53/EU - radio equipment directive ¦ 2015/863/EU - RoHS directive
RMNF22TB30 | Environment | ambient air temperature for storage | -40…70 °C
RMNF22TB30 | Environment | ambient air temperature for operation | -20…60 °C
RMNF22TB30 | Environment | relative humidity | 93…97 % at 25…55 °C conforming to IEC 60068-2-30
RMNF22TB30 | Environment | vibration resistance | 0.075 mm (f= 10…58.1 Hz) not in operation conforming to IEC 60068-2-6 ¦ 1 gn (f= 58.1…150 Hz) not in operation conforming to IEC 60068-2-6 ¦ 0.035 mm (f= 10…58.1 Hz) in operation conforming to IEC 60068-2-6 ¦ 0.5 gn (f= 58.1…150 Hz) in operation conforming to IEC 60068-2-6
RMNF22TB30 | Environment | shock resistance | 15 gn (duration = 11 ms) for not in operation conforming to IEC 60068-2-27 ¦ 5 gn (duration = 11 ms) for in operation conforming to IEC 60068-2-27
RMNF22TB30 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP40 (front panel) conforming to IEC 60529
RMNF22TB30 | Environment | pollution degree | 3 conforming to IEC 60664-1 ¦ 3 conforming to UL 508
RMNF22TB30 | Environment | overvoltage category | III conforming to IEC 60664-1 ¦ III conforming to UL 508
RMNF22TB30 | Offer Sustainability | Sustainable offer status | Green Premium product
RMNF22TB30 | Offer Sustainability | REACh Regulation | REACh Declaration
RMNF22TB30 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMNF22TB30 | Offer Sustainability | Mercury free | Yes
RMNF22TB30 | Offer Sustainability | RoHS exemption information | Yes
RMNF22TB30 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMNF22TB30 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMNF22TB30 | Offer Sustainability | Circularity Profile | End of Life Information
RMNF22TB30 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RE17LAMW | Main | range of product | Zelio Time
RE17LAMW | Main | product or component type | Modular timing relay
RE17LAMW | Main | discrete output type | Solid state
RE17LAMW | Main | width | 17.5 mm
RE17LAMW | Main | component name | RE17L
RE17LAMW | Main | time delay type | A
RE17LAMW | Main | time delay range | 1...10 s ¦ 10...100 h ¦ 6...60 s ¦ 0.1...1 s ¦ 1...10 min ¦ 6...60 min ¦ 1...10 h
RE17LAMW | Main | nominal output current | 0.7 A
RE17LAMW | Complementary | control type | Selector switch front panel
RE17LAMW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE17LAMW | Complementary | voltage range | 0.85...1.1 Us
RE17LAMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17LAMW | Complementary | control signal pulse width | 0.05 s typical
RE17LAMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17LAMW | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17LAMW | Complementary | power on delay | 100 ms
RE17LAMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17LAMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17LAMW | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17LAMW | Complementary | housing material | Self-extinguishing
RE17LAMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17LAMW | Complementary | temperature drift | +/- 0.05 %/°C
RE17LAMW | Complementary | voltage drift | +/- 0.2 %/V
RE17LAMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17LAMW | Complementary | reset time | 350 ms on de-energisation typical
RE17LAMW | Complementary | on-load factor | 100 %
RE17LAMW | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17LAMW | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17LAMW | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL ¦ 0.7 A AC/DC at 20 °C
RE17LAMW | Complementary | operating frequency | 10 Hz
RE17LAMW | Complementary | maximum output current | 20 A
RE17LAMW | Complementary | minimum switching current | 10 mA
RE17LAMW | Complementary | maximum leakage current | 5 mA
RE17LAMW | Complementary | maximum switching voltage | 250 V AC/DC
RE17LAMW | Complementary | maximum voltage drop | <4 V 3-wire ¦ <8 V 2-wire
RE17LAMW | Complementary | electrical durability | 100000000 cycles
RE17LAMW | Complementary | marking | CE
RE17LAMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17LAMW | Complementary | safety reliability data | MTTFd = 353.8 years ¦ B10d = 320000
RE17LAMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17LAMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17LAMW | Complementary | net weight | 0.068 kg
RE17LAMW | Complementary | time delay type | A
RE17LAMW | Complementary | functionality | On-delay timing
RE17LAMW | Complementary | compatibility code | RE17
RE17LAMW | Environment | immunity to microbreaks | 20 ms
RE17LAMW | Environment | derating factor | 5 mA/°C
RE17LAMW | Environment | standards | 2004/108/EC ¦ EN 61000-6-1 ¦ 2006/95/EC ¦ EN 61000-6-3 ¦ EN 61000-6-2 ¦ IEC 61812-1 ¦ EN 61000-6-4
RE17LAMW | Environment | product certifications | GL ¦ CSA ¦ CULus
RE17LAMW | Environment | ambient air temperature for storage | -30…60 °C
RE17LAMW | Environment | ambient air temperature for operation | -20…60 °C
RE17LAMW | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17LAMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17LAMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17LAMW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17LAMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17LAMW | Offer Sustainability | Sustainable offer status | Green Premium product
RE17LAMW | Offer Sustainability | REACh Regulation | REACh Declaration
RE17LAMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17LAMW | Offer Sustainability | Mercury free | Yes
RE17LAMW | Offer Sustainability | RoHS exemption information | Yes
RE17LAMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17LAMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17LAMW | Offer Sustainability | Circularity Profile | End of Life Information
RE17LCBM | Main | range of product | Zelio Time
RE17LCBM | Main | product or component type | Modular timing relay
RE17LCBM | Main | discrete output type | Solid state
RE17LCBM | Main | width | 17.5 mm
RE17LCBM | Main | component name | RE17L
RE17LCBM | Main | time delay type | C
RE17LCBM | Main | time delay range | 10...100 h ¦ 6...60 s ¦ 6...60 min ¦ 1...10 h ¦ 1...10 s ¦ 1...10 min ¦ 0.1...1 s
RE17LCBM | Main | nominal output current | 0.7 A
RE17LCBM | Complementary | control type | Selector switch front panel
RE17LCBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
RE17LCBM | Complementary | voltage range | 0.85...1.1 Us
RE17LCBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17LCBM | Complementary | release of input voltage | 7 V
RE17LCBM | Complementary | control signal pulse width | 0.05 s typical
RE17LCBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17LCBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17LCBM | Complementary | power on delay | 100 ms
RE17LCBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17LCBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17LCBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17LCBM | Complementary | housing material | Self-extinguishing
RE17LCBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17LCBM | Complementary | temperature drift | +/- 0.05 %/°C
RE17LCBM | Complementary | voltage drift | +/- 0.2 %/V
RE17LCBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17LCBM | Complementary | reset time | 350 ms on de-energisation typical
RE17LCBM | Complementary | on-load factor | 100 %
RE17LCBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17LCBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17LCBM | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL ¦ 0.7 A AC/DC at 20 °C
RE17LCBM | Complementary | operating frequency | 10 Hz
RE17LCBM | Complementary | maximum output current | 20 A
RE17LCBM | Complementary | minimum switching current | 10 mA
RE17LCBM | Complementary | maximum leakage current | 5 mA
RE17LCBM | Complementary | maximum switching voltage | 250 V AC
RE17LCBM | Complementary | maximum voltage drop | <4 V 3-wire ¦ <8 V 2-wire
RE17LCBM | Complementary | electrical durability | 100000000 cycles
RE17LCBM | Complementary | marking | CE
RE17LCBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17LCBM | Complementary | safety reliability data | MTTFd = 353.8 years ¦ B10d = 320000
RE17LCBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17LCBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17LCBM | Complementary | net weight | 0.068 kg
RE17LCBM | Complementary | time delay type | C
RE17LCBM | Complementary | functionality | Off-delay timing
RE17LCBM | Complementary | compatibility code | RE17
RE17LCBM | Environment | immunity to microbreaks | 20 ms
RE17LCBM | Environment | derating factor | 5 mA/°C
RE17LCBM | Environment | standards | 2004/108/EC ¦ EN 61000-6-3 ¦ 2006/95/EC ¦ EN 61000-6-2 ¦ IEC 61812-1 ¦ EN 61000-6-4 ¦ EN 61000-6-1
RE17LCBM | Environment | product certifications | CSA ¦ GL ¦ CULus
RE17LCBM | Environment | ambient air temperature for storage | -30…60 °C
RE17LCBM | Environment | ambient air temperature for operation | -20…60 °C
RE17LCBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17LCBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17LCBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17LCBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17LCBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17LCBM | Offer Sustainability | Sustainable offer status | Green Premium product
RE17LCBM | Offer Sustainability | REACh Regulation | REACh Declaration
RE17LCBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17LCBM | Offer Sustainability | Mercury free | Yes
RE17LCBM | Offer Sustainability | RoHS exemption information | Yes
RE17LCBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17LCBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17LCBM | Offer Sustainability | Circularity Profile | End of Life Information
RE17LHBM | Main | range of product | Zelio Time
RE17LHBM | Main | product or component type | Modular timing relay
RE17LHBM | Main | discrete output type | Solid state
RE17LHBM | Main | width | 17.5 mm
RE17LHBM | Main | component name | RE17L
RE17LHBM | Main | time delay type | H
RE17LHBM | Main | time delay range | 1...10 s ¦ 1...10 h ¦ 0.1...1 s ¦ 6...60 s ¦ 6...60 min ¦ 1...10 min ¦ 10...100 h
RE17LHBM | Main | nominal output current | 0.7 A
RE17LHBM | Complementary | control type | Selector switch front panel
RE17LHBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
RE17LHBM | Complementary | voltage range | 0.85...1.1 Us
RE17LHBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17LHBM | Complementary | release of input voltage | 9 V
RE17LHBM | Complementary | control signal pulse width | 0.05 s typical
RE17LHBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17LHBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17LHBM | Complementary | power on delay | 100 ms
RE17LHBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17LHBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17LHBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17LHBM | Complementary | housing material | Self-extinguishing
RE17LHBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17LHBM | Complementary | temperature drift | +/- 0.05 %/°C
RE17LHBM | Complementary | voltage drift | +/- 0.2 %/V
RE17LHBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17LHBM | Complementary | reset time | 350 ms on de-energisation typical
RE17LHBM | Complementary | on-load factor | 100 %
RE17LHBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17LHBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17LHBM | Complementary | breaking capacity | 0.5 A AC/DC conforming to UL ¦ 0.7 A AC/DC at 20 °C
RE17LHBM | Complementary | operating frequency | 10 Hz
RE17LHBM | Complementary | maximum output current | 20 A
RE17LHBM | Complementary | minimum switching current | 10 mA
RE17LHBM | Complementary | maximum leakage current | 5 mA
RE17LHBM | Complementary | maximum switching voltage | 250 V AC
RE17LHBM | Complementary | maximum voltage drop | <4 V 3-wire ¦ <8 V 2-wire
RE17LHBM | Complementary | electrical durability | 100000000 cycles
RE17LHBM | Complementary | marking | CE
RE17LHBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17LHBM | Complementary | safety reliability data | MTTFd = 353.8 years ¦ B10d = 320000
RE17LHBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17LHBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17LHBM | Complementary | net weight | 0.068 kg
RE17LHBM | Complementary | time delay type | H
RE17LHBM | Complementary | functionality | On-delay timing
RE17LHBM | Complementary | compatibility code | RE17
RE17LHBM | Environment | immunity to microbreaks | 20 ms
RE17LHBM | Environment | derating factor | 5 mA/°C
RE17LHBM | Environment | standards | 2006/95/EC ¦ EN 61000-6-1 ¦ EN 61000-6-3 ¦ EN 61000-6-2 ¦ IEC 61812-1 ¦ EN 61000-6-4 ¦ 2004/108/EC
RE17LHBM | Environment | product certifications | CULus ¦ CSA ¦ GL
RE17LHBM | Environment | ambient air temperature for storage | -30…60 °C
RE17LHBM | Environment | ambient air temperature for operation | -20…60 °C
RE17LHBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17LHBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17LHBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17LHBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17LHBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17LHBM | Offer Sustainability | Sustainable offer status | Green Premium product
RE17LHBM | Offer Sustainability | REACh Regulation | REACh Declaration
RE17LHBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17LHBM | Offer Sustainability | Mercury free | Yes
RE17LHBM | Offer Sustainability | RoHS exemption information | Yes
RE17LHBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17LHBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17LHBM | Offer Sustainability | Circularity Profile | End of Life Information
RE17LLBM | Main | range of product | Zelio Time
RE17LLBM | Main | product or component type | Modular timing relay
RE17LLBM | Main | discrete output type | Solid state
RE17LLBM | Main | width | 17.5 mm
RE17LLBM | Main | component name | RE17L
RE17LLBM | Main | time delay type | Li ¦ L
RE17LLBM | Main | time delay range | 6...60 s ¦ 6...60 min ¦ 1...10 min ¦ 0.1...1 s ¦ 1...10 h ¦ 10...100 h ¦ 1...10 s
RE17LLBM | Main | nominal output current | 0.7 A
RE17LLBM | Complementary | control type | Selector switch front panel
RE17LLBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
RE17LLBM | Complementary | voltage range | 0.85...1.1 Us
RE17LLBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17LLBM | Complementary | release of input voltage | 7 V
RE17LLBM | Complementary | control signal pulse width | 0.05 s typical
RE17LLBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17LLBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17LLBM | Complementary | power on delay | 100 ms
RE17LLBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17LLBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17LLBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17LLBM | Complementary | housing material | Self-extinguishing
RE17LLBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17LLBM | Complementary | temperature drift | +/- 0.05 %/°C
RE17LLBM | Complementary | voltage drift | +/- 0.2 %/V
RE17LLBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17LLBM | Complementary | reset time | 350 ms on de-energisation typical
RE17LLBM | Complementary | on-load factor | 100 %
RE17LLBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17LLBM | Complementary | breaking capacity | 0.5 A AC conforming to UL ¦ 0.7 A AC at 20 °C
RE17LLBM | Complementary | operating frequency | 10 Hz
RE17LLBM | Complementary | maximum output current | 20 A
RE17LLBM | Complementary | minimum switching current | 10 mA
RE17LLBM | Complementary | maximum leakage current | 5 mA
RE17LLBM | Complementary | maximum switching voltage | 250 V AC
RE17LLBM | Complementary | maximum voltage drop | <4 V 3-wire ¦ <8 V 2-wire
RE17LLBM | Complementary | electrical durability | 100000000 cycles
RE17LLBM | Complementary | marking | CE
RE17LLBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17LLBM | Complementary | safety reliability data | B10d = 320000 ¦ MTTFd = 353.8 years
RE17LLBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17LLBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17LLBM | Complementary | net weight | 0.068 kg
RE17LLBM | Complementary | time delay type | L, Li
RE17LLBM | Complementary | functionality | Asymmetrical flashing timer
RE17LLBM | Complementary | compatibility code | RE17
RE17LLBM | Environment | immunity to microbreaks | 20 ms
RE17LLBM | Environment | derating factor | 5 mA/°C
RE17LLBM | Environment | standards | EN 61000-6-2 ¦ EN 61000-6-4 ¦ IEC 61812-1 ¦ EN 61000-6-1 ¦ EN 61000-6-3 ¦ 2006/95/EC ¦ 2004/108/EC
RE17LLBM | Environment | product certifications | CULus ¦ GL ¦ CSA
RE17LLBM | Environment | ambient air temperature for storage | -30…60 °C
RE17LLBM | Environment | ambient air temperature for operation | -20…60 °C
RE17LLBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17LLBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17LLBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17LLBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17LLBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17LLBM | Offer Sustainability | Sustainable offer status | Green Premium product
RE17LLBM | Offer Sustainability | REACh Regulation | REACh Declaration
RE17LLBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17LLBM | Offer Sustainability | Mercury free | Yes
RE17LLBM | Offer Sustainability | RoHS exemption information | Yes
RE17LLBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17LLBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17LLBM | Offer Sustainability | Circularity Profile | End of Life Information
RE17LMBM | Main | range of product | Zelio Time
RE17LMBM | Main | product or component type | Modular timing relay
RE17LMBM | Main | discrete output type | Solid state
RE17LMBM | Main | width | 17.5 mm
RE17LMBM | Main | component name | RE17L
RE17LMBM | Main | time delay type | D ¦ A ¦ B ¦ H ¦ Ac ¦ At ¦ Ht ¦ Di ¦ C ¦ Bw
RE17LMBM | Main | time delay range | 1...10 s ¦ 6...60 s ¦ 6...60 min ¦ 1...10 h ¦ 10...100 h ¦ 1...10 min ¦ 0.1...1 s
RE17LMBM | Main | nominal output current | 0.7 A
RE17LMBM | Complementary | control type | Selector switch front panel
RE17LMBM | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz
RE17LMBM | Complementary | voltage range | 0.85...1.1 Us
RE17LMBM | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17LMBM | Complementary | release of input voltage | 8 V
RE17LMBM | Complementary | control signal pulse width | 0.05 s typical
RE17LMBM | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17LMBM | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17LMBM | Complementary | power on delay | 100 ms
RE17LMBM | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17LMBM | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17LMBM | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17LMBM | Complementary | housing material | Self-extinguishing
RE17LMBM | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17LMBM | Complementary | temperature drift | +/- 0.05 %/°C
RE17LMBM | Complementary | voltage drift | +/- 0.2 %/V
RE17LMBM | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17LMBM | Complementary | reset time | 350 ms on de-energisation typical
RE17LMBM | Complementary | on-load factor | 100 %
RE17LMBM | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17LMBM | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17LMBM | Complementary | breaking capacity | 0.5 A AC conforming to UL ¦ 0.7 A AC at 20 °C
RE17LMBM | Complementary | operating frequency | 10 Hz
RE17LMBM | Complementary | maximum output current | 20 A
RE17LMBM | Complementary | minimum switching current | 10 mA
RE17LMBM | Complementary | maximum leakage current | 5 mA
RE17LMBM | Complementary | maximum switching voltage | 250 V AC
RE17LMBM | Complementary | maximum voltage drop | <4 V 3-wire ¦ <8 V 2-wire
RE17LMBM | Complementary | electrical durability | 100000000 cycles
RE17LMBM | Complementary | marking | CE
RE17LMBM | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17LMBM | Complementary | safety reliability data | MTTFd = 353.8 years ¦ B10d = 320000
RE17LMBM | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17LMBM | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17LMBM | Complementary | net weight | 0.068 kg
RE17LMBM | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
RE17LMBM | Complementary | functionality | Multifunction
RE17LMBM | Complementary | compatibility code | RE17
RE17LMBM | Environment | immunity to microbreaks | 20 ms
RE17LMBM | Environment | derating factor | 5 mA/°C
RE17LMBM | Environment | standards | 2004/108/EC ¦ EN 61000-6-2 ¦ IEC 61812-1 ¦ EN 61000-6-4 ¦ EN 61000-6-1 ¦ 2006/95/EC ¦ EN 61000-6-3
RE17LMBM | Environment | product certifications | GL ¦ CULus ¦ CSA
RE17LMBM | Environment | ambient air temperature for storage | -30…60 °C
RE17LMBM | Environment | ambient air temperature for operation | -20…60 °C
RE17LMBM | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17LMBM | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17LMBM | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17LMBM | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17LMBM | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17LMBM | Offer Sustainability | Sustainable offer status | Green Premium product
RE17LMBM | Offer Sustainability | REACh Regulation | REACh Declaration
RE17LMBM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17LMBM | Offer Sustainability | Mercury free | Yes
RE17LMBM | Offer Sustainability | RoHS exemption information | Yes
RE17LMBM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17LMBM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17LMBM | Offer Sustainability | Circularity Profile | End of Life Information
RE17RAMU | Main | range of product | Zelio Time
RE17RAMU | Main | product or component type | Modular timing relay
RE17RAMU | Main | discrete output type | Relay
RE17RAMU | Main | width | 17.5 mm
RE17RAMU | Main | device short name | RE17R
RE17RAMU | Main | time delay type | At ¦ A
RE17RAMU | Main | time delay range | 1...10 min ¦ 10...100 h ¦ 0.1...1 s ¦ 6...60 s ¦ 6...60 min ¦ 1...10 s ¦ 1...10 h
RE17RAMU | Main | nominal output current | 8 A
RE17RAMU | Complementary | contacts type and composition | 1 C/O
RE17RAMU | Complementary | contacts material | Cadmium free
RE17RAMU | Complementary | height | 90 mm
RE17RAMU | Complementary | depth | 72 mm
RE17RAMU | Complementary | control type | Selector switch front panel
RE17RAMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RAMU | Complementary | voltage range | 0.85...1.1 Us
RE17RAMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RAMU | Complementary | release of input voltage | 10 V
RE17RAMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RAMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RAMU | Complementary | housing material | Self-extinguishing
RE17RAMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RAMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RAMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RAMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RAMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RAMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RAMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RAMU | Complementary | on-load factor | 100 %
RE17RAMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RAMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RAMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RAMU | Complementary | maximum switching current | 8 A AC/DC
RE17RAMU | Complementary | maximum switching voltage | 250 V AC
RE17RAMU | Complementary | breaking capacity | 2000 VA
RE17RAMU | Complementary | operating frequency | 10 Hz
RE17RAMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RAMU | Complementary | mechanical durability | 10000000 cycles
RE17RAMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RAMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RAMU | Complementary | power on delay | 100 ms
RE17RAMU | Complementary | marking | CE
RE17RAMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RAMU | Complementary | safety reliability data | B10d = 270000 ¦ MTTFd = 296.8 years
RE17RAMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RAMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RAMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RAMU | Complementary | net weight | 0.07 kg
RE17RAMU | Complementary | time delay type | A, At
RE17RAMU | Complementary | functionality | On-delay timing
RE17RAMU | Complementary | compatibility code | RE17
RE17RAMU | Environment | immunity to microbreaks | 20 ms
RE17RAMU | Environment | standards | 2006/95/EC ¦ 2004/108/EC ¦ IEC 61812-1 ¦ EN 61000-6-3 ¦ EN 61000-6-1 ¦ EN 61000-6-4 ¦ EN 61000-6-2
RE17RAMU | Environment | product certifications | CSA ¦ CULus ¦ GL
RE17RAMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RAMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RAMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RAMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RAMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RAMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RAMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RAMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RAMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RAMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RAMU | Offer Sustainability | Mercury free | Yes
RE17RAMU | Offer Sustainability | RoHS exemption information | Yes
RE17RAMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RAMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RAMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RAMU | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RE17RBMU | Main | range of product | Zelio Time
RE17RBMU | Main | product or component type | Modular timing relay
RE17RBMU | Main | discrete output type | Relay
RE17RBMU | Main | width | 17.5 mm
RE17RBMU | Main | device short name | RE17R
RE17RBMU | Main | time delay type | B
RE17RBMU | Main | time delay range | 10...100 h ¦ 1...10 min ¦ 6...60 min ¦ 1...10 s ¦ 6...60 s ¦ 1...10 h ¦ 0.1...1 s
RE17RBMU | Main | nominal output current | 8 A
RE17RBMU | Complementary | contacts type and composition | 1 C/O
RE17RBMU | Complementary | contacts material | Cadmium free
RE17RBMU | Complementary | height | 90 mm
RE17RBMU | Complementary | depth | 72 mm
RE17RBMU | Complementary | control type | Selector switch front panel
RE17RBMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RBMU | Complementary | voltage range | 0.85...1.1 Us
RE17RBMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RBMU | Complementary | release of input voltage | 10 V
RE17RBMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RBMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RBMU | Complementary | housing material | Self-extinguishing
RE17RBMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RBMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RBMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RBMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RBMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RBMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RBMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RBMU | Complementary | on-load factor | 100 %
RE17RBMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RBMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RBMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RBMU | Complementary | maximum switching current | 8 A AC/DC
RE17RBMU | Complementary | maximum switching voltage | 250 V AC
RE17RBMU | Complementary | breaking capacity | 2000 VA
RE17RBMU | Complementary | operating frequency | 10 Hz
RE17RBMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RBMU | Complementary | mechanical durability | 10000000 cycles
RE17RBMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RBMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RBMU | Complementary | power on delay | 100 ms
RE17RBMU | Complementary | marking | CE
RE17RBMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RBMU | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RBMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RBMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RBMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RBMU | Complementary | net weight | 0.07 kg
RE17RBMU | Complementary | time delay type | B
RE17RBMU | Complementary | functionality | Pulse signal
RE17RBMU | Complementary | compatibility code | RE17
RE17RBMU | Environment | immunity to microbreaks | 20 ms
RE17RBMU | Environment | standards | 2006/95/EC ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 61000-6-4 ¦ IEC 61812-1 ¦ EN 61000-6-1 ¦ 2004/108/EC
RE17RBMU | Environment | product certifications | GL ¦ CULus ¦ CSA
RE17RBMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RBMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RBMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RBMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RBMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RBMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RBMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RBMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RBMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RBMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RBMU | Offer Sustainability | Mercury free | Yes
RE17RBMU | Offer Sustainability | RoHS exemption information | Yes
RE17RBMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RBMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RBMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RCMU | Main | range of product | Zelio Time
RE17RCMU | Main | product or component type | Modular timing relay
RE17RCMU | Main | discrete output type | Relay
RE17RCMU | Main | width | 17.5 mm
RE17RCMU | Main | device short name | RE17R
RE17RCMU | Main | time delay type | C
RE17RCMU | Main | time delay range | 6...60 s ¦ 1...10 h ¦ 1...10 min ¦ 6...60 min ¦ 0.1...1 s ¦ 1...10 s ¦ 10...100 h
RE17RCMU | Main | nominal output current | 8 A
RE17RCMU | Complementary | contacts type and composition | 1 C/O
RE17RCMU | Complementary | contacts material | Cadmium free
RE17RCMU | Complementary | height | 90 mm
RE17RCMU | Complementary | depth | 72 mm
RE17RCMU | Complementary | control type | Selector switch front panel
RE17RCMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RCMU | Complementary | voltage range | 0.85...1.1 Us
RE17RCMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RCMU | Complementary | release of input voltage | 10 V
RE17RCMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RCMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RCMU | Complementary | housing material | Self-extinguishing
RE17RCMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RCMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RCMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RCMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RCMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RCMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RCMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RCMU | Complementary | on-load factor | 100 %
RE17RCMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RCMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RCMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RCMU | Complementary | maximum switching current | 8 A AC/DC
RE17RCMU | Complementary | maximum switching voltage | 250 V AC
RE17RCMU | Complementary | breaking capacity | 2000 VA
RE17RCMU | Complementary | operating frequency | 10 Hz
RE17RCMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RCMU | Complementary | mechanical durability | 10000000 cycles
RE17RCMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RCMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RCMU | Complementary | power on delay | 100 ms
RE17RCMU | Complementary | marking | CE
RE17RCMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RCMU | Complementary | safety reliability data | B10d = 270000 ¦ MTTFd = 296.8 years
RE17RCMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RCMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RCMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RCMU | Complementary | net weight | 0.07 kg
RE17RCMU | Complementary | time delay type | C
RE17RCMU | Complementary | functionality | Off-delay timing
RE17RCMU | Complementary | compatibility code | RE17
RE17RCMU | Environment | immunity to microbreaks | 20 ms
RE17RCMU | Environment | standards | EN 61000-6-4 ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ 2004/108/EC ¦ 2006/95/EC ¦ IEC 61812-1 ¦ EN 61000-6-1
RE17RCMU | Environment | product certifications | CULus ¦ GL ¦ CSA
RE17RCMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RCMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RCMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RCMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RCMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RCMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RCMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RCMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RCMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RCMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RCMU | Offer Sustainability | Mercury free | Yes
RE17RCMU | Offer Sustainability | RoHS exemption information | Yes
RE17RCMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RCMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RCMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RHMU | Main | range of product | Zelio Time
RE17RHMU | Main | product or component type | Modular timing relay
RE17RHMU | Main | discrete output type | Relay
RE17RHMU | Main | width | 17.5 mm
RE17RHMU | Main | device short name | RE17R
RE17RHMU | Main | time delay type | H ¦ Ht
RE17RHMU | Main | time delay range | 10...100 h ¦ 0.1...1 s ¦ 6...60 min ¦ 1...10 s ¦ 1...10 min ¦ 6...60 s ¦ 1...10 h
RE17RHMU | Main | nominal output current | 8 A
RE17RHMU | Complementary | contacts type and composition | 1 C/O
RE17RHMU | Complementary | contacts material | Cadmium free
RE17RHMU | Complementary | height | 90 mm
RE17RHMU | Complementary | depth | 72 mm
RE17RHMU | Complementary | control type | Selector switch front panel
RE17RHMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RHMU | Complementary | voltage range | 0.85...1.1 Us
RE17RHMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RHMU | Complementary | release of input voltage | 10 V
RE17RHMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RHMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RHMU | Complementary | housing material | Self-extinguishing
RE17RHMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RHMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RHMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RHMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RHMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RHMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RHMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RHMU | Complementary | on-load factor | 100 %
RE17RHMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RHMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RHMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RHMU | Complementary | maximum switching current | 8 A AC/DC
RE17RHMU | Complementary | maximum switching voltage | 250 V AC
RE17RHMU | Complementary | breaking capacity | 2000 VA
RE17RHMU | Complementary | operating frequency | 10 Hz
RE17RHMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RHMU | Complementary | mechanical durability | 10000000 cycles
RE17RHMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RHMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RHMU | Complementary | power on delay | 100 ms
RE17RHMU | Complementary | marking | CE
RE17RHMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RHMU | Complementary | safety reliability data | B10d = 270000 ¦ MTTFd = 296.8 years
RE17RHMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RHMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RHMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RHMU | Complementary | net weight | 0.07 kg
RE17RHMU | Complementary | time delay type | H, Ht
RE17RHMU | Complementary | functionality | On-delay timing
RE17RHMU | Complementary | compatibility code | RE17
RE17RHMU | Environment | immunity to microbreaks | 20 ms
RE17RHMU | Environment | standards | EN 61000-6-4 ¦ EN 61000-6-1 ¦ 2006/95/EC ¦ EN 61000-6-3 ¦ IEC 61812-1 ¦ 2004/108/EC ¦ EN 61000-6-2
RE17RHMU | Environment | product certifications | CULus ¦ CSA ¦ GL
RE17RHMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RHMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RHMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RHMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RHMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RHMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RHMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RHMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RHMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RHMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RHMU | Offer Sustainability | Mercury free | Yes
RE17RHMU | Offer Sustainability | RoHS exemption information | Yes
RE17RHMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RHMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RHMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RLJU | Main | range of product | Zelio Time
RE17RLJU | Main | product or component type | Modular timing relay
RE17RLJU | Main | discrete output type | Relay
RE17RLJU | Main | width | 17.5 mm
RE17RLJU | Main | device short name | RE17R
RE17RLJU | Main | time delay type | L ¦ Li
RE17RLJU | Main | time delay range | 6...60 min ¦ 1...10 h ¦ 6...60 s ¦ 1...10 s ¦ 10...100 h ¦ 0.1...1 s ¦ 1...10 min
RE17RLJU | Main | nominal output current | 8 A
RE17RLJU | Complementary | contacts type and composition | 1 C/O
RE17RLJU | Complementary | contacts material | Cadmium free
RE17RLJU | Complementary | height | 90 mm
RE17RLJU | Complementary | depth | 72 mm
RE17RLJU | Complementary | control type | Selector switch front panel
RE17RLJU | Complementary | [Us] rated supply voltage | 12 V AC/DC 50/60 Hz
RE17RLJU | Complementary | voltage range | 0.9...1.2 Us
RE17RLJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RLJU | Complementary | release of input voltage | 5 V
RE17RLJU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RLJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RLJU | Complementary | housing material | Self-extinguishing
RE17RLJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RLJU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RLJU | Complementary | voltage drift | +/- 0.2 %/V
RE17RLJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RLJU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RLJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RLJU | Complementary | reset time | 120 ms on de-energisation typical
RE17RLJU | Complementary | on-load factor | 100 %
RE17RLJU | Complementary | power consumption in VA | 0…0.7 VA at 12 V AC
RE17RLJU | Complementary | maximum power consumption in W | 0.5 W at 12 V DC
RE17RLJU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RLJU | Complementary | maximum switching current | 8 A AC/DC
RE17RLJU | Complementary | maximum switching voltage | 250 V AC
RE17RLJU | Complementary | breaking capacity | 2000 VA
RE17RLJU | Complementary | operating frequency | 10 Hz
RE17RLJU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RLJU | Complementary | mechanical durability | 10000000 cycles
RE17RLJU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RLJU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RLJU | Complementary | power on delay | 100 ms
RE17RLJU | Complementary | marking | CE
RE17RLJU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RLJU | Complementary | safety reliability data | B10d = 270000 ¦ MTTFd = 296.8 years
RE17RLJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RLJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RLJU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF
RE17RLJU | Complementary | net weight | 0.07 kg
RE17RLJU | Complementary | time delay type | L, Li
RE17RLJU | Complementary | functionality | Asymmetrical flashing timer
RE17RLJU | Complementary | compatibility code | RE17
RE17RLJU | Environment | immunity to microbreaks | 20 ms
RE17RLJU | Environment | standards | 2006/95/EC ¦ 2004/108/EC ¦ EN 61000-6-4 ¦ IEC 61812-1 ¦ EN 61000-6-3 ¦ EN 61000-6-2 ¦ EN 61000-6-1
RE17RLJU | Environment | product certifications | CSA ¦ CULus ¦ GL
RE17RLJU | Environment | ambient air temperature for storage | -30…60 °C
RE17RLJU | Environment | ambient air temperature for operation | -20…60 °C
RE17RLJU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RLJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RLJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RLJU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RLJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RLJU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RLJU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RLJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RLJU | Offer Sustainability | Mercury free | Yes
RE17RLJU | Offer Sustainability | RoHS exemption information | Yes
RE17RLJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RLJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RLJU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RLMU | Main | range of product | Zelio Time
RE17RLMU | Main | product or component type | Modular timing relay
RE17RLMU | Main | discrete output type | Relay
RE17RLMU | Main | width | 17.5 mm
RE17RLMU | Main | device short name | RE17R
RE17RLMU | Main | time delay type | Li ¦ L
RE17RLMU | Main | time delay range | 1...10 h ¦ 1...10 s ¦ 0.1...1 s ¦ 6...60 min ¦ 1...10 min ¦ 10...100 h ¦ 6...60 s
RE17RLMU | Main | nominal output current | 8 A
RE17RLMU | Complementary | contacts type and composition | 1 C/O
RE17RLMU | Complementary | contacts material | Cadmium free
RE17RLMU | Complementary | height | 90 mm
RE17RLMU | Complementary | depth | 72 mm
RE17RLMU | Complementary | control type | Selector switch front panel
RE17RLMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RLMU | Complementary | voltage range | 0.85...1.1 Us
RE17RLMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RLMU | Complementary | release of input voltage | 10 V
RE17RLMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RLMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RLMU | Complementary | housing material | Self-extinguishing
RE17RLMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RLMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RLMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RLMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RLMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RLMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RLMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RLMU | Complementary | on-load factor | 100 %
RE17RLMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RLMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RLMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RLMU | Complementary | maximum switching current | 8 A AC/DC
RE17RLMU | Complementary | maximum switching voltage | 250 V AC
RE17RLMU | Complementary | breaking capacity | 2000 VA
RE17RLMU | Complementary | operating frequency | 10 Hz
RE17RLMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RLMU | Complementary | mechanical durability | 10000000 cycles
RE17RLMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RLMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RLMU | Complementary | power on delay | 100 ms
RE17RLMU | Complementary | marking | CE
RE17RLMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RLMU | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RLMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RLMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RLMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF
RE17RLMU | Complementary | net weight | 0.07 kg
RE17RLMU | Complementary | time delay type | L, Li
RE17RLMU | Complementary | functionality | Asymmetrical flashing timer
RE17RLMU | Complementary | compatibility code | RE17
RE17RLMU | Environment | immunity to microbreaks | 20 ms
RE17RLMU | Environment | standards | 2006/95/EC ¦ EN 61000-6-2 ¦ EN 61000-6-4 ¦ 2004/108/EC ¦ IEC 61812-1 ¦ EN 61000-6-3 ¦ EN 61000-6-1
RE17RLMU | Environment | product certifications | GL ¦ CULus ¦ CSA
RE17RLMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RLMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RLMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RLMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RLMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RLMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RLMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RLMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RLMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RLMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RLMU | Offer Sustainability | Mercury free | Yes
RE17RLMU | Offer Sustainability | RoHS exemption information | Yes
RE17RLMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RLMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RLMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMEMU | Main | range of product | Zelio Time
RE17RMEMU | Main | product or component type | Modular timing relay
RE17RMEMU | Main | discrete output type | Relay
RE17RMEMU | Main | width | 17.5 mm
RE17RMEMU | Main | device short name | RE17R
RE17RMEMU | Main | time delay type | A ¦ Ht ¦ H ¦ Di ¦ At ¦ D ¦ B ¦ C
RE17RMEMU | Main | time delay range | 6...60 min ¦ 1...10 min ¦ 1...10 s ¦ 1...10 h ¦ 6...60 s ¦ 0.1...1 s
RE17RMEMU | Main | nominal output current | 8 A
RE17RMEMU | Complementary | contacts type and composition | 1 C/O
RE17RMEMU | Complementary | contacts material | Cadmium free
RE17RMEMU | Complementary | height | 90 mm
RE17RMEMU | Complementary | depth | 72 mm
RE17RMEMU | Complementary | control type | Selector switch front panel
RE17RMEMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RMEMU | Complementary | voltage range | 0.85...1.1 Us
RE17RMEMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMEMU | Complementary | release of input voltage | 10 V
RE17RMEMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMEMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RMEMU | Complementary | housing material | Self-extinguishing
RE17RMEMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMEMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMEMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RMEMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMEMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMEMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMEMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RMEMU | Complementary | on-load factor | 100 %
RE17RMEMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RMEMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RMEMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMEMU | Complementary | maximum switching current | 8 A AC/DC
RE17RMEMU | Complementary | maximum switching voltage | 250 V AC
RE17RMEMU | Complementary | breaking capacity | 2000 VA
RE17RMEMU | Complementary | operating frequency | 10 Hz
RE17RMEMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMEMU | Complementary | mechanical durability | 10000000 cycles
RE17RMEMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMEMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMEMU | Complementary | power on delay | 100 ms
RE17RMEMU | Complementary | marking | CE
RE17RMEMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMEMU | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RMEMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMEMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMEMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMEMU | Complementary | net weight | 0.07 kg
RE17RMEMU | Complementary | time delay type | A, At, B, C, D, Di, H, Ht
RE17RMEMU | Complementary | functionality | Multifunction
RE17RMEMU | Complementary | compatibility code | RE17
RE17RMEMU | Environment | immunity to microbreaks | 20 ms
RE17RMEMU | Environment | standards | 2004/108/EC ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 61000-6-1 ¦ 2006/95/EC ¦ IEC 61812-1 ¦ EN 61000-6-4
RE17RMEMU | Environment | product certifications | CSA ¦ CULus
RE17RMEMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RMEMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RMEMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMEMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMEMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMEMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMEMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMEMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMEMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMEMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMEMU | Offer Sustainability | Mercury free | Yes
RE17RMEMU | Offer Sustainability | RoHS exemption information | Yes
RE17RMEMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMEMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMEMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMJU | Main | range of product | Zelio Time
RE17RMJU | Main | product or component type | Modular timing relay
RE17RMJU | Main | discrete output type | Relay
RE17RMJU | Main | width | 17.5 mm
RE17RMJU | Main | device short name | RE17R
RE17RMJU | Main | time delay type | H ¦ A ¦ C ¦ Ac ¦ Ht ¦ D ¦ Bw ¦ Di ¦ B ¦ At
RE17RMJU | Main | time delay range | 1...10 s ¦ 6...60 s ¦ 10...100 h ¦ 1...10 min ¦ 1...10 h ¦ 0.1...1 s ¦ 6...60 min
RE17RMJU | Main | nominal output current | 8 A
RE17RMJU | Complementary | contacts type and composition | 1 C/O
RE17RMJU | Complementary | contacts material | Cadmium free
RE17RMJU | Complementary | height | 90 mm
RE17RMJU | Complementary | depth | 72 mm
RE17RMJU | Complementary | control type | Selector switch front panel
RE17RMJU | Complementary | [Us] rated supply voltage | 12 V AC/DC 50/60 Hz
RE17RMJU | Complementary | voltage range | 0.9...1.2 Us
RE17RMJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMJU | Complementary | release of input voltage | 5 V
RE17RMJU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RMJU | Complementary | housing material | Self-extinguishing
RE17RMJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMJU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMJU | Complementary | voltage drift | +/- 0.2 %/V
RE17RMJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMJU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMJU | Complementary | reset time | 120 ms on de-energisation typical
RE17RMJU | Complementary | on-load factor | 100 %
RE17RMJU | Complementary | power consumption in VA | 0…0.7 VA at 12 V AC
RE17RMJU | Complementary | maximum power consumption in W | 0.5 W at 12 V DC
RE17RMJU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMJU | Complementary | maximum switching current | 8 A AC/DC
RE17RMJU | Complementary | maximum switching voltage | 250 V AC
RE17RMJU | Complementary | breaking capacity | 2000 VA
RE17RMJU | Complementary | operating frequency | 10 Hz
RE17RMJU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMJU | Complementary | mechanical durability | 10000000 cycles
RE17RMJU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMJU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMJU | Complementary | power on delay | 100 ms
RE17RMJU | Complementary | marking | CE
RE17RMJU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMJU | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RMJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMJU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMJU | Complementary | net weight | 0.07 kg
RE17RMJU | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
RE17RMJU | Complementary | functionality | Multifunction
RE17RMJU | Complementary | compatibility code | RE17
RE17RMJU | Environment | immunity to microbreaks | 20 ms
RE17RMJU | Environment | standards | 2006/95/EC ¦ 2004/108/EC ¦ EN 61000-6-4 ¦ EN 61000-6-1 ¦ EN 61000-6-3 ¦ IEC 61812-1 ¦ EN 61000-6-2
RE17RMJU | Environment | product certifications | CSA ¦ GL ¦ CULus
RE17RMJU | Environment | ambient air temperature for storage | -30…60 °C
RE17RMJU | Environment | ambient air temperature for operation | -20…60 °C
RE17RMJU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMJU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMJU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMJU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMJU | Offer Sustainability | Mercury free | Yes
RE17RMJU | Offer Sustainability | RoHS exemption information | Yes
RE17RMJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMJU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMMU | Main | range of product | Zelio Time
RE17RMMU | Main | product or component type | Modular timing relay
RE17RMMU | Main | discrete output type | Relay
RE17RMMU | Main | width | 17.5 mm
RE17RMMU | Main | device short name | RE17R
RE17RMMU | Main | time delay type | C ¦ A ¦ B ¦ At ¦ D ¦ Ht ¦ Bw ¦ Di ¦ H ¦ Ac
RE17RMMU | Main | time delay range | 6...60 min ¦ 1...10 h ¦ 0.1...1 s ¦ 1...10 s ¦ 1...10 min ¦ 10...100 h ¦ 6...60 s
RE17RMMU | Main | nominal output current | 8 A
RE17RMMU | Complementary | contacts type and composition | 1 C/O
RE17RMMU | Complementary | contacts material | Cadmium free
RE17RMMU | Complementary | height | 90 mm
RE17RMMU | Complementary | depth | 72 mm
RE17RMMU | Complementary | control type | Selector switch front panel
RE17RMMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RMMU | Complementary | voltage range | 0.85...1.1 Us
RE17RMMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMMU | Complementary | release of input voltage | 10 V
RE17RMMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RMMU | Complementary | housing material | Self-extinguishing
RE17RMMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RMMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RMMU | Complementary | on-load factor | 100 %
RE17RMMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RMMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RMMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMMU | Complementary | maximum switching current | 8 A AC/DC
RE17RMMU | Complementary | maximum switching voltage | 250 V AC
RE17RMMU | Complementary | breaking capacity | 2000 VA
RE17RMMU | Complementary | operating frequency | 10 Hz
RE17RMMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMMU | Complementary | mechanical durability | 10000000 cycles
RE17RMMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMMU | Complementary | power on delay | 100 ms
RE17RMMU | Complementary | marking | CE
RE17RMMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMMU | Complementary | safety reliability data | B10d = 270000 ¦ MTTFd = 296.8 years
RE17RMMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMMU | Complementary | net weight | 0.07 kg
RE17RMMU | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
RE17RMMU | Complementary | functionality | Multifunction
RE17RMMU | Complementary | compatibility code | RE17
RE17RMMU | Environment | immunity to microbreaks | 20 ms
RE17RMMU | Environment | standards | 2006/95/EC ¦ 2004/108/EC ¦ IEC 61812-1 ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 61000-6-4 ¦ EN 61000-6-1
RE17RMMU | Environment | product certifications | CSA ¦ GL ¦ CULus
RE17RMMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RMMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RMMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMMU | Offer Sustainability | Mercury free | Yes
RE17RMMU | Offer Sustainability | RoHS exemption information | Yes
RE17RMMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMMU | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMMW | Main | range of product | Zelio Time
RE17RMMW | Main | product or component type | Modular timing relay
RE17RMMW | Main | discrete output type | Relay
RE17RMMW | Main | width | 17.5 mm
RE17RMMW | Main | device short name | RE17R
RE17RMMW | Main | time delay type | At ¦ Di ¦ Ht ¦ H ¦ C ¦ Ac ¦ A ¦ D ¦ B ¦ Bw
RE17RMMW | Main | time delay range | 1...10 h ¦ 0.1...1 s ¦ 6...60 s ¦ 10...100 h ¦ 6...60 min ¦ 1...10 s ¦ 1...10 min
RE17RMMW | Main | nominal output current | 8 A
RE17RMMW | Complementary | contacts type and composition | 1 C/O
RE17RMMW | Complementary | contacts material | Cadmium free
RE17RMMW | Complementary | height | 90 mm
RE17RMMW | Complementary | depth | 72 mm
RE17RMMW | Complementary | control type | Selector switch front panel
RE17RMMW | Complementary | [Us] rated supply voltage | 12...240 V AC/DC 50/60 Hz
RE17RMMW | Complementary | voltage range | 0.85...1.1 Us
RE17RMMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMMW | Complementary | release of input voltage | 5 V
RE17RMMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RMMW | Complementary | housing material | Self-extinguishing
RE17RMMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMMW | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMMW | Complementary | voltage drift | +/- 0.2 %/V
RE17RMMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMMW | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMMW | Complementary | reset time | 120 ms on de-energisation typical
RE17RMMW | Complementary | on-load factor | 100 %
RE17RMMW | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17RMMW | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17RMMW | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMMW | Complementary | maximum switching current | 8 A AC/DC
RE17RMMW | Complementary | maximum switching voltage | 250 V AC
RE17RMMW | Complementary | breaking capacity | 2000 VA
RE17RMMW | Complementary | operating frequency | 10 Hz
RE17RMMW | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMMW | Complementary | mechanical durability | 10000000 cycles
RE17RMMW | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMMW | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMMW | Complementary | power on delay | 100 ms
RE17RMMW | Complementary | marking | CE
RE17RMMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMMW | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RMMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMMW | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMMW | Complementary | net weight | 0.07 kg
RE17RMMW | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
RE17RMMW | Complementary | functionality | Multifunction
RE17RMMW | Complementary | compatibility code | RE17
RE17RMMW | Environment | immunity to microbreaks | 20 ms
RE17RMMW | Environment | standards | 2006/95/EC ¦ EN 61000-6-3 ¦ IEC 61812-1 ¦ EN 61000-6-2 ¦ EN 61000-6-1 ¦ 2004/108/EC ¦ EN 61000-6-4
RE17RMMW | Environment | product certifications | CSA ¦ GL ¦ CULus
RE17RMMW | Environment | ambient air temperature for storage | -30…60 °C
RE17RMMW | Environment | ambient air temperature for operation | -20…60 °C
RE17RMMW | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMMW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMMW | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMMW | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMMW | Offer Sustainability | Mercury free | Yes
RE17RMMW | Offer Sustainability | RoHS exemption information | Yes
RE17RMMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMMW | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMMWS | Main | range of product | Zelio Time
RE17RMMWS | Main | product or component type | Modular timing relay
RE17RMMWS | Main | discrete output type | Relay
RE17RMMWS | Main | width | 17.5 mm
RE17RMMWS | Main | device short name | RE17R
RE17RMMWS | Main | time delay type | D ¦ B ¦ At ¦ Bw ¦ Ac ¦ A ¦ Di ¦ Ht ¦ C ¦ H
RE17RMMWS | Main | time delay range | 6...60 min ¦ 6...60 s ¦ 1...10 min ¦ 1...10 h ¦ 0.1...1 s ¦ 10...100 h ¦ 1...10 s
RE17RMMWS | Main | nominal output current | 8 A
RE17RMMWS | Complementary | contacts type and composition | 1 C/O
RE17RMMWS | Complementary | contacts material | Cadmium free
RE17RMMWS | Complementary | height | 90 mm
RE17RMMWS | Complementary | depth | 72 mm
RE17RMMWS | Complementary | control type | Selector switch front panel
RE17RMMWS | Complementary | [Us] rated supply voltage | 12...240 V AC/DC 50/60 Hz
RE17RMMWS | Complementary | voltage range | 0.85...1.1 Us
RE17RMMWS | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMMWS | Complementary | release of input voltage | 5 V
RE17RMMWS | Complementary | connections - terminals | Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) solid without cable end ¦ Spring terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMMWS | Complementary | housing material | Self-extinguishing
RE17RMMWS | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMMWS | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMMWS | Complementary | voltage drift | +/- 0.2 %/V
RE17RMMWS | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMMWS | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMMWS | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMMWS | Complementary | reset time | 120 ms on de-energisation typical
RE17RMMWS | Complementary | on-load factor | 100 %
RE17RMMWS | Complementary | power consumption in VA | 0…3 VA at 240 V AC
RE17RMMWS | Complementary | maximum power consumption in W | 1.5 W at 240 V DC
RE17RMMWS | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMMWS | Complementary | maximum switching current | 8 A AC/DC
RE17RMMWS | Complementary | maximum switching voltage | 250 V AC
RE17RMMWS | Complementary | breaking capacity | 2000 VA
RE17RMMWS | Complementary | operating frequency | 10 Hz
RE17RMMWS | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMMWS | Complementary | mechanical durability | 10000000 cycles
RE17RMMWS | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMMWS | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMMWS | Complementary | power on delay | 100 ms
RE17RMMWS | Complementary | marking | CE
RE17RMMWS | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMMWS | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RMMWS | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMMWS | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMMWS | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMMWS | Complementary | net weight | 0.07 kg
RE17RMMWS | Complementary | time delay type | A, Ac, At, B, Bw, C, D, Di, H, Ht
RE17RMMWS | Complementary | functionality | Multifunction
RE17RMMWS | Complementary | compatibility code | RE17
RE17RMMWS | Environment | immunity to microbreaks | 20 ms
RE17RMMWS | Environment | standards | 2006/95/EC ¦ EN 61000-6-4 ¦ 2004/108/EC ¦ EN 61000-6-3 ¦ IEC 61812-1 ¦ EN 61000-6-2 ¦ EN 61000-6-1
RE17RMMWS | Environment | product certifications | GL ¦ CULus ¦ CSA
RE17RMMWS | Environment | ambient air temperature for storage | -30…60 °C
RE17RMMWS | Environment | ambient air temperature for operation | -20…60 °C
RE17RMMWS | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMMWS | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMMWS | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMMWS | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMMWS | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMMWS | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMMWS | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMMWS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMMWS | Offer Sustainability | Mercury free | Yes
RE17RMMWS | Offer Sustainability | RoHS exemption information | Yes
RE17RMMWS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMMWS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMMWS | Offer Sustainability | Circularity Profile | End of Life Information
RE17RMXMU | Main | range of product | Zelio Time
RE17RMXMU | Main | product or component type | Modular timing relay
RE17RMXMU | Main | discrete output type | Relay
RE17RMXMU | Main | width | 17.5 mm
RE17RMXMU | Main | device short name | RE17R
RE17RMXMU | Main | time delay type | Ah ¦ Tl ¦ N ¦ Tt ¦ Ad ¦ Pt ¦ O ¦ W ¦ P
RE17RMXMU | Main | time delay range | 6...60 s ¦ 1...10 min ¦ 0.1...1 s ¦ 1...10 h ¦ 1...10 s ¦ 6...60 min ¦ 10...100 h
RE17RMXMU | Main | nominal output current | 8 A
RE17RMXMU | Complementary | contacts type and composition | 1 C/O
RE17RMXMU | Complementary | contacts material | Cadmium free
RE17RMXMU | Complementary | height | 90 mm
RE17RMXMU | Complementary | depth | 72 mm
RE17RMXMU | Complementary | control type | Selector switch front panel
RE17RMXMU | Complementary | [Us] rated supply voltage | 24...240 V AC 50/60 Hz ¦ 24 V DC
RE17RMXMU | Complementary | voltage range | 0.85...1.1 Us
RE17RMXMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE17RMXMU | Complementary | release of input voltage | 10 V
RE17RMXMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE17RMXMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE17RMXMU | Complementary | housing material | Self-extinguishing
RE17RMXMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE17RMXMU | Complementary | temperature drift | +/- 0.05 %/°C
RE17RMXMU | Complementary | voltage drift | +/- 0.2 %/V
RE17RMXMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE17RMXMU | Complementary | control signal pulse width | 100 ms with load in parallel typical ¦ 30 ms typical
RE17RMXMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE17RMXMU | Complementary | reset time | 120 ms on de-energisation typical
RE17RMXMU | Complementary | on-load factor | 100 %
RE17RMXMU | Complementary | power consumption in VA | 0…32 VA at 240 V AC
RE17RMXMU | Complementary | maximum power consumption in W | 0.6 W at 24 V DC
RE17RMXMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE17RMXMU | Complementary | maximum switching current | 8 A AC/DC
RE17RMXMU | Complementary | maximum switching voltage | 250 V AC
RE17RMXMU | Complementary | breaking capacity | 2000 VA
RE17RMXMU | Complementary | operating frequency | 10 Hz
RE17RMXMU | Complementary | electrical durability | 100000 cycles (8 A at 250 V AC maximum) for resistive load
RE17RMXMU | Complementary | mechanical durability | 10000000 cycles
RE17RMXMU | Complementary | dielectric strength | 2.5 kV 1 mA/1 minute 50 Hz conforming to IEC 61812-1
RE17RMXMU | Complementary | [Uimp] rated impulse withstand voltage | 5 kV during 1.2/50 µs
RE17RMXMU | Complementary | power on delay | 100 ms
RE17RMXMU | Complementary | marking | CE
RE17RMXMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE17RMXMU | Complementary | safety reliability data | MTTFd = 296.8 years ¦ B10d = 270000
RE17RMXMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE17RMXMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE17RMXMU | Complementary | local signalling | LED indicator for on steady: relay energised, no timing in progress ¦ LED indicator for flashing: timing in progress 80 % ON and 20 % OFF ¦ LED indicator for pulsing: relay de-energised, no timing in progress (except function Di-D, Li-L) 5 % ON and 95 % OFF
RE17RMXMU | Complementary | net weight | 0.07 kg
RE17RMXMU | Complementary | time delay type | Ad, Ah, N, O, P, Pt, TI, Tt, W
RE17RMXMU | Complementary | functionality | Multifunction
RE17RMXMU | Complementary | compatibility code | RE17
RE17RMXMU | Environment | immunity to microbreaks | 20 ms
RE17RMXMU | Environment | standards | 2006/95/EC ¦ 2004/108/EC ¦ EN 61000-6-1 ¦ EN 61000-6-4 ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ IEC 61812-1
RE17RMXMU | Environment | product certifications | CULus ¦ GL ¦ CSA
RE17RMXMU | Environment | ambient air temperature for storage | -30…60 °C
RE17RMXMU | Environment | ambient air temperature for operation | -20…60 °C
RE17RMXMU | Environment | IP degree of protection | IP20 (terminal block) conforming to IEC 60529 ¦ IP40 (housing) conforming to IEC 60529 ¦ IP50 (front panel) conforming to IEC 60529
RE17RMXMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE17RMXMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE17RMXMU | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-30
RE17RMXMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test: (in contact), level 3, 6 kV, conforming to IEC 61000-4-2 ¦ Electrostatic discharge immunity test: (in air), level 3, 8 kV, conforming to IEC 61000-4-2 ¦ Susceptibility to electromagnetic fields: (80 MHz to 1 GHz), level 3, 10 V/m, conforming to IEC 61000-4-3 ¦ Electrical fast transient/burst immunity test: (capacitive connecting clip), level 3, 1 kV, conforming to IEC 61000-4-4 ¦ Electrical fast transient/burst immunity test: (direct), level 3, 2 kV, conforming to IEC 61000-4-4 ¦ 1.2/50 µs shock waves immunity test: (differential mode), level 3, 1 kV, conforming to IEC 61000-4-5 ¦ 1.2/50 µs shock waves immunity test: (common mode), level 3, 2 kV, conforming to IEC 61000-4-5 ¦ Conducted RF disturbances: (0.15...80 MHz), level 3, 10 V, conforming to IEC 61000-4-6 ¦ Voltage dips and interruptions immunity test: (1 cycle), 0 %, conforming to IEC 61000-4-11 ¦ Voltage dips and interruptions immunity test: (25/30 cycles), 70 %, conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions: , class B, conforming to EN 55022
RE17RMXMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE17RMXMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE17RMXMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE17RMXMU | Offer Sustainability | Mercury free | Yes
RE17RMXMU | Offer Sustainability | RoHS exemption information | Yes
RE17RMXMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE17RMXMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE17RMXMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1QMU | Main | range of product | Zelio Time
RE22R1QMU | Main | product or component type | Modular timing relay
RE22R1QMU | Main | discrete output type | Relay
RE22R1QMU | Main | device short name | RE22
RE22R1QMU | Main | nominal output current | 8 A
RE22R1QMU | Complementary | contacts type and composition | 1 C/O timed contact
RE22R1QMU | Complementary | time delay type | Q
RE22R1QMU | Complementary | time delay range | 1...10 min ¦ 6...60 s ¦ 0.1...1 s ¦ 1...10 h ¦ 1...10 s ¦ 6...60 min ¦ 10...100 h
RE22R1QMU | Complementary | control type | Rotary knob front panel
RE22R1QMU | Complementary | [Us] rated supply voltage | 24...240 V AC ¦ 24 V DC
RE22R1QMU | Complementary | voltage range | 0.85...1.1 Us
RE22R1QMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1QMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R1QMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1QMU | Complementary | housing material | Self-extinguishing
RE22R1QMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1QMU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1QMU | Complementary | voltage drift | +/- 0.2 %/V
RE22R1QMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1QMU | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R1QMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1QMU | Complementary | Recovery time | 120 ms on de-energisation
RE22R1QMU | Complementary | immunity to microbreaks | 10 ms
RE22R1QMU | Complementary | power consumption in VA | 50 VA at 240 V AC
RE22R1QMU | Complementary | power consumption in W | 0.7 W at 24 V DC
RE22R1QMU | Complementary | breaking capacity | 2000 VA
RE22R1QMU | Complementary | minimum switching current | 10 mA at 5 V
RE22R1QMU | Complementary | maximum switching current | 8 mA
RE22R1QMU | Complementary | maximum switching voltage | 250 V
RE22R1QMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R1QMU | Complementary | mechanical durability | 10000000 cycles
RE22R1QMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R1QMU | Complementary | Power on delay | 100 ms
RE22R1QMU | Complementary | safety reliability data | MTTFd = 182.6 years ¦ B10d = 170000
RE22R1QMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R1QMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1QMU | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R1QMU | Complementary | width | 22.5 mm
RE22R1QMU | Complementary | net weight | 0.086 kg
RE22R1QMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R1QMU | Environment | standards | EN 61000-6-4 ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 61000-6-1 ¦ IEC 61812-1
RE22R1QMU | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1QMU | Environment | product certifications | CSA ¦ China RoHS ¦ EAC ¦ RCM ¦ CE ¦ CCC ¦ GL ¦ CULus
RE22R1QMU | Environment | ambient air temperature for operation | -20…60 °C
RE22R1QMU | Environment | ambient air temperature for storage | -30…60 °C
RE22R1QMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R1QMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1QMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R1QMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R1QMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R1QMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1QMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1QMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1QMU | Offer Sustainability | Mercury free | Yes
RE22R1QMU | Offer Sustainability | RoHS exemption information | Yes
RE22R1QMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1QMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1QMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1QMQ | Main | range of product | Zelio Time
RE22R1QMQ | Main | product or component type | Modular timing relay
RE22R1QMQ | Main | discrete output type | Relay
RE22R1QMQ | Main | device short name | RE22
RE22R1QMQ | Main | nominal output current | 8 A
RE22R1QMQ | Complementary | contacts type and composition | 1 C/O timed contact
RE22R1QMQ | Complementary | time delay type | Q
RE22R1QMQ | Complementary | time delay range | 1...10 h ¦ 10...100 h ¦ 6...60 s ¦ 1...10 min ¦ 0.1...1 s ¦ 1...10 s ¦ 6...60 min
RE22R1QMQ | Complementary | control type | Rotary knob front panel
RE22R1QMQ | Complementary | [Us] rated supply voltage | 380...440 V AC ¦ 230...240 V AC
RE22R1QMQ | Complementary | voltage range | 0.85...1.1 Us
RE22R1QMQ | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1QMQ | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R1QMQ | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1QMQ | Complementary | housing material | Self-extinguishing
RE22R1QMQ | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1QMQ | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1QMQ | Complementary | voltage drift | +/- 0.2 %/V
RE22R1QMQ | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1QMQ | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R1QMQ | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1QMQ | Complementary | Recovery time | 120 ms on de-energisation
RE22R1QMQ | Complementary | immunity to microbreaks | 10 ms
RE22R1QMQ | Complementary | power consumption in VA | 8 VA at 230...240 V ¦ 17 VA at 380...440 V
RE22R1QMQ | Complementary | breaking capacity | 2000 VA
RE22R1QMQ | Complementary | minimum switching current | 10 mA at 5 V
RE22R1QMQ | Complementary | maximum switching current | 8 mA
RE22R1QMQ | Complementary | maximum switching voltage | 250 V
RE22R1QMQ | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R1QMQ | Complementary | mechanical durability | 10000000 cycles
RE22R1QMQ | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R1QMQ | Complementary | Power on delay | 100 ms
RE22R1QMQ | Complementary | safety reliability data | B10d = 260000 ¦ MTTFd = 273.9 years
RE22R1QMQ | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R1QMQ | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1QMQ | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R1QMQ | Complementary | width | 22.5 mm
RE22R1QMQ | Complementary | net weight | 0.093 kg
RE22R1QMQ | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R1QMQ | Environment | standards | EN 61000-6-4 ¦ IEC 61812-1 ¦ EN 61000-6-1 ¦ EN 61000-6-3 ¦ EN 61000-6-2
RE22R1QMQ | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1QMQ | Environment | product certifications | CULus ¦ RCM ¦ CSA ¦ China RoHS ¦ EAC ¦ GL ¦ CCC ¦ CE
RE22R1QMQ | Environment | ambient air temperature for operation | -20…60 °C
RE22R1QMQ | Environment | ambient air temperature for storage | -30…60 °C
RE22R1QMQ | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R1QMQ | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1QMQ | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R1QMQ | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R1QMQ | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R1QMQ | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1QMQ | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1QMQ | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1QMQ | Offer Sustainability | Mercury free | Yes
RE22R1QMQ | Offer Sustainability | RoHS exemption information | Yes
RE22R1QMQ | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1QMQ | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1QMQ | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2AMU | Main | range of product | Zelio Time
RE22R2AMU | Main | product or component type | Modular timing relay
RE22R2AMU | Main | discrete output type | Relay
RE22R2AMU | Main | device short name | RE22
RE22R2AMU | Main | nominal output current | 8 A
RE22R2AMU | Complementary | contacts type and composition | 2 C/O timed contact
RE22R2AMU | Complementary | time delay type | At ¦ A
RE22R2AMU | Complementary | time delay range | 1...10 min ¦ 10...100 h ¦ 1...10 s ¦ 0.1...1 s ¦ 6...60 s ¦ 6...60 min ¦ 1...10 h
RE22R2AMU | Complementary | control type | Rotary knob front panel
RE22R2AMU | Complementary | [Us] rated supply voltage | 24...240 V AC ¦ 24 V DC
RE22R2AMU | Complementary | voltage range | 0.85...1.1 Us
RE22R2AMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2AMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R2AMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2AMU | Complementary | housing material | Self-extinguishing
RE22R2AMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2AMU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2AMU | Complementary | voltage drift | +/- 0.2 %/V
RE22R2AMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2AMU | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R2AMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2AMU | Complementary | Recovery time | 120 ms on de-energisation
RE22R2AMU | Complementary | immunity to microbreaks | 10 ms
RE22R2AMU | Complementary | power consumption in VA | 50 VA at 240 V AC
RE22R2AMU | Complementary | power consumption in W | 0.7 W at 24 V DC
RE22R2AMU | Complementary | breaking capacity | 2000 VA
RE22R2AMU | Complementary | minimum switching current | 10 mA at 5 V
RE22R2AMU | Complementary | maximum switching current | 8 mA
RE22R2AMU | Complementary | maximum switching voltage | 250 V
RE22R2AMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R2AMU | Complementary | mechanical durability | 10000000 cycles
RE22R2AMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R2AMU | Complementary | Power on delay | 100 ms
RE22R2AMU | Complementary | safety reliability data | MTTFd = 182.6 years ¦ B10d = 170000
RE22R2AMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R2AMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2AMU | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R2AMU | Complementary | width | 22.5 mm
RE22R2AMU | Complementary | net weight | 0.09 kg
RE22R2AMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R2AMU | Environment | standards | EN 61000-6-3 ¦ EN 61000-6-4 ¦ EN 61000-6-2 ¦ IEC 61812-1 ¦ EN 61000-6-1
RE22R2AMU | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2AMU | Environment | product certifications | CULus ¦ CE ¦ EAC ¦ CSA ¦ RCM ¦ CCC ¦ China RoHS ¦ GL
RE22R2AMU | Environment | ambient air temperature for operation | -20…60 °C
RE22R2AMU | Environment | ambient air temperature for storage | -30…60 °C
RE22R2AMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R2AMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2AMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R2AMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R2AMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R2AMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2AMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2AMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2AMU | Offer Sustainability | Mercury free | Yes
RE22R2AMU | Offer Sustainability | RoHS exemption information | Yes
RE22R2AMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2AMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2AMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MJU | Main | range of product | Zelio Time
RE22R2MJU | Main | product or component type | Modular timing relay
RE22R2MJU | Main | discrete output type | Relay
RE22R2MJU | Main | device short name | RE22
RE22R2MJU | Main | nominal output current | 8 A
RE22R2MJU | Complementary | contacts type and composition | 1 C/O timed contact ¦ 1 C/O timed or instantaneous contact
RE22R2MJU | Complementary | time delay type | B ¦ C ¦ Di ¦ Ht ¦ Bw ¦ Ac ¦ H ¦ At ¦ A ¦ D
RE22R2MJU | Complementary | time delay range | 1...10 min ¦ 6...60 min ¦ 0.1...1 s ¦ 6...60 s ¦ 1...10 s ¦ 1...10 h ¦ 10...100 h
RE22R2MJU | Complementary | control type | Rotary knob front panel
RE22R2MJU | Complementary | [Us] rated supply voltage | 12 V AC/DC
RE22R2MJU | Complementary | voltage range | 0.9...1.2 Us
RE22R2MJU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MJU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R2MJU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MJU | Complementary | housing material | Self-extinguishing
RE22R2MJU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MJU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MJU | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MJU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MJU | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R2MJU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MJU | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MJU | Complementary | immunity to microbreaks | 10 ms
RE22R2MJU | Complementary | power consumption in VA | 1.2 VA at 12 V AC
RE22R2MJU | Complementary | power consumption in W | 0.5 W at 12 V DC
RE22R2MJU | Complementary | breaking capacity | 2000 VA
RE22R2MJU | Complementary | minimum switching current | 10 mA at 5 V
RE22R2MJU | Complementary | maximum switching current | 8 mA
RE22R2MJU | Complementary | maximum switching voltage | 250 V
RE22R2MJU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R2MJU | Complementary | mechanical durability | 10000000 cycles
RE22R2MJU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R2MJU | Complementary | Power on delay | 100 ms
RE22R2MJU | Complementary | safety reliability data | B10d = 190000 ¦ MTTFd = 205.4 years
RE22R2MJU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R2MJU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MJU | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R2MJU | Complementary | width | 22.5 mm
RE22R2MJU | Complementary | net weight | 0.09 kg
RE22R2MJU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R2MJU | Environment | standards | EN 61000-6-1 ¦ IEC 61812-1 ¦ EN 61000-6-4 ¦ EN 61000-6-3 ¦ EN 61000-6-2
RE22R2MJU | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2MJU | Environment | product certifications | CSA ¦ CULus ¦ China RoHS ¦ CE ¦ EAC ¦ GL ¦ CCC ¦ RCM
RE22R2MJU | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MJU | Environment | ambient air temperature for storage | -30…60 °C
RE22R2MJU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R2MJU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MJU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R2MJU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R2MJU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R2MJU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MJU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MJU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MJU | Offer Sustainability | Mercury free | Yes
RE22R2MJU | Offer Sustainability | RoHS exemption information | Yes
RE22R2MJU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MJU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MJU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MMW | Main | range of product | Zelio Time
RE22R2MMW | Main | product or component type | Modular timing relay
RE22R2MMW | Main | discrete output type | Relay
RE22R2MMW | Main | device short name | RE22
RE22R2MMW | Main | nominal output current | 8 A
RE22R2MMW | Complementary | contacts type and composition | 1 C/O timed contact ¦ 1 C/O timed or instantaneous contact
RE22R2MMW | Complementary | time delay type | C ¦ Di ¦ D ¦ B ¦ At ¦ H ¦ Bw ¦ Ac ¦ A
RE22R2MMW | Complementary | time delay range | 0.1...1 s ¦ 6...60 s ¦ 1...10 h ¦ 1...10 min ¦ 1...10 s ¦ 10...100 h ¦ 6...60 min
RE22R2MMW | Complementary | control type | Rotary knob front panel
RE22R2MMW | Complementary | [Us] rated supply voltage | 12...240 V AC/DC
RE22R2MMW | Complementary | voltage range | 0.85...1.1 Us
RE22R2MMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MMW | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R2MMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MMW | Complementary | housing material | Self-extinguishing
RE22R2MMW | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MMW | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MMW | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MMW | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MMW | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R2MMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MMW | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MMW | Complementary | immunity to microbreaks | 10 ms
RE22R2MMW | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2MMW | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2MMW | Complementary | breaking capacity | 2000 VA
RE22R2MMW | Complementary | minimum switching current | 10 mA at 5 V
RE22R2MMW | Complementary | maximum switching current | 8 mA
RE22R2MMW | Complementary | maximum switching voltage | 250 V
RE22R2MMW | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R2MMW | Complementary | mechanical durability | 10000000 cycles
RE22R2MMW | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R2MMW | Complementary | Power on delay | 100 ms
RE22R2MMW | Complementary | safety reliability data | B10d = 230000 ¦ MTTFd = 251.1 years
RE22R2MMW | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R2MMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MMW | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R2MMW | Complementary | width | 22.5 mm
RE22R2MMW | Complementary | net weight | 0.093 kg
RE22R2MMW | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R2MMW | Environment | standards | IEC 61812-1 ¦ EN 61000-6-2 ¦ EN 61000-6-1 ¦ EN 61000-6-4 ¦ EN 61000-6-3
RE22R2MMW | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2MMW | Environment | product certifications | CSA ¦ CE ¦ CULus ¦ GL ¦ RCM ¦ CCC ¦ China RoHS ¦ EAC
RE22R2MMW | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MMW | Environment | ambient air temperature for storage | -30…60 °C
RE22R2MMW | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R2MMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MMW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R2MMW | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R2MMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R2MMW | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MMW | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MMW | Offer Sustainability | Mercury free | Yes
RE22R2MMW | Offer Sustainability | RoHS exemption information | Yes
RE22R2MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MMW | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MMU | Main | range of product | Zelio Time
RE22R2MMU | Main | product or component type | Modular timing relay
RE22R2MMU | Main | discrete output type | Relay
RE22R2MMU | Main | device short name | RE22
RE22R2MMU | Main | nominal output current | 8 A
RE22R2MMU | Complementary | contacts type and composition | 1 C/O timed contact ¦ 1 C/O timed or instantaneous contact
RE22R2MMU | Complementary | time delay type | Ht ¦ At ¦ Bw ¦ C ¦ Di ¦ B ¦ Ac ¦ H ¦ A ¦ D
RE22R2MMU | Complementary | time delay range | 10...100 h ¦ 6...60 s ¦ 0.1...1 s ¦ 1...10 h ¦ 1...10 s ¦ 1...10 min ¦ 6...60 min
RE22R2MMU | Complementary | control type | Rotary knob front panel
RE22R2MMU | Complementary | [Us] rated supply voltage | 24...240 V AC ¦ 24 V DC
RE22R2MMU | Complementary | voltage range | 0.85...1.1 Us
RE22R2MMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R2MMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MMU | Complementary | housing material | Self-extinguishing
RE22R2MMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MMU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MMU | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MMU | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R2MMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MMU | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MMU | Complementary | immunity to microbreaks | 10 ms
RE22R2MMU | Complementary | power consumption in VA | 50 VA at 240 V AC
RE22R2MMU | Complementary | power consumption in W | 0.7 W at 24 V DC
RE22R2MMU | Complementary | breaking capacity | 2000 VA
RE22R2MMU | Complementary | minimum switching current | 10 mA at 5 V
RE22R2MMU | Complementary | maximum switching current | 8 mA
RE22R2MMU | Complementary | maximum switching voltage | 250 V
RE22R2MMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R2MMU | Complementary | mechanical durability | 10000000 cycles
RE22R2MMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R2MMU | Complementary | Power on delay | 100 ms
RE22R2MMU | Complementary | safety reliability data | MTTFd = 182.6 years ¦ B10d = 170000
RE22R2MMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R2MMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MMU | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R2MMU | Complementary | width | 22.5 mm
RE22R2MMU | Complementary | net weight | 0.09 kg
RE22R2MMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R2MMU | Environment | standards | IEC 61812-1 ¦ EN 61000-6-1 ¦ EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 61000-6-4
RE22R2MMU | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2MMU | Environment | product certifications | CULus ¦ CSA ¦ CE ¦ China RoHS ¦ CCC ¦ RCM ¦ GL ¦ EAC
RE22R2MMU | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MMU | Environment | ambient air temperature for storage | -30…60 °C
RE22R2MMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529
RE22R2MMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R2MMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R2MMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Conducted and radiated emissions class B conforming to EN 55022
RE22R2MMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MMU | Offer Sustainability | Mercury free | Yes
RE22R2MMU | Offer Sustainability | RoHS exemption information | Yes
RE22R2MMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MXMU | Main | range of product | Zelio Time
RE22R2MXMU | Main | product or component type | Modular timing relay
RE22R2MXMU | Main | discrete output type | Relay
RE22R2MXMU | Main | device short name | RE22
RE22R2MXMU | Main | nominal output current | 8 A
RE22R2MXMU | Complementary | contacts type and composition | 1 C/O timed contact ¦ 1 C/O timed or instantaneous contact
RE22R2MXMU | Complementary | time delay type | Pt ¦ O ¦ P ¦ A ¦ Tl ¦ Ah ¦ N ¦ Tt ¦ W
RE22R2MXMU | Complementary | time delay range | 0.1...1 s ¦ 1...10 h ¦ 1...10 s ¦ 6...60 min ¦ 10...100 h ¦ 6...60 s ¦ 1...10 min
RE22R2MXMU | Complementary | control type | Rotary knob front panel
RE22R2MXMU | Complementary | [Us] rated supply voltage | 24...240 V AC ¦ 24 V DC
RE22R2MXMU | Complementary | voltage range | 0.85...1.1 Us
RE22R2MXMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MXMU | Complementary | connections - terminals | Screw terminals, 2 x 1.5 mm² with cable end ¦ Screw terminals, 2 x 2.5 mm² without cable end
RE22R2MXMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MXMU | Complementary | housing material | Self-extinguishing
RE22R2MXMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MXMU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MXMU | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MXMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MXMU | Complementary | Control signal pulse width | 30 ms ¦ 100 ms under load
RE22R2MXMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MXMU | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MXMU | Complementary | immunity to microbreaks | 10 ms
RE22R2MXMU | Complementary | power consumption in VA | 50 VA at 240 V AC
RE22R2MXMU | Complementary | power consumption in W | 0.7 W at 24 V DC
RE22R2MXMU | Complementary | breaking capacity | 2000 VA
RE22R2MXMU | Complementary | minimum switching current | 10 mA at 5 V
RE22R2MXMU | Complementary | maximum switching current | 8 mA
RE22R2MXMU | Complementary | maximum switching voltage | 250 V
RE22R2MXMU | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RE22R2MXMU | Complementary | mechanical durability | 10000000 cycles
RE22R2MXMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 ¦ 5 kV conforming to IEC 61812-1
RE22R2MXMU | Complementary | Power on delay | 100 ms
RE22R2MXMU | Complementary | safety reliability data | B10d = 170000 ¦ MTTFd = 182.6 years
RE22R2MXMU | Complementary | mounting position | Any position in relation to normal vertical mounting plane
RE22R2MXMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MXMU | Complementary | status LED | LED green (flashing) for timing in progress ¦ LED green (steady) for power ON ¦ LED yellow for relay energised
RE22R2MXMU | Complementary | width | 22.5 mm
RE22R2MXMU | Complementary | net weight | 0.09 kg
RE22R2MXMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz conforming to IEC 61812-1
RE22R2MXMU | Environment | standards | IEC 61812-1 ¦ EN 61000-6-1 ¦ EN 61000-6-3 ¦ EN 61000-6-4 ¦ EN 61000-6-2
RE22R2MXMU | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2MXMU | Environment | product certifications | China RoHS ¦ CSA ¦ CCC ¦ GL ¦ CULus ¦ EAC ¦ CE ¦ RCM
RE22R2MXMU | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MXMU | Environment | ambient air temperature for storage | -30…60 °C
RE22R2MXMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminal block: conforming to IEC 60529
RE22R2MXMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MXMU | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60068-2-27
RE22R2MXMU | Environment | relative humidity | 93 %, without condensation conforming to IEC 60068-2-30
RE22R2MXMU | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2MXMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MXMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MXMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MXMU | Offer Sustainability | Mercury free | Yes
RE22R2MXMU | Offer Sustainability | RoHS exemption information | Yes
RE22R2MXMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MXMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MXMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1ACMR | Main | range of product | Zelio Time
RE22R1ACMR | Main | product or component type | Modular timing relay
RE22R1ACMR | Main | discrete output type | Relay
RE22R1ACMR | Main | device short name | RE22
RE22R1ACMR | Main | nominal output current | 8 A
RE22R1ACMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1ACMR | Complementary | time delay type | Ac ¦ Act
RE22R1ACMR | Complementary | time delay range | 3...30 min ¦ 1...10 s ¦ 30...300 s ¦ 10...100 s ¦ 3...30 s ¦ 30...300 min ¦ 30...300 h ¦ 0.3...3 s ¦ 0.05...1 s ¦ 3...30 h
RE22R1ACMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1ACMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1ACMR | Complementary | Release input voltage | <= 2.4 V
RE22R1ACMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1ACMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1ACMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1ACMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1ACMR | Complementary | housing material | Self-extinguishing
RE22R1ACMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1ACMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1ACMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1ACMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1ACMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1ACMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1ACMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1ACMR | Complementary | immunity to microbreaks | 10 ms
RE22R1ACMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1ACMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1ACMR | Complementary | switching capacity in VA | 2000 VA
RE22R1ACMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1ACMR | Complementary | maximum switching current | 8 A
RE22R1ACMR | Complementary | maximum switching voltage | 250 V AC
RE22R1ACMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1ACMR | Complementary | mechanical durability | 10000000 cycles
RE22R1ACMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1ACMR | Complementary | Power on delay | 100 ms
RE22R1ACMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1ACMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1ACMR | Complementary | safety reliability data | B10d = 190000 ¦ MTTFd = 205.4 years
RE22R1ACMR | Complementary | mounting position | Any position
RE22R1ACMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1ACMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1ACMR | Complementary | width | 22.5 mm
RE22R1ACMR | Complementary | net weight | 0.1 kg
RE22R1ACMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1ACMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R1ACMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1ACMR | Environment | product certifications | CE ¦ CCC ¦ GL ¦ UL ¦ China RoHS ¦ CSA ¦ EAC ¦ RCM
RE22R1ACMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1ACMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1ACMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1ACMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1ACMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1ACMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1ACMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1ACMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1ACMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1ACMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1ACMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1ACMR | Offer Sustainability | Mercury free | Yes
RE22R1ACMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1ACMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1ACMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1ACMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1AKMR | Main | range of product | Zelio Time
RE22R1AKMR | Main | product or component type | Modular timing relay
RE22R1AKMR | Main | discrete output type | Relay
RE22R1AKMR | Main | device short name | RE22
RE22R1AKMR | Main | nominal output current | 8 A
RE22R1AKMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1AKMR | Complementary | time delay type | Ak ¦ Akt
RE22R1AKMR | Complementary | time delay range | 30...300 h ¦ 3...30 min ¦ 30...300 s ¦ 0.05...1 s ¦ 30...300 min ¦ 10...100 s ¦ 0.3...3 s ¦ 3...30 h ¦ 1...10 s
RE22R1AKMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1AKMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1AKMR | Complementary | Release input voltage | <= 2.4 V
RE22R1AKMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1AKMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1AKMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1AKMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1AKMR | Complementary | housing material | Self-extinguishing
RE22R1AKMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1AKMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1AKMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1AKMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1AKMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1AKMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1AKMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1AKMR | Complementary | immunity to microbreaks | 10 ms
RE22R1AKMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1AKMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1AKMR | Complementary | switching capacity in VA | 2000 VA
RE22R1AKMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1AKMR | Complementary | maximum switching current | 8 A
RE22R1AKMR | Complementary | maximum switching voltage | 250 V AC
RE22R1AKMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1AKMR | Complementary | mechanical durability | 10000000 cycles
RE22R1AKMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1AKMR | Complementary | Power on delay | 100 ms
RE22R1AKMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1AKMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1AKMR | Complementary | safety reliability data | B10d = 180000 ¦ MTTFd = 194 years
RE22R1AKMR | Complementary | mounting position | Any position
RE22R1AKMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1AKMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1AKMR | Complementary | width | 22.5 mm
RE22R1AKMR | Complementary | net weight | 0.1 kg
RE22R1AKMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1AKMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1AKMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1AKMR | Environment | product certifications | China RoHS ¦ EAC ¦ CSA ¦ UL ¦ RCM ¦ CCC ¦ GL ¦ CE
RE22R1AKMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1AKMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1AKMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1AKMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1AKMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1AKMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1AKMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1AKMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1AKMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1AKMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1AKMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1AKMR | Offer Sustainability | Mercury free | Yes
RE22R1AKMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1AKMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1AKMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1AKMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1AMR | Main | range of product | Zelio Time
RE22R1AMR | Main | product or component type | Modular timing relay
RE22R1AMR | Main | discrete output type | Relay
RE22R1AMR | Main | device short name | RE22
RE22R1AMR | Main | nominal output current | 8 A
RE22R1AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1AMR | Complementary | time delay type | A ¦ Aw
RE22R1AMR | Complementary | time delay range | 3...30 s ¦ 30...300 s ¦ 10...100 s ¦ 0.05...1 s ¦ 1...10 s ¦ 30...300 h ¦ 30...300 min ¦ 0.3...3 s ¦ 3...30 h ¦ 3...30 min
RE22R1AMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R1AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1AMR | Complementary | Release input voltage | <= 2.4 V
RE22R1AMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1AMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1AMR | Complementary | housing material | Self-extinguishing
RE22R1AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1AMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1AMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1AMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1AMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1AMR | Complementary | immunity to microbreaks | 10 ms
RE22R1AMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1AMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1AMR | Complementary | switching capacity in VA | 2000 VA
RE22R1AMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1AMR | Complementary | maximum switching current | 8 A
RE22R1AMR | Complementary | maximum switching voltage | 250 V AC
RE22R1AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1AMR | Complementary | mechanical durability | 10000000 cycles
RE22R1AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1AMR | Complementary | Power on delay | 100 ms
RE22R1AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1AMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1AMR | Complementary | safety reliability data | MTTFd = 308.2 years ¦ B10d = 280000
RE22R1AMR | Complementary | mounting position | Any position
RE22R1AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1AMR | Complementary | width | 22.5 mm
RE22R1AMR | Complementary | net weight | 0.1 kg
RE22R1AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1AMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1AMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1AMR | Environment | product certifications | CE ¦ UL ¦ GL ¦ CCC ¦ China RoHS ¦ EAC ¦ RCM ¦ CSA
RE22R1AMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1AMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1AMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1AMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1AMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1AMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1AMR | Offer Sustainability | Mercury free | Yes
RE22R1AMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1AMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1CMR | Main | range of product | Zelio Time
RE22R1CMR | Main | product or component type | Modular timing relay
RE22R1CMR | Main | discrete output type | Relay
RE22R1CMR | Main | device short name | RE22
RE22R1CMR | Main | nominal output current | 8 A
RE22R1CMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1CMR | Complementary | time delay type | C ¦ Ct
RE22R1CMR | Complementary | time delay range | 10...100 s ¦ 3...30 s ¦ 0.05...1 s ¦ 30...300 s ¦ 30...300 h ¦ 30...300 min ¦ 3...30 min ¦ 3...30 h ¦ 0.3...3 s ¦ 1...10 s
RE22R1CMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1CMR | Complementary | Release input voltage | <= 2.4 V
RE22R1CMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1CMR | Complementary | housing material | Self-extinguishing
RE22R1CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1CMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1CMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1CMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1CMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1CMR | Complementary | immunity to microbreaks | 10 ms
RE22R1CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1CMR | Complementary | switching capacity in VA | 2000 VA
RE22R1CMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1CMR | Complementary | maximum switching current | 8 A
RE22R1CMR | Complementary | maximum switching voltage | 250 V AC
RE22R1CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1CMR | Complementary | mechanical durability | 10000000 cycles
RE22R1CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1CMR | Complementary | Power on delay | 100 ms
RE22R1CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1CMR | Complementary | safety reliability data | MTTFd = 205.4 years ¦ B10d = 190000
RE22R1CMR | Complementary | mounting position | Any position
RE22R1CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1CMR | Complementary | width | 22.5 mm
RE22R1CMR | Complementary | net weight | 0.1 kg
RE22R1CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1CMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1CMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1CMR | Environment | product certifications | UL ¦ CE ¦ CCC ¦ CSA ¦ China RoHS ¦ GL ¦ RCM ¦ EAC
RE22R1CMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1CMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1CMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1CMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1CMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1CMR | Offer Sustainability | Mercury free | Yes
RE22R1CMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1CMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1CMR | Main | range of product | Zelio Time
RE22R1CMR | Main | product or component type | Modular timing relay
RE22R1CMR | Main | discrete output type | Relay
RE22R1CMR | Main | device short name | RE22
RE22R1CMR | Main | nominal output current | 8 A
RE22R1CMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1CMR | Complementary | time delay type | C ¦ Ct
RE22R1CMR | Complementary | time delay range | 10...100 s ¦ 3...30 s ¦ 0.05...1 s ¦ 30...300 s ¦ 30...300 h ¦ 30...300 min ¦ 3...30 min ¦ 3...30 h ¦ 0.3...3 s ¦ 1...10 s
RE22R1CMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1CMR | Complementary | Release input voltage | <= 2.4 V
RE22R1CMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1CMR | Complementary | housing material | Self-extinguishing
RE22R1CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1CMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1CMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1CMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1CMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1CMR | Complementary | immunity to microbreaks | 10 ms
RE22R1CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1CMR | Complementary | switching capacity in VA | 2000 VA
RE22R1CMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1CMR | Complementary | maximum switching current | 8 A
RE22R1CMR | Complementary | maximum switching voltage | 250 V AC
RE22R1CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1CMR | Complementary | mechanical durability | 10000000 cycles
RE22R1CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1CMR | Complementary | Power on delay | 100 ms
RE22R1CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1CMR | Complementary | safety reliability data | MTTFd = 205.4 years ¦ B10d = 190000
RE22R1CMR | Complementary | mounting position | Any position
RE22R1CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1CMR | Complementary | width | 22.5 mm
RE22R1CMR | Complementary | net weight | 0.1 kg
RE22R1CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1CMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1CMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1CMR | Environment | product certifications | UL ¦ CE ¦ CCC ¦ CSA ¦ China RoHS ¦ GL ¦ RCM ¦ EAC
RE22R1CMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1CMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1CMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1CMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1CMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1CMR | Offer Sustainability | Mercury free | Yes
RE22R1CMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1CMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1DMR | Main | range of product | Zelio Time
RE22R1DMR | Main | product or component type | Modular timing relay
RE22R1DMR | Main | discrete output type | Relay
RE22R1DMR | Main | device short name | RE22
RE22R1DMR | Main | nominal output current | 8 A
RE22R1DMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1DMR | Complementary | time delay type | Dw ¦ D
RE22R1DMR | Complementary | time delay range | 0.05...1 s ¦ 30...300 h ¦ 30...300 min ¦ 30...300 s ¦ 3...30 min ¦ 1...10 s ¦ 3...30 s ¦ 0.3...3 s ¦ 10...100 s ¦ 3...30 h
RE22R1DMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R1DMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1DMR | Complementary | Release input voltage | <= 2.4 V
RE22R1DMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1DMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1DMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1DMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1DMR | Complementary | housing material | Self-extinguishing
RE22R1DMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1DMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1DMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1DMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1DMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1DMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1DMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1DMR | Complementary | immunity to microbreaks | 10 ms
RE22R1DMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1DMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1DMR | Complementary | switching capacity in VA | 2000 VA
RE22R1DMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1DMR | Complementary | maximum switching current | 8 A
RE22R1DMR | Complementary | maximum switching voltage | 250 V AC
RE22R1DMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1DMR | Complementary | mechanical durability | 10000000 cycles
RE22R1DMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1DMR | Complementary | Power on delay | 100 ms
RE22R1DMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1DMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1DMR | Complementary | safety reliability data | B10d = 280000 ¦ MTTFd = 308.2 years
RE22R1DMR | Complementary | mounting position | Any position
RE22R1DMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1DMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1DMR | Complementary | width | 22.5 mm
RE22R1DMR | Complementary | net weight | 0.1 kg
RE22R1DMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1DMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1DMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1DMR | Environment | product certifications | China RoHS ¦ GL ¦ EAC ¦ UL ¦ CCC ¦ CSA ¦ CE ¦ RCM
RE22R1DMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1DMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1DMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1DMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1DMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1DMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1DMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1DMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1DMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1DMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1DMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1DMR | Offer Sustainability | Mercury free | Yes
RE22R1DMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1DMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1DMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1DMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1HMR | Main | range of product | Zelio Time
RE22R1HMR | Main | product or component type | Modular timing relay
RE22R1HMR | Main | discrete output type | Relay
RE22R1HMR | Main | device short name | RE22
RE22R1HMR | Main | nominal output current | 8 A
RE22R1HMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1HMR | Complementary | time delay type | Hw ¦ H
RE22R1HMR | Complementary | time delay range | 3...30 s ¦ 0.3...3 s ¦ 30...300 s ¦ 30...300 h ¦ 0.05...1 s ¦ 1...10 s ¦ 3...30 min ¦ 30...300 min ¦ 3...30 h ¦ 10...100 s
RE22R1HMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R1HMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1HMR | Complementary | Release input voltage | <= 2.4 V
RE22R1HMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1HMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1HMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1HMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1HMR | Complementary | housing material | Self-extinguishing
RE22R1HMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1HMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1HMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1HMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1HMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1HMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1HMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1HMR | Complementary | immunity to microbreaks | 10 ms
RE22R1HMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1HMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1HMR | Complementary | switching capacity in VA | 2000 VA
RE22R1HMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1HMR | Complementary | maximum switching current | 8 A
RE22R1HMR | Complementary | maximum switching voltage | 250 V AC
RE22R1HMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1HMR | Complementary | mechanical durability | 10000000 cycles
RE22R1HMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1HMR | Complementary | Power on delay | 100 ms
RE22R1HMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1HMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1HMR | Complementary | safety reliability data | B10d = 280000 ¦ MTTFd = 308.2 years
RE22R1HMR | Complementary | mounting position | Any position
RE22R1HMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1HMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1HMR | Complementary | width | 22.5 mm
RE22R1HMR | Complementary | net weight | 0.1 kg
RE22R1HMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1HMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1HMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1HMR | Environment | product certifications | CE ¦ EAC ¦ CSA ¦ RCM ¦ China RoHS ¦ CCC ¦ GL ¦ UL
RE22R1HMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1HMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1HMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1HMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1HMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1HMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1HMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1HMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1HMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1HMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1HMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1HMR | Offer Sustainability | Mercury free | Yes
RE22R1HMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1HMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1HMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1HMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1KMR | Main | range of product | Zelio Time
RE22R1KMR | Main | product or component type | Modular timing relay
RE22R1KMR | Main | discrete output type | Relay
RE22R1KMR | Main | device short name | RE22
RE22R1KMR | Main | nominal output current | 5 A
RE22R1KMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1KMR | Complementary | time delay type | K
RE22R1KMR | Complementary | time delay range | 10...100 s ¦ 1...10 min ¦ 1...10 s ¦ 0.3...3 s ¦ 3...30 s ¦ 0.05...1 s ¦ 30...300 s
RE22R1KMR | Complementary | control type | Rotary knob
RE22R1KMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1KMR | Complementary | Release input voltage | <= 2.4 V
RE22R1KMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1KMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1KMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1KMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1KMR | Complementary | housing material | Self-extinguishing
RE22R1KMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1KMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1KMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1KMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1KMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1KMR | Complementary | Recovery time | 100 ms on de-energisation
RE22R1KMR | Complementary | immunity to microbreaks | 10 ms
RE22R1KMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1KMR | Complementary | power consumption in W | 2 W at 240 V DC
RE22R1KMR | Complementary | switching capacity in VA | 1250 VA
RE22R1KMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1KMR | Complementary | maximum switching current | 5 A
RE22R1KMR | Complementary | maximum switching voltage | 250 V AC
RE22R1KMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 ¦ 100000 cycles, 5 A at 250 V, AC-1
RE22R1KMR | Complementary | mechanical durability | 10000000 cycles
RE22R1KMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1KMR | Complementary | Power on delay | 200 ms
RE22R1KMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1KMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1KMR | Complementary | safety reliability data | MTTFd = 194 years ¦ B10d = 180000
RE22R1KMR | Complementary | mounting position | Any position
RE22R1KMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1KMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (steady) for power ON
RE22R1KMR | Complementary | width | 22.5 mm
RE22R1KMR | Complementary | net weight | 0.1 kg
RE22R1KMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1KMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R1KMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1KMR | Environment | product certifications | CCC ¦ CSA ¦ GL ¦ China RoHS ¦ RCM ¦ CE ¦ EAC ¦ UL
RE22R1KMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1KMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1KMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1KMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1KMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1KMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1KMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1KMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1KMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1KMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1KMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1KMR | Offer Sustainability | Mercury free | Yes
RE22R1KMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1KMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1KMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1KMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1MAMR | Main | range of product | Zelio Time
RE22R1MAMR | Main | product or component type | Modular timing relay
RE22R1MAMR | Main | discrete output type | Relay
RE22R1MAMR | Main | device short name | RE22
RE22R1MAMR | Main | nominal output current | 8 A
RE22R1MAMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1MAMR | Complementary | time delay type | A ¦ At ¦ Aw
RE22R1MAMR | Complementary | time delay range | 3...30 h ¦ 0.05...1 s ¦ 30...300 s ¦ 3...30 min ¦ 3...30 s ¦ 30...300 h ¦ 30...300 min ¦ 0.3...3 s ¦ 10...100 s ¦ 1...10 s
RE22R1MAMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1MAMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1MAMR | Complementary | Release input voltage | <= 2.4 V
RE22R1MAMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1MAMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1MAMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1MAMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1MAMR | Complementary | housing material | Self-extinguishing
RE22R1MAMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1MAMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1MAMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1MAMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1MAMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1MAMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1MAMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1MAMR | Complementary | immunity to microbreaks | 10 ms
RE22R1MAMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1MAMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1MAMR | Complementary | switching capacity in VA | 2000 VA
RE22R1MAMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1MAMR | Complementary | maximum switching current | 8 A
RE22R1MAMR | Complementary | maximum switching voltage | 250 V AC
RE22R1MAMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1MAMR | Complementary | mechanical durability | 10000000 cycles
RE22R1MAMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1MAMR | Complementary | Power on delay | 100 ms
RE22R1MAMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1MAMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1MAMR | Complementary | safety reliability data | B10d = 190000 ¦ MTTFd = 205.4 years
RE22R1MAMR | Complementary | mounting position | Any position
RE22R1MAMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1MAMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1MAMR | Complementary | width | 22.5 mm
RE22R1MAMR | Complementary | net weight | 0.1 kg
RE22R1MAMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1MAMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1MAMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1MAMR | Environment | product certifications | EAC ¦ CSA ¦ RCM ¦ UL ¦ China RoHS ¦ GL ¦ CE ¦ CCC
RE22R1MAMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1MAMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1MAMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1MAMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1MAMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1MAMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1MAMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1MAMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1MAMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1MAMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1MAMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1MAMR | Offer Sustainability | Mercury free | Yes
RE22R1MAMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1MAMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1MAMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1MAMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1MKMR | Main | range of product | Zelio Time
RE22R1MKMR | Main | product or component type | Modular timing relay
RE22R1MKMR | Main | discrete output type | Relay
RE22R1MKMR | Main | device short name | RE22
RE22R1MKMR | Main | nominal output current | 5 A
RE22R1MKMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1MKMR | Complementary | time delay type | K ¦ He
RE22R1MKMR | Complementary | time delay range | 0.3...3 s ¦ 0.05...0.5 s ¦ 3...30 s ¦ 0.1...1 s ¦ 30...300 s ¦ 10...100 s ¦ 1...10 s
RE22R1MKMR | Complementary | control type | Rotary knob
RE22R1MKMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1MKMR | Complementary | Release input voltage | <= 2.4 V
RE22R1MKMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1MKMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1MKMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1MKMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1MKMR | Complementary | housing material | Self-extinguishing
RE22R1MKMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1MKMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1MKMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1MKMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1MKMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1MKMR | Complementary | Recovery time | 50 ms on de-energisation
RE22R1MKMR | Complementary | immunity to microbreaks | 10 ms
RE22R1MKMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1MKMR | Complementary | power consumption in W | 2 W at 240 V DC
RE22R1MKMR | Complementary | switching capacity in VA | 1250 VA
RE22R1MKMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1MKMR | Complementary | maximum switching current | 5 A
RE22R1MKMR | Complementary | maximum switching voltage | 250 V AC
RE22R1MKMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 ¦ 100000 cycles, 5 A at 250 V, AC-1
RE22R1MKMR | Complementary | mechanical durability | 10000000 cycles
RE22R1MKMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1MKMR | Complementary | Power on delay | 100 ms
RE22R1MKMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1MKMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1MKMR | Complementary | safety reliability data | B10d = 180000 ¦ MTTFd = 194 years
RE22R1MKMR | Complementary | mounting position | Any position
RE22R1MKMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1MKMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (steady) for power ON
RE22R1MKMR | Complementary | width | 22.5 mm
RE22R1MKMR | Complementary | net weight | 0.1 kg
RE22R1MKMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1MKMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R1MKMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R1MKMR | Environment | product certifications | GL ¦ UL ¦ CSA ¦ RCM ¦ CCC ¦ China RoHS ¦ CE ¦ EAC
RE22R1MKMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1MKMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1MKMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1MKMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1MKMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1MKMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1MKMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1MKMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1MKMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1MKMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1MKMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1MKMR | Offer Sustainability | Mercury free | Yes
RE22R1MKMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1MKMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1MKMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1MKMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1MLMR | Main | range of product | Zelio Time
RE22R1MLMR | Main | product or component type | Modular timing relay
RE22R1MLMR | Main | discrete output type | Relay
RE22R1MLMR | Main | device short name | RE22
RE22R1MLMR | Main | nominal output current | 8 A
RE22R1MLMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1MLMR | Complementary | time delay type | Li ¦ Lit ¦ L ¦ Lt
RE22R1MLMR | Complementary | time delay range | 0.05...1 s ¦ 30...300 min ¦ 30...300 h ¦ 30...300 s ¦ 3...30 h ¦ 0.3...3 s ¦ 3...30 min ¦ 3...30 s ¦ 10...100 s ¦ 1...10 s
RE22R1MLMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1MLMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1MLMR | Complementary | Release input voltage | <= 2.4 V
RE22R1MLMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1MLMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1MLMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1MLMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1MLMR | Complementary | housing material | Self-extinguishing
RE22R1MLMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1MLMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1MLMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1MLMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1MLMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1MLMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1MLMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1MLMR | Complementary | immunity to microbreaks | 10 ms
RE22R1MLMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1MLMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1MLMR | Complementary | switching capacity in VA | 2000 VA
RE22R1MLMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1MLMR | Complementary | maximum switching current | 8 A
RE22R1MLMR | Complementary | maximum switching voltage | 250 V AC
RE22R1MLMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1MLMR | Complementary | mechanical durability | 10000000 cycles
RE22R1MLMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1MLMR | Complementary | Power on delay | 100 ms
RE22R1MLMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1MLMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1MLMR | Complementary | safety reliability data | MTTFd = 194 years ¦ B10d = 180000
RE22R1MLMR | Complementary | mounting position | Any position
RE22R1MLMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1MLMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1MLMR | Complementary | width | 22.5 mm
RE22R1MLMR | Complementary | net weight | 0.1 kg
RE22R1MLMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1MLMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R1MLMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1MLMR | Environment | product certifications | EAC ¦ UL ¦ GL ¦ China RoHS ¦ CSA ¦ RCM ¦ CCC ¦ CE
RE22R1MLMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1MLMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1MLMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1MLMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1MLMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1MLMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1MLMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1MLMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1MLMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1MLMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1MLMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1MLMR | Offer Sustainability | Mercury free | Yes
RE22R1MLMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1MLMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1MLMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1MLMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1MYMR | Main | range of product | Zelio Time
RE22R1MYMR | Main | product or component type | Modular timing relay
RE22R1MYMR | Main | discrete output type | Relay
RE22R1MYMR | Main | device short name | RE22
RE22R1MYMR | Main | nominal output current | 8 A
RE22R1MYMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1MYMR | Complementary | time delay type | Dw ¦ Ac ¦ C ¦ Dit ¦ Ht ¦ D ¦ A ¦ Di ¦ Hw ¦ W ¦ Ct ¦ Act ¦ At ¦ Wt ¦ H ¦ Dt ¦ Diw ¦ Aw
RE22R1MYMR | Complementary | time delay range | 30...300 s ¦ 10...100 s ¦ 3...30 s ¦ 30...300 min ¦ 3...30 min ¦ 0.3...3 s ¦ 0.05...1 s ¦ 30...300 h ¦ 1...10 s ¦ 3...30 h
RE22R1MYMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R1MYMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R1MYMR | Complementary | Release input voltage | <= 2.4 V
RE22R1MYMR | Complementary | voltage range | 0.85...1.1 Us
RE22R1MYMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1MYMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1MYMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1MYMR | Complementary | housing material | Self-extinguishing
RE22R1MYMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1MYMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1MYMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R1MYMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1MYMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R1MYMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1MYMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R1MYMR | Complementary | immunity to microbreaks | 10 ms
RE22R1MYMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R1MYMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R1MYMR | Complementary | switching capacity in VA | 2000 VA
RE22R1MYMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1MYMR | Complementary | maximum switching current | 8 A
RE22R1MYMR | Complementary | maximum switching voltage | 250 V AC
RE22R1MYMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1MYMR | Complementary | mechanical durability | 10000000 cycles
RE22R1MYMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1MYMR | Complementary | Power on delay | 100 ms
RE22R1MYMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1MYMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1MYMR | Complementary | safety reliability data | MTTFd = 205.4 years ¦ B10d = 190000
RE22R1MYMR | Complementary | mounting position | Any position
RE22R1MYMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1MYMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1MYMR | Complementary | width | 22.5 mm
RE22R1MYMR | Complementary | net weight | 0.1 kg
RE22R1MYMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1MYMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R1MYMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1MYMR | Environment | product certifications | RCM ¦ GL ¦ EAC ¦ CE ¦ CSA ¦ CCC ¦ China RoHS ¦ UL
RE22R1MYMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R1MYMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R1MYMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1MYMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1MYMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1MYMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1MYMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R1MYMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1MYMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1MYMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1MYMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1MYMR | Offer Sustainability | Mercury free | Yes
RE22R1MYMR | Offer Sustainability | RoHS exemption information | Yes
RE22R1MYMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1MYMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1MYMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R1QCMU | Main | range of product | Zelio Time
RE22R1QCMU | Main | product or component type | Modular timing relay
RE22R1QCMU | Main | discrete output type | Relay
RE22R1QCMU | Main | device short name | RE22
RE22R1QCMU | Main | nominal output current | 8 A
RE22R1QCMU | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free
RE22R1QCMU | Complementary | time delay type | Qc
RE22R1QCMU | Complementary | time delay range | 10...100 s ¦ 3...30 s ¦ 0.1...1 s ¦ 0.3...3 s ¦ 0.05...0.5 s ¦ 1...10 s ¦ 30...300 s
RE22R1QCMU | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R1QCMU | Complementary | [Us] rated supply voltage | 24 V DC ¦ 24...240 V AC 50/60 Hz
RE22R1QCMU | Complementary | Release input voltage | <= 2.4 V
RE22R1QCMU | Complementary | voltage range | 0.85...1.1 Us
RE22R1QCMU | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R1QCMU | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R1QCMU | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R1QCMU | Complementary | housing material | Self-extinguishing
RE22R1QCMU | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R1QCMU | Complementary | temperature drift | +/- 0.05 %/°C
RE22R1QCMU | Complementary | voltage drift | +/- 0.2 %/V
RE22R1QCMU | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R1QCMU | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R1QCMU | Complementary | Recovery time | 120 ms on de-energisation
RE22R1QCMU | Complementary | immunity to microbreaks | 10 ms
RE22R1QCMU | Complementary | power consumption in VA | 35 VA at 240 V AC
RE22R1QCMU | Complementary | power consumption in W | 0.6 W at 24 V DC
RE22R1QCMU | Complementary | switching capacity in VA | 2000 VA
RE22R1QCMU | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R1QCMU | Complementary | maximum switching current | 8 A
RE22R1QCMU | Complementary | maximum switching voltage | 250 V AC
RE22R1QCMU | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R1QCMU | Complementary | mechanical durability | 10000000 cycles
RE22R1QCMU | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R1QCMU | Complementary | Power on delay | 100 ms
RE22R1QCMU | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R1QCMU | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R1QCMU | Complementary | safety reliability data | MTTFd = 285.3 years ¦ B10d = 270000
RE22R1QCMU | Complementary | mounting position | Any position
RE22R1QCMU | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R1QCMU | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R1QCMU | Complementary | width | 22.5 mm
RE22R1QCMU | Complementary | net weight | 0.08 kg
RE22R1QCMU | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R1QCMU | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R1QCMU | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R1QCMU | Environment | product certifications | GL ¦ China RoHS ¦ CE ¦ CCC ¦ EAC ¦ UL ¦ CSA ¦ RCM
RE22R1QCMU | Environment | ambient air temperature for operation | -20…60 °C
RE22R1QCMU | Environment | ambient air temperature for storage | -40…70 °C
RE22R1QCMU | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R1QCMU | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R1QCMU | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R1QCMU | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R1QCMU | Environment | relative humidity | 95 % at 25…55 °C
RE22R1QCMU | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R1QCMU | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R1QCMU | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R1QCMU | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R1QCMU | Offer Sustainability | Mercury free | Yes
RE22R1QCMU | Offer Sustainability | RoHS exemption information | Yes
RE22R1QCMU | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R1QCMU | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R1QCMU | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2ACMR | Main | range of product | Zelio Time
RE22R2ACMR | Main | product or component type | Modular timing relay
RE22R2ACMR | Main | discrete output type | Relay
RE22R2ACMR | Main | device short name | RE22
RE22R2ACMR | Main | nominal output current | 8 A
RE22R2ACMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free ¦ 1 C/O timed or instantaneous contact, cadmium free
RE22R2ACMR | Complementary | time delay type | Ac
RE22R2ACMR | Complementary | time delay range | 3...30 h ¦ 30...300 h ¦ 0.05...1 s ¦ 30...300 s ¦ 0.3...3 s ¦ 10...100 s ¦ 1...10 s ¦ 3...30 min ¦ 30...300 min ¦ 3...30 s
RE22R2ACMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2ACMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2ACMR | Complementary | Release input voltage | <= 2.4 V
RE22R2ACMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2ACMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2ACMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2ACMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2ACMR | Complementary | housing material | Self-extinguishing
RE22R2ACMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2ACMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2ACMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2ACMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2ACMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2ACMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2ACMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2ACMR | Complementary | immunity to microbreaks | 10 ms
RE22R2ACMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2ACMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2ACMR | Complementary | switching capacity in VA | 2000 VA
RE22R2ACMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2ACMR | Complementary | maximum switching current | 8 A
RE22R2ACMR | Complementary | maximum switching voltage | 250 V AC
RE22R2ACMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2ACMR | Complementary | mechanical durability | 10000000 cycles
RE22R2ACMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2ACMR | Complementary | Power on delay | 100 ms
RE22R2ACMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2ACMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2ACMR | Complementary | safety reliability data | MTTFd = 251.1 years ¦ B10d = 230000
RE22R2ACMR | Complementary | mounting position | Any position
RE22R2ACMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2ACMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2ACMR | Complementary | width | 22.5 mm
RE22R2ACMR | Complementary | net weight | 0.105 kg
RE22R2ACMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2ACMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2ACMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2ACMR | Environment | product certifications | China RoHS ¦ RCM ¦ CCC ¦ CSA ¦ UL ¦ EAC ¦ CE ¦ GL
RE22R2ACMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2ACMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2ACMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP50 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RE22R2ACMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2ACMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2ACMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2ACMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2ACMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2ACMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2ACMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2ACMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2ACMR | Offer Sustainability | Mercury free | Yes
RE22R2ACMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2ACMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2ACMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2ACMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2AMR | Main | range of product | Zelio Time
RE22R2AMR | Main | product or component type | Modular timing relay
RE22R2AMR | Main | discrete output type | Relay
RE22R2AMR | Main | device short name | RE22
RE22R2AMR | Main | nominal output current | 8 A
RE22R2AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free ¦ 1 C/O timed or instantaneous contact, cadmium free
RE22R2AMR | Complementary | time delay type | Aw ¦ A
RE22R2AMR | Complementary | time delay range | 0.05...1 s ¦ 0.3...3 s ¦ 3...30 h ¦ 30...300 min ¦ 10...100 s ¦ 30...300 s ¦ 3...30 s ¦ 30...300 h ¦ 1...10 s ¦ 3...30 min
RE22R2AMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R2AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2AMR | Complementary | Release input voltage | <= 2.4 V
RE22R2AMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2AMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2AMR | Complementary | housing material | Self-extinguishing
RE22R2AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2AMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2AMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2AMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2AMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2AMR | Complementary | immunity to microbreaks | 10 ms
RE22R2AMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2AMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2AMR | Complementary | switching capacity in VA | 2000 VA
RE22R2AMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2AMR | Complementary | maximum switching current | 8 A
RE22R2AMR | Complementary | maximum switching voltage | 250 V AC
RE22R2AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2AMR | Complementary | mechanical durability | 10000000 cycles
RE22R2AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2AMR | Complementary | Power on delay | 100 ms
RE22R2AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2AMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2AMR | Complementary | safety reliability data | B10d = 200000 ¦ MTTFd = 216.8 years
RE22R2AMR | Complementary | mounting position | Any position
RE22R2AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2AMR | Complementary | width | 22.5 mm
RE22R2AMR | Complementary | net weight | 0.105 kg
RE22R2AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2AMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2AMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2AMR | Environment | product certifications | CE ¦ CCC ¦ GL ¦ China RoHS ¦ UL ¦ RCM ¦ EAC ¦ CSA
RE22R2AMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2AMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2AMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2AMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2AMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2AMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2AMR | Offer Sustainability | Mercury free | Yes
RE22R2AMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2AMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2CMR | Main | range of product | Zelio Time
RE22R2CMR | Main | product or component type | Modular timing relay
RE22R2CMR | Main | discrete output type | Relay
RE22R2CMR | Main | device short name | RE22
RE22R2CMR | Main | nominal output current | 8 A
RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free ¦ 2 C/O timed contact, cadmium free
RE22R2CMR | Complementary | time delay type | C
RE22R2CMR | Complementary | time delay range | 10...100 s ¦ 3...30 h ¦ 1...10 s ¦ 3...30 s ¦ 30...300 h ¦ 0.3...3 s ¦ 0.05...1 s ¦ 30...300 min ¦ 30...300 s ¦ 3...30 min
RE22R2CMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2CMR | Complementary | Release input voltage | <= 2.4 V
RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2CMR | Complementary | housing material | Self-extinguishing
RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2CMR | Complementary | immunity to microbreaks | 10 ms
RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2CMR | Complementary | switching capacity in VA | 2000 VA
RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2CMR | Complementary | maximum switching current | 8 A
RE22R2CMR | Complementary | maximum switching voltage | 250 V AC
RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2CMR | Complementary | mechanical durability | 10000000 cycles
RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2CMR | Complementary | Power on delay | 100 ms
RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years ¦ B10d = 230000
RE22R2CMR | Complementary | mounting position | Any position
RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2CMR | Complementary | width | 22.5 mm
RE22R2CMR | Complementary | net weight | 0.105 kg
RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2CMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2CMR | Environment | product certifications | CSA ¦ CCC ¦ RCM ¦ China RoHS ¦ CE ¦ GL ¦ UL ¦ EAC
RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2CMR | Offer Sustainability | Mercury free | Yes
RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2DMR | Main | range of product | Zelio Time
RE22R2DMR | Main | product or component type | Modular timing relay
RE22R2DMR | Main | discrete output type | Relay
RE22R2DMR | Main | device short name | RE22
RE22R2DMR | Main | nominal output current | 8 A
RE22R2DMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free ¦ 1 C/O timed or instantaneous contact, cadmium free
RE22R2DMR | Complementary | time delay type | D ¦ Dw
RE22R2DMR | Complementary | time delay range | 1...10 s ¦ 30...300 min ¦ 3...30 s ¦ 10...100 s ¦ 30...300 h ¦ 30...300 s ¦ 3...30 min ¦ 0.3...3 s ¦ 0.05...1 s ¦ 3...30 h
RE22R2DMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R2DMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2DMR | Complementary | Release input voltage | <= 2.4 V
RE22R2DMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2DMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2DMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2DMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2DMR | Complementary | housing material | Self-extinguishing
RE22R2DMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2DMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2DMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2DMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2DMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2DMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2DMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2DMR | Complementary | immunity to microbreaks | 10 ms
RE22R2DMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2DMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2DMR | Complementary | switching capacity in VA | 2000 VA
RE22R2DMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2DMR | Complementary | maximum switching current | 8 A
RE22R2DMR | Complementary | maximum switching voltage | 250 V AC
RE22R2DMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2DMR | Complementary | mechanical durability | 10000000 cycles
RE22R2DMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2DMR | Complementary | Power on delay | 100 ms
RE22R2DMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2DMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2DMR | Complementary | safety reliability data | B10d = 200000 ¦ MTTFd = 216.8 years
RE22R2DMR | Complementary | mounting position | Any position
RE22R2DMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2DMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2DMR | Complementary | width | 22.5 mm
RE22R2DMR | Complementary | net weight | 0.105 kg
RE22R2DMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2DMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2DMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2DMR | Environment | product certifications | CCC ¦ China RoHS ¦ CSA ¦ RCM ¦ GL ¦ CE ¦ UL ¦ EAC
RE22R2DMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2DMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2DMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2DMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2DMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2DMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2DMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2DMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2DMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2DMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2DMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2DMR | Offer Sustainability | Mercury free | Yes
RE22R2DMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2DMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2DMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2DMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2HMR | Main | range of product | Zelio Time
RE22R2HMR | Main | product or component type | Modular timing relay
RE22R2HMR | Main | discrete output type | Relay
RE22R2HMR | Main | device short name | RE22
RE22R2HMR | Main | nominal output current | 8 A
RE22R2HMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free ¦ 1 C/O timed or instantaneous contact, cadmium free
RE22R2HMR | Complementary | time delay type | H ¦ Hw
RE22R2HMR | Complementary | time delay range | 1...10 s ¦ 3...30 h ¦ 10...100 s ¦ 30...300 s ¦ 0.05...1 s ¦ 3...30 min ¦ 0.3...3 s ¦ 3...30 s ¦ 30...300 min ¦ 30...300 h
RE22R2HMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R2HMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2HMR | Complementary | Release input voltage | <= 2.4 V
RE22R2HMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2HMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2HMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2HMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2HMR | Complementary | housing material | Self-extinguishing
RE22R2HMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2HMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2HMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2HMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2HMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2HMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2HMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2HMR | Complementary | immunity to microbreaks | 10 ms
RE22R2HMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2HMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2HMR | Complementary | switching capacity in VA | 2000 VA
RE22R2HMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2HMR | Complementary | maximum switching current | 8 A
RE22R2HMR | Complementary | maximum switching voltage | 250 V AC
RE22R2HMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2HMR | Complementary | mechanical durability | 10000000 cycles
RE22R2HMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2HMR | Complementary | Power on delay | 100 ms
RE22R2HMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2HMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2HMR | Complementary | safety reliability data | B10d = 200000 ¦ MTTFd = 216.8 years
RE22R2HMR | Complementary | mounting position | Any position
RE22R2HMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2HMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2HMR | Complementary | width | 22.5 mm
RE22R2HMR | Complementary | net weight | 0.105 kg
RE22R2HMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2HMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2HMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2HMR | Environment | product certifications | RCM ¦ CSA ¦ CE ¦ EAC ¦ UL ¦ CCC ¦ GL ¦ China RoHS
RE22R2HMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2HMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2HMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2HMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2HMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2HMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2HMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2HMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2HMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2HMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2HMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2HMR | Offer Sustainability | Mercury free | Yes
RE22R2HMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2HMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2HMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2HMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2KMR | Main | range of product | Zelio Time
RE22R2KMR | Main | product or component type | Modular timing relay
RE22R2KMR | Main | discrete output type | Relay
RE22R2KMR | Main | device short name | RE22
RE22R2KMR | Main | nominal output current | 5 A
RE22R2KMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
RE22R2KMR | Complementary | time delay type | K
RE22R2KMR | Complementary | time delay range | 10...100 s ¦ 0.05...1 s ¦ 30...300 s ¦ 3...30 s ¦ 1...10 min ¦ 1...10 s ¦ 0.3...3 s
RE22R2KMR | Complementary | control type | Rotary knob ¦ Potentiometer external
RE22R2KMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2KMR | Complementary | Release input voltage | <= 2.4 V
RE22R2KMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2KMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2KMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2KMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2KMR | Complementary | housing material | Self-extinguishing
RE22R2KMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2KMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2KMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2KMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2KMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2KMR | Complementary | Recovery time | 100 ms on de-energisation
RE22R2KMR | Complementary | immunity to microbreaks | 10 ms
RE22R2KMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2KMR | Complementary | power consumption in W | 2 W at 240 V DC
RE22R2KMR | Complementary | switching capacity in VA | 1250 VA
RE22R2KMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2KMR | Complementary | maximum switching current | 5 A
RE22R2KMR | Complementary | maximum switching voltage | 250 V AC
RE22R2KMR | Complementary | electrical durability | 100000 cycles, 2 A at 24 V, DC-1 ¦ 100000 cycles, 5 A at 250 V, AC-1
RE22R2KMR | Complementary | mechanical durability | 10000000 cycles
RE22R2KMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2KMR | Complementary | Power on delay | 200 ms
RE22R2KMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2KMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2KMR | Complementary | safety reliability data | B10d = 160000 ¦ MTTFd = 171.2 years
RE22R2KMR | Complementary | mounting position | Any position
RE22R2KMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2KMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (steady) for power ON
RE22R2KMR | Complementary | width | 22.5 mm
RE22R2KMR | Complementary | net weight | 0.1 kg
RE22R2KMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2KMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2KMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2KMR | Environment | product certifications | China RoHS ¦ EAC ¦ UL ¦ RCM ¦ GL ¦ CCC ¦ CSA ¦ CE
RE22R2KMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2KMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2KMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2KMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2KMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2KMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2KMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2KMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2KMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2KMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2KMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2KMR | Offer Sustainability | Mercury free | Yes
RE22R2KMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2KMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2KMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2KMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MWMR | Main | range of product | Zelio Time
RE22R2MWMR | Main | product or component type | Modular timing relay
RE22R2MWMR | Main | discrete output type | Relay
RE22R2MWMR | Main | device short name | RE22
RE22R2MWMR | Main | nominal output current | 8 A
RE22R2MWMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free ¦ 1 C/O timed or instantaneous contact, cadmium free
RE22R2MWMR | Complementary | time delay type | W ¦ Wt
RE22R2MWMR | Complementary | time delay range | 0.05...1 s ¦ 30...300 min ¦ 30...300 s ¦ 3...30 h ¦ 0.3...3 s ¦ 1...10 s ¦ 3...30 s ¦ 30...300 h ¦ 3...30 min ¦ 10...100 s
RE22R2MWMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R2MWMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2MWMR | Complementary | Release input voltage | <= 2.4 V
RE22R2MWMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2MWMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MWMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2MWMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MWMR | Complementary | housing material | Self-extinguishing
RE22R2MWMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MWMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MWMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MWMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MWMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2MWMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MWMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MWMR | Complementary | immunity to microbreaks | 10 ms
RE22R2MWMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2MWMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2MWMR | Complementary | switching capacity in VA | 2000 VA
RE22R2MWMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2MWMR | Complementary | maximum switching current | 8 A
RE22R2MWMR | Complementary | maximum switching voltage | 250 V AC
RE22R2MWMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2MWMR | Complementary | mechanical durability | 10000000 cycles
RE22R2MWMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2MWMR | Complementary | Power on delay | 100 ms
RE22R2MWMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2MWMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2MWMR | Complementary | safety reliability data | B10d = 160000 ¦ MTTFd = 171.2 years
RE22R2MWMR | Complementary | mounting position | Any position
RE22R2MWMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MWMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2MWMR | Complementary | width | 22.5 mm
RE22R2MWMR | Complementary | net weight | 0.105 kg
RE22R2MWMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2MWMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2MWMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2MWMR | Environment | product certifications | UL ¦ GL ¦ CE ¦ China RoHS ¦ CSA ¦ RCM ¦ EAC ¦ CCC
RE22R2MWMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MWMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2MWMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2MWMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2MWMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MWMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2MWMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2MWMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2MWMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MWMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MWMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MWMR | Offer Sustainability | Mercury free | Yes
RE22R2MWMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2MWMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MWMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MWMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2MYMR | Main | range of product | Zelio Time
RE22R2MYMR | Main | product or component type | Modular timing relay
RE22R2MYMR | Main | discrete output type | Relay
RE22R2MYMR | Main | device short name | RE22
RE22R2MYMR | Main | nominal output current | 8 A
RE22R2MYMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free ¦ 2 C/O timed contact, cadmium free
RE22R2MYMR | Complementary | time delay type | Ht ¦ Dit ¦ Qgt ¦ D ¦ Dt ¦ W ¦ Ct ¦ Dw ¦ A ¦ Qt ¦ Qtt ¦ Diw ¦ C ¦ Wt ¦ Di ¦ Hw ¦ Qg ¦ At ¦ Aw ¦ H
RE22R2MYMR | Complementary | time delay range | 3...30 min ¦ 30...300 min ¦ 0.3...3 s ¦ 3...30 h ¦ 10...100 s ¦ 1...10 s ¦ 0.05...1 s ¦ 30...300 s ¦ 30...300 h ¦ 3...30 s
RE22R2MYMR | Complementary | control type | Rotary knob ¦ Diagnostic button ¦ Potentiometer external
RE22R2MYMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2MYMR | Complementary | Release input voltage | <= 2.4 V
RE22R2MYMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2MYMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2MYMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2MYMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2MYMR | Complementary | housing material | Self-extinguishing
RE22R2MYMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2MYMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2MYMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2MYMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2MYMR | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 30 ms
RE22R2MYMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2MYMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2MYMR | Complementary | immunity to microbreaks | 10 ms
RE22R2MYMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2MYMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2MYMR | Complementary | switching capacity in VA | 2000 VA
RE22R2MYMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2MYMR | Complementary | maximum switching current | 8 A
RE22R2MYMR | Complementary | maximum switching voltage | 250 V AC
RE22R2MYMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2MYMR | Complementary | mechanical durability | 10000000 cycles
RE22R2MYMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2MYMR | Complementary | Power on delay | 100 ms
RE22R2MYMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2MYMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2MYMR | Complementary | safety reliability data | B10d = 160000 ¦ MTTFd = 171.2 years
RE22R2MYMR | Complementary | mounting position | Any position
RE22R2MYMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2MYMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2MYMR | Complementary | width | 22.5 mm
RE22R2MYMR | Complementary | net weight | 0.105 kg
RE22R2MYMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2MYMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2MYMR | Environment | directives | 2004/108/EC - electromagnetic compatibility ¦ 2006/95/EC - low voltage directive
RE22R2MYMR | Environment | product certifications | RCM ¦ CE ¦ China RoHS ¦ EAC ¦ CSA ¦ CCC ¦ UL ¦ GL
RE22R2MYMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2MYMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2MYMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2MYMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2MYMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2MYMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2MYMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2MYMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2MYMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2MYMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2MYMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2MYMR | Offer Sustainability | Mercury free | Yes
RE22R2MYMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2MYMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2MYMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2MYMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2QEMR | Main | range of product | Zelio Time
RE22R2QEMR | Main | product or component type | Modular timing relay
RE22R2QEMR | Main | discrete output type | Relay
RE22R2QEMR | Main | device short name | RE22
RE22R2QEMR | Main | nominal output current | 8 A
RE22R2QEMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
RE22R2QEMR | Complementary | time delay type | Qe
RE22R2QEMR | Complementary | time delay range | 0.3...30 s
RE22R2QEMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2QEMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2QEMR | Complementary | Release input voltage | <= 2.4 V
RE22R2QEMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2QEMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2QEMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2QEMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2QEMR | Complementary | housing material | Self-extinguishing
RE22R2QEMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2QEMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2QEMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2QEMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2QEMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2QEMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2QEMR | Complementary | immunity to microbreaks | 10 ms
RE22R2QEMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2QEMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2QEMR | Complementary | switching capacity in VA | 2000 VA
RE22R2QEMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2QEMR | Complementary | maximum switching current | 8 A
RE22R2QEMR | Complementary | maximum switching voltage | 250 V AC
RE22R2QEMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2QEMR | Complementary | mechanical durability | 10000000 cycles
RE22R2QEMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2QEMR | Complementary | Power on delay | 100 ms
RE22R2QEMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2QEMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2QEMR | Complementary | safety reliability data | B10d = 320000 ¦ MTTFd = 353.8 years
RE22R2QEMR | Complementary | mounting position | Any position
RE22R2QEMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2QEMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2QEMR | Complementary | width | 22.5 mm
RE22R2QEMR | Complementary | net weight | 0.09 kg
RE22R2QEMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2QEMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2QEMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2QEMR | Environment | product certifications | CE ¦ CSA ¦ GL ¦ China RoHS ¦ EAC ¦ UL ¦ RCM ¦ CCC
RE22R2QEMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2QEMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2QEMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2QEMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2QEMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2QEMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2QEMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2QEMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2QEMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2QEMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2QEMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2QEMR | Offer Sustainability | Mercury free | Yes
RE22R2QEMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2QEMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2QEMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2QEMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2QEMT | Main | range of product | Zelio Time
RE22R2QEMT | Main | product or component type | Modular timing relay
RE22R2QEMT | Main | discrete output type | Relay
RE22R2QEMT | Main | device short name | RE22
RE22R2QEMT | Main | nominal output current | 8 A
RE22R2QEMT | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
RE22R2QEMT | Complementary | time delay type | Qe
RE22R2QEMT | Complementary | time delay range | 0.3...30 s
RE22R2QEMT | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2QEMT | Complementary | [Us] rated supply voltage | 380...415 V AC 50/60 Hz
RE22R2QEMT | Complementary | Release input voltage | <= 38 V
RE22R2QEMT | Complementary | voltage range | 0.85...1.16 Us
RE22R2QEMT | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2QEMT | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2QEMT | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2QEMT | Complementary | housing material | Self-extinguishing
RE22R2QEMT | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2QEMT | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2QEMT | Complementary | voltage drift | +/- 0.2 %/V
RE22R2QEMT | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2QEMT | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2QEMT | Complementary | Recovery time | 120 ms on de-energisation
RE22R2QEMT | Complementary | immunity to microbreaks | 10 ms
RE22R2QEMT | Complementary | power consumption in VA | 15 VA at 380 V AC
RE22R2QEMT | Complementary | switching capacity in VA | 2000 VA
RE22R2QEMT | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2QEMT | Complementary | maximum switching current | 8 A
RE22R2QEMT | Complementary | maximum switching voltage | 250 V AC
RE22R2QEMT | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2QEMT | Complementary | mechanical durability | 10000000 cycles
RE22R2QEMT | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2QEMT | Complementary | Power on delay | 100 ms
RE22R2QEMT | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2QEMT | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2QEMT | Complementary | safety reliability data | B10d = 250000 ¦ MTTFd = 273.9 years
RE22R2QEMT | Complementary | mounting position | Any position
RE22R2QEMT | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2QEMT | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2QEMT | Complementary | width | 22.5 mm
RE22R2QEMT | Complementary | net weight | 0.09 kg
RE22R2QEMT | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2QEMT | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2QEMT | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2QEMT | Environment | product certifications | EAC ¦ GL ¦ CSA ¦ China RoHS ¦ UL ¦ CCC ¦ RCM ¦ CE
RE22R2QEMT | Environment | ambient air temperature for operation | -20…60 °C
RE22R2QEMT | Environment | ambient air temperature for storage | -40…70 °C
RE22R2QEMT | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2QEMT | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2QEMT | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2QEMT | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2QEMT | Environment | relative humidity | 95 % at 25…55 °C
RE22R2QEMT | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Surge immunity test - test level: 2 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 4 kV level 3 (common mode) conforming to IEC 61000-4-5
RE22R2QEMT | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2QEMT | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2QEMT | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2QEMT | Offer Sustainability | Mercury free | Yes
RE22R2QEMT | Offer Sustainability | RoHS exemption information | Yes
RE22R2QEMT | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2QEMT | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2QEMT | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2QGMR | Main | range of product | Zelio Time
RE22R2QGMR | Main | product or component type | Modular timing relay
RE22R2QGMR | Main | discrete output type | Relay
RE22R2QGMR | Main | device short name | RE22
RE22R2QGMR | Main | nominal output current | 8 A
RE22R2QGMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
RE22R2QGMR | Complementary | time delay type | Qg
RE22R2QGMR | Complementary | time delay range | 3...30 s ¦ 0.05...1 s ¦ 30...300 s ¦ 30...300 min ¦ 0.3...3 s ¦ 1...10 s ¦ 3...30 h ¦ 10...100 s ¦ 30...300 h ¦ 3...30 min
RE22R2QGMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2QGMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2QGMR | Complementary | Release input voltage | <= 2.4 V
RE22R2QGMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2QGMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2QGMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2QGMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2QGMR | Complementary | housing material | Self-extinguishing
RE22R2QGMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2QGMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2QGMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2QGMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2QGMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2QGMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2QGMR | Complementary | immunity to microbreaks | 10 ms
RE22R2QGMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2QGMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2QGMR | Complementary | switching capacity in VA | 2000 VA
RE22R2QGMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2QGMR | Complementary | maximum switching current | 8 A
RE22R2QGMR | Complementary | maximum switching voltage | 250 V AC
RE22R2QGMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2QGMR | Complementary | mechanical durability | 10000000 cycles
RE22R2QGMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2QGMR | Complementary | Power on delay | 100 ms
RE22R2QGMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2QGMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2QGMR | Complementary | safety reliability data | MTTFd = 342.4 years ¦ B10d = 320000
RE22R2QGMR | Complementary | mounting position | Any position
RE22R2QGMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2QGMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2QGMR | Complementary | width | 22.5 mm
RE22R2QGMR | Complementary | net weight | 0.105 kg
RE22R2QGMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2QGMR | Environment | standards | UL 508 ¦ IEC 61812-1
RE22R2QGMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2QGMR | Environment | product certifications | CCC ¦ CSA ¦ RCM ¦ GL ¦ EAC ¦ CE ¦ UL ¦ China RoHS
RE22R2QGMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2QGMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2QGMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2QGMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2QGMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2QGMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2QGMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2QGMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2QGMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2QGMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2QGMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2QGMR | Offer Sustainability | Mercury free | Yes
RE22R2QGMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2QGMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2QGMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2QGMR | Offer Sustainability | Circularity Profile | End of Life Information
RE22R2QTMR | Main | range of product | Zelio Time
RE22R2QTMR | Main | product or component type | Modular timing relay
RE22R2QTMR | Main | discrete output type | Relay
RE22R2QTMR | Main | device short name | RE22
RE22R2QTMR | Main | nominal output current | 8 A
RE22R2QTMR | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free
RE22R2QTMR | Complementary | time delay type | Qt
RE22R2QTMR | Complementary | time delay range | 1...10 s ¦ 3...30 s ¦ 10...100 s ¦ 30...300 min ¦ 0.05...1 s ¦ 3...30 min ¦ 0.3...3 s ¦ 30...300 s ¦ 3...30 h ¦ 30...300 h
RE22R2QTMR | Complementary | control type | Rotary knob ¦ Diagnostic button
RE22R2QTMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE22R2QTMR | Complementary | Release input voltage | <= 2.4 V
RE22R2QTMR | Complementary | voltage range | 0.85...1.1 Us
RE22R2QTMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
RE22R2QTMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RE22R2QTMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RE22R2QTMR | Complementary | housing material | Self-extinguishing
RE22R2QTMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
RE22R2QTMR | Complementary | temperature drift | +/- 0.05 %/°C
RE22R2QTMR | Complementary | voltage drift | +/- 0.2 %/V
RE22R2QTMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
RE22R2QTMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RE22R2QTMR | Complementary | Recovery time | 120 ms on de-energisation
RE22R2QTMR | Complementary | immunity to microbreaks | 10 ms
RE22R2QTMR | Complementary | power consumption in VA | 3 VA at 240 V AC
RE22R2QTMR | Complementary | power consumption in W | 1.5 W at 240 V DC
RE22R2QTMR | Complementary | switching capacity in VA | 2000 VA
RE22R2QTMR | Complementary | minimum switching current | 10 mA at 5 V DC
RE22R2QTMR | Complementary | maximum switching current | 8 A
RE22R2QTMR | Complementary | maximum switching voltage | 250 V AC
RE22R2QTMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 ¦ 100000 cycles, 2 A at 24 V, DC-1
RE22R2QTMR | Complementary | mechanical durability | 10000000 cycles
RE22R2QTMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
RE22R2QTMR | Complementary | Power on delay | 100 ms
RE22R2QTMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RE22R2QTMR | Complementary | overvoltage category | III conforming to IEC 60664-1
RE22R2QTMR | Complementary | safety reliability data | MTTFd = 342.4 years ¦ B10d = 320000
RE22R2QTMR | Complementary | mounting position | Any position
RE22R2QTMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RE22R2QTMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication ¦ LED yellow (steady) for output relay energised ¦ LED yellow (fast flashing) for timing in progress and output relay de-energised ¦ LED yellow (slow flashing) for timing in progress and output relay energised
RE22R2QTMR | Complementary | width | 22.5 mm
RE22R2QTMR | Complementary | net weight | 0.105 kg
RE22R2QTMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
RE22R2QTMR | Environment | standards | IEC 61812-1 ¦ UL 508
RE22R2QTMR | Environment | directives | 2006/95/EC - low voltage directive ¦ 2004/108/EC - electromagnetic compatibility
RE22R2QTMR | Environment | product certifications | CCC ¦ GL ¦ UL ¦ EAC ¦ RCM ¦ CSA ¦ China RoHS ¦ CE
RE22R2QTMR | Environment | ambient air temperature for operation | -20…60 °C
RE22R2QTMR | Environment | ambient air temperature for storage | -40…70 °C
RE22R2QTMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529 ¦ IP50 front panel: conforming to IEC 60529
RE22R2QTMR | Environment | pollution degree | 3 conforming to IEC 60664-1
RE22R2QTMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RE22R2QTMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RE22R2QTMR | Environment | relative humidity | 95 % at 25…55 °C
RE22R2QTMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
RE22R2QTMR | Offer Sustainability | Sustainable offer status | Green Premium product
RE22R2QTMR | Offer Sustainability | REACh Regulation | REACh Declaration
RE22R2QTMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE22R2QTMR | Offer Sustainability | Mercury free | Yes
RE22R2QTMR | Offer Sustainability | RoHS exemption information | Yes
RE22R2QTMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE22R2QTMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE22R2QTMR | Offer Sustainability | Circularity Profile | End of Life Information
RENF22R2MMW | Main | range of product | Zelio Time
RENF22R2MMW | Main | product or component type | Modular timing relay
RENF22R2MMW | Main | device short name | RENF22
RENF22R2MMW | Main | Supported OS | Android
RENF22R2MMW | Main | software version | V4.4 and above
RENF22R2MMW | Main | App for product | Zelio NFC (downloadable from Google Play store)
RENF22R2MMW | Complementary | discrete output type | Relay
RENF22R2MMW | Complementary | nominal output current | 8 A
RENF22R2MMW | Complementary | contacts type and composition | 2 C/O timed contact, cadmium free ¦ 1 C/O timed and instantaneous contact, cadmium free
RENF22R2MMW | Complementary | time delay type | Tt ¦ Ak ¦ Ah ¦ Di ¦ Pt ¦ H ¦ At ¦ Dt ¦ Ad ¦ A ¦ Qt ¦ N ¦ Li ¦ L ¦ Qtt ¦ O ¦ Ht ¦ Lit ¦ C ¦ Lt ¦ W ¦ Tl ¦ P ¦ Ac ¦ Dit ¦ B ¦ D ¦ Bw
RENF22R2MMW | Complementary | time delay range | 0.1 s...999 h
RENF22R2MMW | Complementary | product compatibility | NFC enabled mobile device
RENF22R2MMW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC
RENF22R2MMW | Complementary | Release input voltage | <= 2.4 V
RENF22R2MMW | Complementary | voltage range | 0.85...1.1 Un
RENF22R2MMW | Complementary | Maximum RF power transmitted | 0.0002 mW
RENF22R2MMW | Complementary | NFC operating frequency | 13.56 MHz
RENF22R2MMW | Complementary | supply frequency | 50...60 Hz +/- 5 %
RENF22R2MMW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RENF22R2MMW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 ¦ 0.60…0.99 N.m conforming to IEC 60947-1
RENF22R2MMW | Complementary | housing material | Self-extinguishing
RENF22R2MMW | Complementary | repeat accuracy | +/- 0.2 % for 10 s...999 h time delay range ¦ +/- 0.5 % for 100 ms...10 s time delay range
RENF22R2MMW | Complementary | temperature drift | +/- 0.05 %/°C
RENF22R2MMW | Complementary | voltage drift | +/- 0.2 %/V
RENF22R2MMW | Complementary | setting accuracy of time delay | +/- 1 % for 1...999 h time delay range at 25 °C ¦ +/- 2 % for 1 h time delay range at 25 °C ¦ +/- 20 ms for 100 ms...10 s time delay range at 25 °C
RENF22R2MMW | Complementary | Control signal pulse width | 100 ms with load in parallel ¦ 60 ms no-load
RENF22R2MMW | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
RENF22R2MMW | Complementary | Recovery time | 120 ms on de-energisation
RENF22R2MMW | Complementary | power consumption in VA | 3 VA at 240 V AC
RENF22R2MMW | Complementary | power consumption in W | 1.5 W at 240 V DC ¦ 0.6 W at 24 V DC
RENF22R2MMW | Complementary | switching capacity in VA | 2000 VA
RENF22R2MMW | Complementary | minimum switching current | 10 mA at 5 V
RENF22R2MMW | Complementary | maximum switching current | 8 A
RENF22R2MMW | Complementary | maximum switching voltage | 250 V
RENF22R2MMW | Complementary | electrical durability | 100000 cycles for resistive load, 8 A at 250 V, AC
RENF22R2MMW | Complementary | mechanical durability | 10000000 cycles
RENF22R2MMW | Complementary | Rated impulse withstand voltage | 5 kV 1.2/50 µs conforming to IEC 60664-1
RENF22R2MMW | Complementary | power on delay | 100 ms
RENF22R2MMW | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
RENF22R2MMW | Complementary | overvoltage category | III conforming to IEC 60664-1
RENF22R2MMW | Complementary | safety reliability data | MTTFd = 227.5 years 100 % duty cycle continuous operating condition at 30 °C
RENF22R2MMW | Complementary | mounting position | Any position
RENF22R2MMW | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
RENF22R2MMW | Complementary | status LED | LED Un: (steady), green for power ON ¦ LED R1: (steady), amber for relay energised ¦ LED R2: (steady), amber for relay energised ¦ LED pairing: (steady), green for communication status ¦ LED Un: (fast blinking), green for diagnosis mode ¦ LED R1: (blinking), amber for timing in progress ¦ LED R2: (blinking), amber for timing in progress
RENF22R2MMW | Complementary | Maximum communication distance | 10 mm
RENF22R2MMW | Complementary | response time | 2 s
RENF22R2MMW | Complementary | width | 22.5 mm
RENF22R2MMW | Complementary | net weight | 0.0904 kg
RENF22R2MMW | Environment | immunity to microbreaks | 10 ms
RENF22R2MMW | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz with between relay output and power supply with basic insulation ¦ with basic insulation
RENF22R2MMW | Environment | standards | EN 61000-6-1 ¦ EN 61000-6-2 ¦ EN 61000-6-4 ¦ EN 61812-1 ¦ EN 61000-6-3
RENF22R2MMW | Environment | directives | 2014/35/EU - low voltage directive ¦ 2014/53/EU - radio equipment directive ¦ 2014/30/EU - electromagnetic compatibility
RENF22R2MMW | Environment | product certifications | CE ¦ CSA ¦ KC ¦ UL ¦ CCC ¦ EAC ¦ DNV-GL
RENF22R2MMW | Environment | ambient air temperature for operation | -20…60 °C
RENF22R2MMW | Environment | ambient air temperature for storage | -40…70 °C
RENF22R2MMW | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 ¦ IP40 front face: conforming to IEC 60529 ¦ IP20 terminals: conforming to IEC 60529
RENF22R2MMW | Environment | pollution degree | 3 conforming to IEC 60664-1
RENF22R2MMW | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
RENF22R2MMW | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 ¦ 5 gn in operation for 11 ms conforming to IEC 60068-2-27
RENF22R2MMW | Environment | relative humidity | 95 % at 25…55 °C
RENF22R2MMW | Environment | electromagnetic compatibility | Electrostatic discharge immunity test - test level: 6 kV level 3 (contact discharge) conforming to EN/IEC 61000-4-2 ¦ Electrostatic discharge immunity test - test level: 8 kV level 3 (air discharge) conforming to EN/IEC 61000-4-2 ¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 ¦ Fast transients immunity test - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 ¦ Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 ¦ Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 ¦ Radiated radio-frequency electromagnetic field immunity test - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 ¦ Electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 ¦ Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 ¦ Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 ¦ Radiated emission class B conforming to EN 55022 ¦ Conducted emission class A conforming to EN 55022 ¦ Electromagnetic field immunity test - test level: 3 V/m level 2 (1.4 GHz...2 GHz) conforming to IEC 61000-4-3 ¦ Electromagnetic field immunity test - test level: 1 V/m level 1 (2...2.7 GHz) conforming to IEC 61000-4-3
RENF22R2MMW | Offer Sustainability | Sustainable offer status | Green Premium product
RENF22R2MMW | Offer Sustainability | REACh Regulation | REACh Declaration
RENF22R2MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RENF22R2MMW | Offer Sustainability | Mercury free | Yes
RENF22R2MMW | Offer Sustainability | RoHS exemption information | Yes
RENF22R2MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RENF22R2MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RENF22R2MMW | Offer Sustainability | Circularity Profile | End of Life Information
RE48AML12MW | Main | range of product | Zelio Time
RE48AML12MW | Main | product or component type | Electronic timing relay
RE48AML12MW | Main | electrical connection | Plug-in sub-base 11 pin(s)
RE48AML12MW | Main | discrete output type | Relay
RE48AML12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
RE48AML12MW | Main | component name | RE48A
RE48AML12MW | Main | time delay type | B ¦ Di ¦ A ¦ C
RE48AML12MW | Main | time delay range | 0.5...30 s ¦ 5...300 s ¦ 0.2...12 min ¦ 0.5...30 h ¦ 2...120 s ¦ 0.05...3 s ¦ 0.2...12 s ¦ 0.02...1.2 s ¦ 2...120 min ¦ 5...300 min ¦ 0.5...30 min ¦ 5...300 h ¦ 2...120 h ¦ 0.2...12 h
RE48AML12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE48AML12MW | Main | voltage range | 0.85...1.1 Us AC ¦ 0.9...1.1 Us DC
RE48AML12MW | Main | [In] rated current | 5 A
RE48AML12MW | Complementary | product front plate size | 48 x 48 mm
RE48AML12MW | Complementary | control type | Selector switch front panel
RE48AML12MW | Complementary | housing material | Self-extinguishing
RE48AML12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
RE48AML12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
RE48AML12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V ¦ +/- 1 %/V of the maximum setting value at 24...48 V
RE48AML12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
RE48AML12MW | Complementary | minimum pulse duration | 20 ms
RE48AML12MW | Complementary | reset time | 25 ms on de-energisation
RE48AML12MW | Complementary | pick up duration | 55 ms
RE48AML12MW | Complementary | on-load factor | 100 %
RE48AML12MW | Complementary | power consumption in VA | 1.1 VA at 24 V ¦ 4.8 VA at 240 V
RE48AML12MW | Complementary | power consumption in W | 0.5 W at 24 V ¦ 1.7 W at 240 V
RE48AML12MW | Complementary | breaking capacity | 1250 VA
RE48AML12MW | Complementary | minimum switching current | 100 mA
RE48AML12MW | Complementary | maximum switching current | 5 A
RE48AML12MW | Complementary | maximum switching voltage | 250 V AC/DC
RE48AML12MW | Complementary | electrical durability | 100000 cycles
RE48AML12MW | Complementary | mechanical durability | 30000000 cycles
RE48AML12MW | Complementary | output voltage | 240 V at 5 A AC-12 ¦ 30 V at 2 A DC-13 ¦ 240 V at 1.5 A AC-15
RE48AML12MW | Complementary | marking | CE
RE48AML12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 ¦ 2 kV common mode conforming to IEC 61000-4-5 level 3
RE48AML12MW | Complementary | mounting support | Base mounted: socket ¦ Panel mounted: system supplied with the product
RE48AML12MW | Complementary | local signalling | 1 LED (yellow) for output relay state ¦ LED indicator (green) for flashing: relay energised timing in progress ¦ LED indicator (green) for on steady: relay energised, no timing in progress
RE48AML12MW | Complementary | net weight | 0.14 kg
RE48AML12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
RE48AML12MW | Environment | immunity to microbreaks | 10 ms
RE48AML12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
RE48AML12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 ¦ 4 kV class III conforming to IEC 61812-1
RE48AML12MW | Environment | standards | IEC 61812-1 ¦ EN 50081-1/2 ¦ 93/68/EEC ¦ 89/336/EEC ¦ EN 50082-1/2 ¦ IEC 60669-2-3 ¦ 73/23/EEC
RE48AML12MW | Environment | product certifications | GL ¦ UL ¦ CULus ¦ CSA ¦ C-Tick
RE48AML12MW | Environment | ambient air temperature for storage | -40…70 °C
RE48AML12MW | Environment | ambient air temperature for operation | -20…50 °C
RE48AML12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 ¦ IP50 (front face) conforming to IEC 60529
RE48AML12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
RE48AML12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
RE48AML12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
RE48AML12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
RE48AML12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 ¦ 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
RE48AML12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
RE48AML12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11 ¦ 95 % / 5 s conforming to EN/IEC 61000-4-11
RE48AML12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
RE48AML12MW | Offer Sustainability | Sustainable offer status | Green Premium product
RE48AML12MW | Offer Sustainability | REACh Regulation | REACh Declaration
RE48AML12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE48AML12MW | Offer Sustainability | Mercury free | Yes
RE48AML12MW | Offer Sustainability | RoHS exemption information | Yes
RE48AML12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE48AML12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE48AML12MW | Offer Sustainability | Circularity Profile | End of Life Information
RE48AML12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RE48AML12MW | Contractual warranty | Warranty | 18 months
RE48ATM12MW | Main | range of product | Zelio Time
RE48ATM12MW | Main | product or component type | Electronic timing relay
RE48ATM12MW | Main | electrical connection | Plug-in sub-base 8 pin(s)
RE48ATM12MW | Main | discrete output type | Relay
RE48ATM12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
RE48ATM12MW | Main | component name | RE48
RE48ATM12MW | Main | time delay type | A
RE48ATM12MW | Main | time delay range | 5...300 h ¦ 2...120 min ¦ 0.5...30 h ¦ 0.2...12 h ¦ 0.2...12 min ¦ 0.2...12 s ¦ 0.5...30 min ¦ 2...120 h ¦ 2...120 s ¦ 0.02...1.2 s ¦ 0.5...30 s ¦ 5...300 s ¦ 0.05...3 s ¦ 5...300 min
RE48ATM12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE48ATM12MW | Main | voltage range | 0.85...1.1 Us AC ¦ 0.9...1.1 Us DC
RE48ATM12MW | Main | [In] rated current | 5 A
RE48ATM12MW | Complementary | product front plate size | 48 x 48 mm
RE48ATM12MW | Complementary | control type | Selector switch front panel
RE48ATM12MW | Complementary | housing material | Self-extinguishing
RE48ATM12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
RE48ATM12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
RE48ATM12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V ¦ +/- 1 %/V of the maximum setting value at 24...48 V
RE48ATM12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
RE48ATM12MW | Complementary | minimum pulse duration | 20 ms
RE48ATM12MW | Complementary | reset time | 25 ms on de-energisation
RE48ATM12MW | Complementary | pick up duration | 55 ms
RE48ATM12MW | Complementary | on-load factor | 100 %
RE48ATM12MW | Complementary | power consumption in VA | 1.1 VA at 24 V ¦ 4.8 VA at 240 V
RE48ATM12MW | Complementary | power consumption in W | 0.5 W at 24 V ¦ 1.7 W at 240 V
RE48ATM12MW | Complementary | breaking capacity | 1250 VA
RE48ATM12MW | Complementary | minimum switching current | 100 mA
RE48ATM12MW | Complementary | maximum switching current | 5 A
RE48ATM12MW | Complementary | maximum switching voltage | 250 V AC/DC
RE48ATM12MW | Complementary | electrical durability | 100000 cycles
RE48ATM12MW | Complementary | mechanical durability | 30000000 cycles
RE48ATM12MW | Complementary | output voltage | 240 V at 5 A AC-12 ¦ 30 V at 2 A DC-13 ¦ 240 V at 1.5 A AC-15
RE48ATM12MW | Complementary | marking | CE
RE48ATM12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 ¦ 2 kV common mode conforming to IEC 61000-4-5 level 3
RE48ATM12MW | Complementary | mounting support | Panel mounted: system supplied with the product ¦ Base mounted: socket
RE48ATM12MW | Complementary | local signalling | 1 LED (yellow) for output relay state ¦ LED indicator (green) for flashing: relay energised timing in progress ¦ LED indicator (green) for on steady: relay energised, no timing in progress
RE48ATM12MW | Complementary | net weight | 0.14 kg
RE48ATM12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
RE48ATM12MW | Environment | immunity to microbreaks | 10 ms
RE48ATM12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
RE48ATM12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 ¦ 4 kV class III conforming to IEC 61812-1
RE48ATM12MW | Environment | standards | 73/23/EEC ¦ 93/68/EEC ¦ EN 50082-1/2 ¦ 89/336/EEC ¦ EN 50081-1/2 ¦ IEC 61812-1 ¦ IEC 60669-2-3
RE48ATM12MW | Environment | product certifications | GL ¦ UL ¦ CULus ¦ C-Tick ¦ CSA
RE48ATM12MW | Environment | ambient air temperature for storage | -40…70 °C
RE48ATM12MW | Environment | ambient air temperature for operation | -20…50 °C
RE48ATM12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 ¦ IP50 (front face) conforming to IEC 60529
RE48ATM12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
RE48ATM12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
RE48ATM12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
RE48ATM12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
RE48ATM12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 ¦ 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
RE48ATM12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
RE48ATM12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11 ¦ 95 % / 5 s conforming to EN/IEC 61000-4-11
RE48ATM12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
RE48ATM12MW | Offer Sustainability | Sustainable offer status | Green Premium product
RE48ATM12MW | Offer Sustainability | REACh Regulation | REACh Declaration
RE48ATM12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE48ATM12MW | Offer Sustainability | Mercury free | Yes
RE48ATM12MW | Offer Sustainability | RoHS exemption information | Yes
RE48ATM12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE48ATM12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE48ATM12MW | Offer Sustainability | Circularity Profile | End of Life Information
RE48ATM12MW | Contractual warranty | Warranty | 18 months
RE48AMH13MW | Main | range of product | Zelio Time
RE48AMH13MW | Main | product or component type | Electronic timing relay
RE48AMH13MW | Main | electrical connection | Plug-in sub-base 8 pin(s)
RE48AMH13MW | Main | discrete output type | Relay
RE48AMH13MW | Main | contacts type and composition | 1 C/O + 1 C/O timed or instantaneous contact, AgNi (cadmium free)
RE48AMH13MW | Main | component name | RE48
RE48AMH13MW | Main | time delay type | H1 ¦ A2 ¦ A1 ¦ H2
RE48AMH13MW | Main | time delay range | 2...120 h ¦ 5...300 min ¦ 0.2...12 min ¦ 2...120 s ¦ 0.2...12 h ¦ 0.02...1.2 s ¦ 0.5...30 h ¦ 0.2...12 s ¦ 5...300 h ¦ 0.5...30 s ¦ 0.05...3 s ¦ 5...300 s ¦ 2...120 min ¦ 0.5...30 min
RE48AMH13MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE48AMH13MW | Main | voltage range | 0.85...1.1 Us AC ¦ 0.9...1.1 Us DC
RE48AMH13MW | Main | [In] rated current | 5 A
RE48AMH13MW | Complementary | product front plate size | 48 x 48 mm
RE48AMH13MW | Complementary | control type | Selector switch front panel
RE48AMH13MW | Complementary | housing material | Self-extinguishing
RE48AMH13MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
RE48AMH13MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
RE48AMH13MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V ¦ +/- 1 %/V of the maximum setting value at 24...48 V
RE48AMH13MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
RE48AMH13MW | Complementary | minimum pulse duration | 20 ms
RE48AMH13MW | Complementary | reset time | 25 ms on de-energisation
RE48AMH13MW | Complementary | pick up duration | 55 ms
RE48AMH13MW | Complementary | on-load factor | 100 %
RE48AMH13MW | Complementary | power consumption in VA | 1.1 VA at 24 V ¦ 4.8 VA at 240 V
RE48AMH13MW | Complementary | power consumption in W | 0.5 W at 24 V ¦ 1.7 W at 240 V
RE48AMH13MW | Complementary | breaking capacity | 1250 VA
RE48AMH13MW | Complementary | minimum switching current | 100 mA
RE48AMH13MW | Complementary | maximum switching current | 5 A
RE48AMH13MW | Complementary | maximum switching voltage | 250 V AC/DC
RE48AMH13MW | Complementary | electrical durability | 100000 cycles
RE48AMH13MW | Complementary | mechanical durability | 30000000 cycles
RE48AMH13MW | Complementary | output voltage | 240 V at 5 A AC-12 ¦ 30 V at 2 A DC-13 ¦ 240 V at 1.5 A AC-15
RE48AMH13MW | Complementary | marking | CE
RE48AMH13MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 ¦ 2 kV common mode conforming to IEC 61000-4-5 level 3
RE48AMH13MW | Complementary | mounting support | Base mounted: socket ¦ Panel mounted: system supplied with the product
RE48AMH13MW | Complementary | local signalling | 1 LED (yellow) for output relay state ¦ LED indicator (green) for flashing: relay energised timing in progress ¦ LED indicator (green) for on steady: relay energised, no timing in progress
RE48AMH13MW | Complementary | net weight | 0.14 kg
RE48AMH13MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
RE48AMH13MW | Environment | immunity to microbreaks | 10 ms
RE48AMH13MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
RE48AMH13MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 ¦ 4 kV class III conforming to IEC 61812-1
RE48AMH13MW | Environment | standards | EN 50082-1/2 ¦ EN 50081-1/2 ¦ 93/68/EEC ¦ 73/23/EEC ¦ 89/336/EEC ¦ IEC 60669-2-3 ¦ IEC 61812-1
RE48AMH13MW | Environment | product certifications | GL ¦ CULus ¦ UL ¦ CSA ¦ C-Tick
RE48AMH13MW | Environment | ambient air temperature for storage | -40…70 °C
RE48AMH13MW | Environment | ambient air temperature for operation | -20…50 °C
RE48AMH13MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 ¦ IP50 (front face) conforming to IEC 60529
RE48AMH13MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
RE48AMH13MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
RE48AMH13MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
RE48AMH13MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to IEC 61000-4-3 level 3
RE48AMH13MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 ¦ 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
RE48AMH13MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
RE48AMH13MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11 ¦ 95 % / 5 s conforming to EN/IEC 61000-4-11
RE48AMH13MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
RE48AMH13MW | Offer Sustainability | Sustainable offer status | Green Premium product
RE48AMH13MW | Offer Sustainability | REACh Regulation | REACh Declaration
RE48AMH13MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE48AMH13MW | Offer Sustainability | Mercury free | Yes
RE48AMH13MW | Offer Sustainability | RoHS exemption information | Yes
RE48AMH13MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE48AMH13MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE48AMH13MW | Offer Sustainability | Circularity Profile | End of Life Information
RE48AMH13MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RE48AMH13MW | Contractual warranty | Warranty | 18 months
RE48ACV12MW | Main | range of product | Zelio Time
RE48ACV12MW | Main | product or component type | Electronic timing relay
RE48ACV12MW | Main | electrical connection | Plug-in sub-base 11 pin(s)
RE48ACV12MW | Main | discrete output type | Relay
RE48ACV12MW | Main | contacts type and composition | 2 C/O timed contacts, AgNi (cadmium free)
RE48ACV12MW | Main | component name | RE48A
RE48ACV12MW | Main | time delay type | Li ¦ L
RE48ACV12MW | Main | time delay range | 0.2...12 min ¦ 5...300 s ¦ 0.02...1.2 s ¦ 0.5...30 min ¦ 5...300 h ¦ 0.2...12 h ¦ 0.2...12 s ¦ 0.5...30 s ¦ 2...120 s ¦ 0.05...3 s ¦ 2...120 min ¦ 5...300 min ¦ 0.5...30 h ¦ 2...120 h
RE48ACV12MW | Main | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
RE48ACV12MW | Main | voltage range | 0.85...1.1 Us AC ¦ 0.9...1.1 Us DC
RE48ACV12MW | Main | [In] rated current | 5 A
RE48ACV12MW | Complementary | product front plate size | 48 x 48 mm
RE48ACV12MW | Complementary | control type | Selector switch front panel
RE48ACV12MW | Complementary | housing material | Self-extinguishing
RE48ACV12MW | Complementary | repeat accuracy | +/- 0.2 % of the maximum setting value conforming to IEC 61812-1
RE48ACV12MW | Complementary | temperature drift | +/- 0.02 %/°C of the maximum setting value conforming to IEC 61812-1
RE48ACV12MW | Complementary | voltage drift | +/- 0.2 %/V of the maximum setting value at 48...240 V ¦ +/- 1 %/V of the maximum setting value at 24...48 V
RE48ACV12MW | Complementary | setting accuracy of time delay | +/- 5 % of full scale at 25 °C conforming to IEC 61812-1
RE48ACV12MW | Complementary | minimum pulse duration | 20 ms
RE48ACV12MW | Complementary | reset time | 25 ms on de-energisation
RE48ACV12MW | Complementary | pick up duration | 55 ms
RE48ACV12MW | Complementary | on-load factor | 100 %
RE48ACV12MW | Complementary | power consumption in VA | 1.1 VA at 24 V ¦ 4.8 VA at 240 V
RE48ACV12MW | Complementary | power consumption in W | 0.5 W at 24 V ¦ 1.7 W at 240 V
RE48ACV12MW | Complementary | breaking capacity | 1250 VA
RE48ACV12MW | Complementary | minimum switching current | 100 mA
RE48ACV12MW | Complementary | maximum switching current | 5 A
RE48ACV12MW | Complementary | maximum switching voltage | 250 V AC/DC
RE48ACV12MW | Complementary | electrical durability | 100000 cycles
RE48ACV12MW | Complementary | mechanical durability | 30000000 cycles
RE48ACV12MW | Complementary | output voltage | 240 V at 5 A AC-12 ¦ 30 V at 2 A DC-13 ¦ 240 V at 1.5 A AC-15
RE48ACV12MW | Complementary | marking | CE
RE48ACV12MW | Complementary | surge withstand | 1 kV differential mode conforming to IEC 61000-4-5 level 3 ¦ 2 kV common mode conforming to IEC 61000-4-5 level 3
RE48ACV12MW | Complementary | mounting support | Base mounted: socket ¦ Panel mounted: system supplied with the product
RE48ACV12MW | Complementary | local signalling | 1 LED (yellow) for output relay state ¦ LED indicator (green) for flashing: relay energised timing in progress ¦ LED indicator (green) for on steady: relay energised, no timing in progress
RE48ACV12MW | Complementary | net weight | 0.14 kg
RE48ACV12MW | Environment | humidity drift | +/- 0.05 %/%RH of the maximum setting value conforming to IEC 61812-1
RE48ACV12MW | Environment | immunity to microbreaks | 10 ms
RE48ACV12MW | Environment | dielectric strength | 1 kV 1 mA/1 minute conforming to IEC 61812-1
RE48ACV12MW | Environment | protection against electric shocks | 4 kV class III conforming to IEC 60664-1 ¦ 4 kV class III conforming to IEC 61812-1
RE48ACV12MW | Environment | standards | EN 50081-1/2 ¦ EN 50082-1/2 ¦ IEC 61812-1 ¦ 93/68/EEC ¦ 89/336/EEC ¦ IEC 60669-2-3 ¦ 73/23/EEC
RE48ACV12MW | Environment | product certifications | GL ¦ UL ¦ C-Tick ¦ CULus ¦ CSA
RE48ACV12MW | Environment | ambient air temperature for storage | -40…70 °C
RE48ACV12MW | Environment | ambient air temperature for operation | -20…50 °C
RE48ACV12MW | Environment | IP degree of protection | IP40 (housing) conforming to IEC 60529 ¦ IP50 (front face) conforming to IEC 60529
RE48ACV12MW | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
RE48ACV12MW | Environment | relative humidity | 93 % without condensation conforming to IEC 60068-2-3
RE48ACV12MW | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
RE48ACV12MW | Environment | resistance to electromagnetic fields | 10 V/m 26 MHz to 1 GHz conforming to EN/IEC 61000-4-3 level 3
RE48ACV12MW | Environment | resistance to fast transients | 2 kV (capacitive connecting clip) conforming to EN/IEC 61000-4-4 level 4 ¦ 4 kV (direct) conforming to EN/IEC 61000-4-4 level 4
RE48ACV12MW | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
RE48ACV12MW | Environment | immunity to voltage dips | 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11 ¦ 95 % / 5 s conforming to EN/IEC 61000-4-11
RE48ACV12MW | Environment | disturbance radiated/conducted | Class B 0.15...30 MHz conforming to EN 55022 (EN 55011 group 1)
RE48ACV12MW | Offer Sustainability | Sustainable offer status | Green Premium product
RE48ACV12MW | Offer Sustainability | REACh Regulation | REACh Declaration
RE48ACV12MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RE48ACV12MW | Offer Sustainability | Mercury free | Yes
RE48ACV12MW | Offer Sustainability | RoHS exemption information | Yes
RE48ACV12MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RE48ACV12MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RE48ACV12MW | Offer Sustainability | Circularity Profile | End of Life Information
RE48ACV12MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RE48ACV12MW | Contractual warranty | Warranty | 18 months
REXL2TMJD | Main | range of product | Zelio Time
REXL2TMJD | Main | product or component type | Miniature timing relay
REXL2TMJD | Main | fixing mode | Plug-in (socket)
REXL2TMJD | Main | discrete output type | Relay
REXL2TMJD | Main | contacts type and composition | 2 C/O
REXL2TMJD | Main | component name | REXL
REXL2TMJD | Main | time delay type | A
REXL2TMJD | Main | time delay range | 10...100 h ¦ 0.1...1 s ¦ 1...10 s ¦ 6...60 min ¦ 1...10 h ¦ 1...10 min ¦ 6...60 s
REXL2TMJD | Complementary | contacts material | Cadmium free
REXL2TMJD | Complementary | [Us] rated supply voltage | 12 V DC
REXL2TMJD | Complementary | voltage range | 0.9...1.1 Us
REXL2TMJD | Complementary | [In] rated current | 5 A AC
REXL2TMJD | Complementary | repeat accuracy | +/- 0.5 %
REXL2TMJD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL2TMJD | Complementary | temperature drift | 0.05 %/°C
REXL2TMJD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL2TMJD | Complementary | voltage drift | +/- 0.2 %/V
REXL2TMJD | Complementary | maximum switching capacity | 4 x 5 A
REXL2TMJD | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL2TMJD | Complementary | minimum switching current | 100 mA
REXL2TMJD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL2TMJD | Complementary | mechanical durability | 10000000 cycles
REXL2TMJD | Complementary | maximum power consumption | 1.5 W
REXL2TMJD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL2TMJD | Complementary | output overvoltage protection | 2 J
REXL2TMJD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL2TMJD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL2TMJD | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL2TMJD | Complementary | net weight | 0.05 kg
REXL2TMJD | Environment | immunity to microbreaks | 5 ms
REXL2TMJD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL2TMJD | Environment | standards | 93/68/EEC ¦ EN/IEC 61812-1 ¦ EN/IEC 60601-1 ¦ 89/336/EEC ¦ EN/IEC 60601-2 ¦ 73/23/EEC ¦ EN 61000-6-2 ¦ EN 50081-2
REXL2TMJD | Environment | product certifications | UL ¦ CUL
REXL2TMJD | Environment | ambient air temperature for operation | -20…60 °C
REXL2TMJD | Environment | ambient air temperature for storage | -40…70 °C
REXL2TMJD | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL2TMJD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL2TMJD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL2TMJD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL2TMJD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL2TMJD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL2TMJD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL2TMJD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL2TMJD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL2TMJD | Offer Sustainability | Sustainable offer status | Green Premium product
REXL2TMJD | Offer Sustainability | REACh Regulation | REACh Declaration
REXL2TMJD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL2TMJD | Offer Sustainability | Mercury free | Yes
REXL2TMJD | Offer Sustainability | RoHS exemption information | Yes
REXL2TMJD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL2TMJD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL2TMJD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL2TMJD | Contractual warranty | Warranty | 18 months
REXL2TMBD | Main | range of product | Zelio Time
REXL2TMBD | Main | product or component type | Miniature timing relay
REXL2TMBD | Main | fixing mode | Plug-in (socket)
REXL2TMBD | Main | discrete output type | Relay
REXL2TMBD | Main | contacts type and composition | 2 C/O
REXL2TMBD | Main | component name | REXL
REXL2TMBD | Main | time delay type | A
REXL2TMBD | Main | time delay range | 1...10 s ¦ 1...10 min ¦ 6...60 min ¦ 0.1...1 s ¦ 1...10 h ¦ 10...100 h ¦ 6...60 s
REXL2TMBD | Complementary | contacts material | Cadmium free
REXL2TMBD | Complementary | [Us] rated supply voltage | 24 V DC
REXL2TMBD | Complementary | voltage range | 0.9...1.1 Us
REXL2TMBD | Complementary | [In] rated current | 5 A AC
REXL2TMBD | Complementary | repeat accuracy | +/- 0.5 %
REXL2TMBD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL2TMBD | Complementary | temperature drift | 0.05 %/°C
REXL2TMBD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL2TMBD | Complementary | voltage drift | +/- 0.2 %/V
REXL2TMBD | Complementary | maximum switching capacity | 4 x 5 A
REXL2TMBD | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL2TMBD | Complementary | minimum switching current | 100 mA
REXL2TMBD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL2TMBD | Complementary | mechanical durability | 10000000 cycles
REXL2TMBD | Complementary | maximum power consumption | 1.2 W
REXL2TMBD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL2TMBD | Complementary | output overvoltage protection | 2 J
REXL2TMBD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL2TMBD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL2TMBD | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL2TMBD | Complementary | net weight | 0.05 kg
REXL2TMBD | Environment | immunity to microbreaks | 5 ms
REXL2TMBD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL2TMBD | Environment | standards | 73/23/EEC ¦ EN 50081-2 ¦ 93/68/EEC ¦ EN/IEC 61812-1 ¦ EN 61000-6-2 ¦ EN/IEC 60601-1 ¦ EN/IEC 60601-2 ¦ 89/336/EEC
REXL2TMBD | Environment | product certifications | CUL ¦ UL
REXL2TMBD | Environment | ambient air temperature for operation | -20…60 °C
REXL2TMBD | Environment | ambient air temperature for storage | -40…70 °C
REXL2TMBD | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL2TMBD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL2TMBD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL2TMBD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL2TMBD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL2TMBD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL2TMBD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL2TMBD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL2TMBD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL2TMBD | Offer Sustainability | Sustainable offer status | Green Premium product
REXL2TMBD | Offer Sustainability | REACh Regulation | REACh Declaration
REXL2TMBD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL2TMBD | Offer Sustainability | Mercury free | Yes
REXL2TMBD | Offer Sustainability | RoHS exemption information | Yes
REXL2TMBD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL2TMBD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL2TMBD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL2TMBD | Contractual warranty | Warranty | 18 months
REXL2TMB7 | Main | range of product | Zelio Time
REXL2TMB7 | Main | product or component type | Miniature timing relay
REXL2TMB7 | Main | fixing mode | Plug-in (socket)
REXL2TMB7 | Main | discrete output type | Relay
REXL2TMB7 | Main | contacts type and composition | 2 C/O
REXL2TMB7 | Main | component name | REXL
REXL2TMB7 | Main | time delay type | A
REXL2TMB7 | Main | time delay range | 10...100 h ¦ 6...60 min ¦ 0.1...1 s ¦ 1...10 h ¦ 1...10 min ¦ 6...60 s ¦ 1...10 s
REXL2TMB7 | Complementary | contacts material | Cadmium free
REXL2TMB7 | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz
REXL2TMB7 | Complementary | voltage range | 0.85...1.15 Us
REXL2TMB7 | Complementary | [In] rated current | 5 A AC
REXL2TMB7 | Complementary | repeat accuracy | +/- 0.5 %
REXL2TMB7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL2TMB7 | Complementary | temperature drift | 0.05 %/°C
REXL2TMB7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL2TMB7 | Complementary | voltage drift | +/- 0.2 %/V
REXL2TMB7 | Complementary | maximum switching capacity | 4 x 5 A
REXL2TMB7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL2TMB7 | Complementary | minimum switching current | 100 mA
REXL2TMB7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL2TMB7 | Complementary | mechanical durability | 10000000 cycles
REXL2TMB7 | Complementary | maximum power consumption | 1.7 VA
REXL2TMB7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL2TMB7 | Complementary | output overvoltage protection | 2 J
REXL2TMB7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL2TMB7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL2TMB7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL2TMB7 | Complementary | net weight | 0.05 kg
REXL2TMB7 | Environment | immunity to microbreaks | 5 ms
REXL2TMB7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL2TMB7 | Environment | standards | EN 50081-2 ¦ EN 61000-6-2 ¦ EN/IEC 60601-2 ¦ EN/IEC 61812-1 ¦ 93/68/EEC ¦ 73/23/EEC ¦ 89/336/EEC ¦ EN/IEC 60601-1
REXL2TMB7 | Environment | product certifications | UL ¦ CUL
REXL2TMB7 | Environment | ambient air temperature for operation | -20…60 °C
REXL2TMB7 | Environment | ambient air temperature for storage | -40…70 °C
REXL2TMB7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL2TMB7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL2TMB7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL2TMB7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL2TMB7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL2TMB7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL2TMB7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL2TMB7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL2TMB7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL2TMB7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL2TMB7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL2TMB7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL2TMB7 | Offer Sustainability | Mercury free | Yes
REXL2TMB7 | Offer Sustainability | RoHS exemption information | Yes
REXL2TMB7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL2TMB7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL2TMB7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL2TMB7 | Contractual warranty | Warranty | 18 months
REXL2TMF7 | Main | range of product | Zelio Time
REXL2TMF7 | Main | product or component type | Miniature timing relay
REXL2TMF7 | Main | fixing mode | Plug-in (socket)
REXL2TMF7 | Main | discrete output type | Relay
REXL2TMF7 | Main | contacts type and composition | 2 C/O
REXL2TMF7 | Main | component name | REXL
REXL2TMF7 | Main | time delay type | A
REXL2TMF7 | Main | time delay range | 10...100 h ¦ 6...60 s ¦ 6...60 min ¦ 1...10 min ¦ 0.1...1 s ¦ 1...10 s ¦ 1...10 h
REXL2TMF7 | Complementary | contacts material | Cadmium free
REXL2TMF7 | Complementary | [Us] rated supply voltage | 120 V AC 50/60 Hz
REXL2TMF7 | Complementary | voltage range | 0.85...1.15 Us
REXL2TMF7 | Complementary | [In] rated current | 5 A AC
REXL2TMF7 | Complementary | repeat accuracy | +/- 0.5 %
REXL2TMF7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL2TMF7 | Complementary | temperature drift | 0.05 %/°C
REXL2TMF7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL2TMF7 | Complementary | voltage drift | +/- 0.2 %/V
REXL2TMF7 | Complementary | maximum switching capacity | 4 x 5 A
REXL2TMF7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL2TMF7 | Complementary | minimum switching current | 100 mA
REXL2TMF7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL2TMF7 | Complementary | mechanical durability | 10000000 cycles
REXL2TMF7 | Complementary | maximum power consumption | 2.6 VA
REXL2TMF7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL2TMF7 | Complementary | output overvoltage protection | 2 J
REXL2TMF7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL2TMF7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL2TMF7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL2TMF7 | Complementary | net weight | 0.05 kg
REXL2TMF7 | Environment | immunity to microbreaks | 5 ms
REXL2TMF7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL2TMF7 | Environment | standards | EN 61000-6-2 ¦ 93/68/EEC ¦ EN 50081-2 ¦ EN/IEC 61812-1 ¦ 73/23/EEC ¦ EN/IEC 60601-2 ¦ 89/336/EEC ¦ EN/IEC 60601-1
REXL2TMF7 | Environment | product certifications | CUL ¦ UL
REXL2TMF7 | Environment | ambient air temperature for operation | -20…60 °C
REXL2TMF7 | Environment | ambient air temperature for storage | -40…70 °C
REXL2TMF7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL2TMF7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL2TMF7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL2TMF7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL2TMF7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL2TMF7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL2TMF7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL2TMF7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL2TMF7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL2TMF7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL2TMF7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL2TMF7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL2TMF7 | Offer Sustainability | Mercury free | Yes
REXL2TMF7 | Offer Sustainability | RoHS exemption information | Yes
REXL2TMF7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL2TMF7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL2TMF7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL2TMF7 | Contractual warranty | Warranty | 18 months
REXL2TMP7 | Main | range of product | Zelio Time
REXL2TMP7 | Main | product or component type | Miniature timing relay
REXL2TMP7 | Main | fixing mode | Plug-in (socket)
REXL2TMP7 | Main | discrete output type | Relay
REXL2TMP7 | Main | contacts type and composition | 2 C/O
REXL2TMP7 | Main | component name | REXL
REXL2TMP7 | Main | time delay type | A
REXL2TMP7 | Main | time delay range | 10...100 h ¦ 1...10 min ¦ 1...10 h ¦ 0.1...1 s ¦ 6...60 min ¦ 6...60 s ¦ 1...10 s
REXL2TMP7 | Complementary | contacts material | Cadmium free
REXL2TMP7 | Complementary | [Us] rated supply voltage | 230 V AC 50/60 Hz
REXL2TMP7 | Complementary | voltage range | 0.85...1.15 Us
REXL2TMP7 | Complementary | [In] rated current | 5 A AC
REXL2TMP7 | Complementary | repeat accuracy | +/- 0.5 %
REXL2TMP7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL2TMP7 | Complementary | temperature drift | 0.05 %/°C
REXL2TMP7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL2TMP7 | Complementary | voltage drift | +/- 0.2 %/V
REXL2TMP7 | Complementary | maximum switching capacity | 4 x 5 A
REXL2TMP7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL2TMP7 | Complementary | minimum switching current | 100 mA
REXL2TMP7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL2TMP7 | Complementary | mechanical durability | 10000000 cycles
REXL2TMP7 | Complementary | maximum power consumption | 3 VA
REXL2TMP7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL2TMP7 | Complementary | output overvoltage protection | 2 J
REXL2TMP7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL2TMP7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL2TMP7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL2TMP7 | Complementary | net weight | 0.05 kg
REXL2TMP7 | Environment | immunity to microbreaks | 5 ms
REXL2TMP7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL2TMP7 | Environment | standards | EN/IEC 60601-1 ¦ 89/336/EEC ¦ EN 61000-6-2 ¦ EN 50081-2 ¦ EN/IEC 61812-1 ¦ 73/23/EEC ¦ EN/IEC 60601-2 ¦ 93/68/EEC
REXL2TMP7 | Environment | product certifications | UL ¦ CUL
REXL2TMP7 | Environment | ambient air temperature for operation | -20…60 °C
REXL2TMP7 | Environment | ambient air temperature for storage | -40…70 °C
REXL2TMP7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL2TMP7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL2TMP7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL2TMP7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL2TMP7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL2TMP7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL2TMP7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL2TMP7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL2TMP7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL2TMP7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL2TMP7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL2TMP7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL2TMP7 | Offer Sustainability | Mercury free | Yes
REXL2TMP7 | Offer Sustainability | RoHS exemption information | Yes
REXL2TMP7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL2TMP7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL2TMP7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL2TMP7 | Contractual warranty | Warranty | 18 months
REXL4TMJD | Main | range of product | Zelio Time
REXL4TMJD | Main | product or component type | Miniature timing relay
REXL4TMJD | Main | fixing mode | Plug-in (socket)
REXL4TMJD | Main | discrete output type | Relay
REXL4TMJD | Main | contacts type and composition | 4 C/O
REXL4TMJD | Main | component name | REXL
REXL4TMJD | Main | time delay type | A
REXL4TMJD | Main | time delay range | 10...100 h ¦ 6...60 min ¦ 1...10 h ¦ 0.1...1 s ¦ 6...60 s ¦ 1...10 s ¦ 1...10 min
REXL4TMJD | Complementary | contacts material | Cadmium free
REXL4TMJD | Complementary | [Us] rated supply voltage | 12 V DC
REXL4TMJD | Complementary | voltage range | 0.9...1.1 Us
REXL4TMJD | Complementary | [In] rated current | 5 A AC
REXL4TMJD | Complementary | repeat accuracy | +/- 0.5 %
REXL4TMJD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL4TMJD | Complementary | temperature drift | 0.05 %/°C
REXL4TMJD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL4TMJD | Complementary | voltage drift | +/- 0.2 %/V
REXL4TMJD | Complementary | maximum switching capacity | 4 x 5 A
REXL4TMJD | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL4TMJD | Complementary | minimum switching current | 100 mA
REXL4TMJD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL4TMJD | Complementary | mechanical durability | 10000000 cycles
REXL4TMJD | Complementary | maximum power consumption | 1.5 W
REXL4TMJD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL4TMJD | Complementary | output overvoltage protection | 2 J
REXL4TMJD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL4TMJD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL4TMJD | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL4TMJD | Complementary | net weight | 0.05 kg
REXL4TMJD | Environment | immunity to microbreaks | 5 ms
REXL4TMJD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL4TMJD | Environment | standards | 93/68/EEC ¦ EN 50081-2 ¦ 73/23/EEC ¦ EN 61000-6-2 ¦ EN/IEC 60601-2 ¦ EN/IEC 60601-1 ¦ 89/336/EEC ¦ EN/IEC 61812-1
REXL4TMJD | Environment | product certifications | UL ¦ CUL
REXL4TMJD | Environment | ambient air temperature for operation | -20…60 °C
REXL4TMJD | Environment | ambient air temperature for storage | -40…70 °C
REXL4TMJD | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL4TMJD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL4TMJD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL4TMJD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL4TMJD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL4TMJD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL4TMJD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL4TMJD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL4TMJD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL4TMJD | Offer Sustainability | Sustainable offer status | Green Premium product
REXL4TMJD | Offer Sustainability | REACh Regulation | REACh Declaration
REXL4TMJD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL4TMJD | Offer Sustainability | Mercury free | Yes
REXL4TMJD | Offer Sustainability | RoHS exemption information | Yes
REXL4TMJD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL4TMJD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL4TMJD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL4TMJD | Contractual warranty | Warranty | 18 months
REXL4TMBD | Main | range of product | Zelio Time
REXL4TMBD | Main | product or component type | Miniature timing relay
REXL4TMBD | Main | fixing mode | Plug-in (socket)
REXL4TMBD | Main | discrete output type | Relay
REXL4TMBD | Main | contacts type and composition | 4 C/O
REXL4TMBD | Main | component name | REXL
REXL4TMBD | Main | time delay type | A
REXL4TMBD | Main | time delay range | 10...100 h ¦ 6...60 s ¦ 6...60 min ¦ 1...10 s ¦ 1...10 h ¦ 1...10 min ¦ 0.1...1 s
REXL4TMBD | Complementary | contacts material | Cadmium free
REXL4TMBD | Complementary | [Us] rated supply voltage | 24 V DC
REXL4TMBD | Complementary | voltage range | 0.9...1.1 Us
REXL4TMBD | Complementary | [In] rated current | 5 A AC
REXL4TMBD | Complementary | repeat accuracy | +/- 0.5 %
REXL4TMBD | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL4TMBD | Complementary | temperature drift | 0.05 %/°C
REXL4TMBD | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL4TMBD | Complementary | voltage drift | +/- 0.2 %/V
REXL4TMBD | Complementary | maximum switching capacity | 4 x 5 A
REXL4TMBD | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL4TMBD | Complementary | minimum switching current | 100 mA
REXL4TMBD | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL4TMBD | Complementary | mechanical durability | 10000000 cycles
REXL4TMBD | Complementary | maximum power consumption | 1.2 W
REXL4TMBD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL4TMBD | Complementary | output overvoltage protection | 2 J
REXL4TMBD | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL4TMBD | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL4TMBD | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL4TMBD | Complementary | net weight | 0.05 kg
REXL4TMBD | Environment | immunity to microbreaks | 5 ms
REXL4TMBD | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL4TMBD | Environment | standards | EN/IEC 60601-2 ¦ EN 61000-6-2 ¦ 73/23/EEC ¦ EN/IEC 61812-1 ¦ 93/68/EEC ¦ EN/IEC 60601-1 ¦ 89/336/EEC ¦ EN 50081-2
REXL4TMBD | Environment | product certifications | UL ¦ CUL
REXL4TMBD | Environment | ambient air temperature for operation | -20…60 °C
REXL4TMBD | Environment | ambient air temperature for storage | -40…70 °C
REXL4TMBD | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL4TMBD | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL4TMBD | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL4TMBD | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL4TMBD | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL4TMBD | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL4TMBD | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL4TMBD | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL4TMBD | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL4TMBD | Offer Sustainability | Sustainable offer status | Green Premium product
REXL4TMBD | Offer Sustainability | REACh Regulation | REACh Declaration
REXL4TMBD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL4TMBD | Offer Sustainability | Mercury free | Yes
REXL4TMBD | Offer Sustainability | RoHS exemption information | Yes
REXL4TMBD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL4TMBD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL4TMBD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL4TMBD | Contractual warranty | Warranty | 18 months
REXL4TMB7 | Main | range of product | Zelio Time
REXL4TMB7 | Main | product or component type | Miniature timing relay
REXL4TMB7 | Main | fixing mode | Plug-in (socket)
REXL4TMB7 | Main | discrete output type | Relay
REXL4TMB7 | Main | contacts type and composition | 4 C/O
REXL4TMB7 | Main | component name | REXL
REXL4TMB7 | Main | time delay type | A
REXL4TMB7 | Main | time delay range | 6...60 s ¦ 1...10 s ¦ 1...10 h ¦ 1...10 min ¦ 6...60 min ¦ 10...100 h ¦ 0.1...1 s
REXL4TMB7 | Complementary | contacts material | Cadmium free
REXL4TMB7 | Complementary | [Us] rated supply voltage | 24 V AC 50/60 Hz
REXL4TMB7 | Complementary | voltage range | 0.85...1.15 Us
REXL4TMB7 | Complementary | [In] rated current | 5 A AC
REXL4TMB7 | Complementary | repeat accuracy | +/- 0.5 %
REXL4TMB7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL4TMB7 | Complementary | temperature drift | 0.05 %/°C
REXL4TMB7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL4TMB7 | Complementary | voltage drift | +/- 0.2 %/V
REXL4TMB7 | Complementary | maximum switching capacity | 4 x 5 A
REXL4TMB7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL4TMB7 | Complementary | minimum switching current | 100 mA
REXL4TMB7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL4TMB7 | Complementary | mechanical durability | 10000000 cycles
REXL4TMB7 | Complementary | maximum power consumption | 1.7 VA
REXL4TMB7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL4TMB7 | Complementary | output overvoltage protection | 2 J
REXL4TMB7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL4TMB7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL4TMB7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL4TMB7 | Complementary | net weight | 0.05 kg
REXL4TMB7 | Environment | immunity to microbreaks | 5 ms
REXL4TMB7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL4TMB7 | Environment | standards | EN/IEC 60601-1 ¦ 89/336/EEC ¦ EN/IEC 61812-1 ¦ EN/IEC 60601-2 ¦ 73/23/EEC ¦ 93/68/EEC ¦ EN 61000-6-2 ¦ EN 50081-2
REXL4TMB7 | Environment | product certifications | UL ¦ CUL
REXL4TMB7 | Environment | ambient air temperature for operation | -20…60 °C
REXL4TMB7 | Environment | ambient air temperature for storage | -40…70 °C
REXL4TMB7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL4TMB7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL4TMB7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL4TMB7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL4TMB7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL4TMB7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL4TMB7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL4TMB7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL4TMB7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL4TMB7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL4TMB7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL4TMB7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL4TMB7 | Offer Sustainability | Mercury free | Yes
REXL4TMB7 | Offer Sustainability | RoHS exemption information | Yes
REXL4TMB7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL4TMB7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL4TMB7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL4TMB7 | Contractual warranty | Warranty | 18 months
REXL4TMF7 | Main | range of product | Zelio Time
REXL4TMF7 | Main | product or component type | Miniature timing relay
REXL4TMF7 | Main | fixing mode | Plug-in (socket)
REXL4TMF7 | Main | discrete output type | Relay
REXL4TMF7 | Main | contacts type and composition | 4 C/O
REXL4TMF7 | Main | component name | REXL
REXL4TMF7 | Main | time delay type | A
REXL4TMF7 | Main | time delay range | 1...10 min ¦ 10...100 h ¦ 6...60 s ¦ 0.1...1 s ¦ 1...10 h ¦ 6...60 min ¦ 1...10 s
REXL4TMF7 | Complementary | contacts material | Cadmium free
REXL4TMF7 | Complementary | [Us] rated supply voltage | 120 V AC 50/60 Hz
REXL4TMF7 | Complementary | voltage range | 0.85...1.15 Us
REXL4TMF7 | Complementary | [In] rated current | 5 A AC
REXL4TMF7 | Complementary | repeat accuracy | +/- 0.5 %
REXL4TMF7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL4TMF7 | Complementary | temperature drift | 0.05 %/°C
REXL4TMF7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL4TMF7 | Complementary | voltage drift | +/- 0.2 %/V
REXL4TMF7 | Complementary | maximum switching capacity | 4 x 5 A
REXL4TMF7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL4TMF7 | Complementary | minimum switching current | 100 mA
REXL4TMF7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL4TMF7 | Complementary | mechanical durability | 10000000 cycles
REXL4TMF7 | Complementary | maximum power consumption | 2.6 VA
REXL4TMF7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL4TMF7 | Complementary | output overvoltage protection | 2 J
REXL4TMF7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL4TMF7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL4TMF7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL4TMF7 | Complementary | net weight | 0.05 kg
REXL4TMF7 | Environment | immunity to microbreaks | 5 ms
REXL4TMF7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL4TMF7 | Environment | standards | EN 61000-6-2 ¦ EN/IEC 60601-1 ¦ 89/336/EEC ¦ 93/68/EEC ¦ EN/IEC 61812-1 ¦ EN/IEC 60601-2 ¦ 73/23/EEC ¦ EN 50081-2
REXL4TMF7 | Environment | product certifications | CUL ¦ UL
REXL4TMF7 | Environment | ambient air temperature for operation | -20…60 °C
REXL4TMF7 | Environment | ambient air temperature for storage | -40…70 °C
REXL4TMF7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL4TMF7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL4TMF7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL4TMF7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL4TMF7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL4TMF7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL4TMF7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL4TMF7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL4TMF7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL4TMF7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL4TMF7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL4TMF7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL4TMF7 | Offer Sustainability | Mercury free | Yes
REXL4TMF7 | Offer Sustainability | RoHS exemption information | Yes
REXL4TMF7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL4TMF7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL4TMF7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
REXL4TMF7 | Contractual warranty | Warranty | 18 months
REXL4TMP7 | Main | range of product | Zelio Time
REXL4TMP7 | Main | product or component type | Miniature timing relay
REXL4TMP7 | Main | fixing mode | Plug-in (socket)
REXL4TMP7 | Main | discrete output type | Relay
REXL4TMP7 | Main | contacts type and composition | 4 C/O
REXL4TMP7 | Main | component name | REXL
REXL4TMP7 | Main | time delay type | A
REXL4TMP7 | Main | time delay range | 6...60 s ¦ 1...10 s ¦ 6...60 min ¦ 1...10 min ¦ 0.1...1 s ¦ 10...100 h ¦ 1...10 h
REXL4TMP7 | Complementary | contacts material | Cadmium free
REXL4TMP7 | Complementary | [Us] rated supply voltage | 230 V AC 50/60 Hz
REXL4TMP7 | Complementary | voltage range | 0.85...1.15 Us
REXL4TMP7 | Complementary | [In] rated current | 5 A AC
REXL4TMP7 | Complementary | repeat accuracy | +/- 0.5 %
REXL4TMP7 | Complementary | setting accuracy of time delay | 10 % at full scale at 25 °C conforming to EN/IEC 61812-1
REXL4TMP7 | Complementary | temperature drift | 0.05 %/°C
REXL4TMP7 | Complementary | maximum reset time | 250 ms after time delay, on de-energisation ¦ 50 ms during time delay, on de-energisation
REXL4TMP7 | Complementary | voltage drift | +/- 0.2 %/V
REXL4TMP7 | Complementary | maximum switching capacity | 4 x 5 A
REXL4TMP7 | Complementary | maximum temporary permissible current | 10 A for < 10 s
REXL4TMP7 | Complementary | minimum switching current | 100 mA
REXL4TMP7 | Complementary | electrical durability | 100000 cycles at 250 V AC resistive
REXL4TMP7 | Complementary | mechanical durability | 10000000 cycles
REXL4TMP7 | Complementary | maximum power consumption | 3 VA
REXL4TMP7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 255 Group C ¦ 250 V conforming to VDE 0010
REXL4TMP7 | Complementary | output overvoltage protection | 2 J
REXL4TMP7 | Complementary | surge withstand | 2 kV conforming to EN/IEC 61000-4-5 level 3
REXL4TMP7 | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
REXL4TMP7 | Complementary | local signalling | 1 LED (red) for output in operation ¦ 1 LED (yellow) for power ON
REXL4TMP7 | Complementary | net weight | 0.05 kg
REXL4TMP7 | Environment | immunity to microbreaks | 5 ms
REXL4TMP7 | Environment | dielectric strength | 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 60601-1 ¦ 2 kV for 1 mA/1 minute at 50 Hz conforming to EN/IEC 61812-1
REXL4TMP7 | Environment | standards | EN 61000-6-2 ¦ EN 50081-2 ¦ EN/IEC 60601-1 ¦ EN/IEC 60601-2 ¦ 73/23/EEC ¦ 93/68/EEC ¦ 89/336/EEC ¦ EN/IEC 61812-1
REXL4TMP7 | Environment | product certifications | CUL ¦ UL
REXL4TMP7 | Environment | ambient air temperature for operation | -20…60 °C
REXL4TMP7 | Environment | ambient air temperature for storage | -40…70 °C
REXL4TMP7 | Environment | IP degree of protection | IP50 conforming to IEC 60529
REXL4TMP7 | Environment | vibration resistance | 0.35 mm (f= 10…55 Hz) conforming to IEC 60068-2-6
REXL4TMP7 | Environment | relative humidity | 95 % without condensation conforming to IEC 60068-2-6
REXL4TMP7 | Environment | resistance to electrostatic discharge | 6 kV in contact conforming to EN/IEC 61000-4-2 level 3 ¦ 8 kV in air conforming to EN/IEC 61000-4-2 level 3
REXL4TMP7 | Environment | resistance to electromagnetic fields | 10 V/m conforming to EN/IEC 61000-4-3 level 3
REXL4TMP7 | Environment | resistance to fast transients | 2 kV conforming to EN/IEC 61000-4-4 level 3
REXL4TMP7 | Environment | immunity to radioelectric fields | 10 V (0.15...80 MHz) conforming to EN/IEC 61000-4-6 level 3
REXL4TMP7 | Environment | immunity to voltage dips | >= 95 % / 1 s conforming to EN/IEC 61000-4-11 ¦ 30 % / 10 ms conforming to EN/IEC 61000-4-11 ¦ 60 % / 100 ms conforming to EN/IEC 61000-4-11
REXL4TMP7 | Environment | disturbance radiated/conducted | Class B conforming to EN 55022 (EN 55011 group 1)
REXL4TMP7 | Offer Sustainability | Sustainable offer status | Green Premium product
REXL4TMP7 | Offer Sustainability | REACh Regulation | REACh Declaration
REXL4TMP7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
REXL4TMP7 | Offer Sustainability | Mercury free | Yes
REXL4TMP7 | Offer Sustainability | RoHS exemption information | Yes
REXL4TMP7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
REXL4TMP7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
REXL4TMP7 | Contractual warranty | Warranty | 18 months
RMPT10BD | Main | range of product | Zelio Analog
RMPT10BD | Main | product or component type | Converter for Universal Pt100 probes
RMPT10BD | Main | analogue input type | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires
RMPT10BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT10BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output ¦ Reverse polarity protection on power supply
RMPT10BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT10BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT10BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT10BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT10BD | Complementary | local signalling | LED (green)power ON:
RMPT10BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT10BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT10BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT10BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT10BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMPT10BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT10BD | Complementary | marking | CE
RMPT10BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT10BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT10BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMPT10BD | Complementary | safety reliability data | B10d = 30437 ¦ MTTFd = 32.9 years
RMPT10BD | Complementary | net weight | 0.12 kg
RMPT10BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT10BD | Environment | standards | DIN 43760 ¦ EN/IEC 60584-1 ¦ EN/IEC 60947-1 ¦ EN/IEC 60751
RMPT10BD | Environment | product certifications | UL ¦ GL ¦ CSA
RMPT10BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT10BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT10BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT10BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT10BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT10BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT10BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT10BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT10BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT10BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMPT10BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMPT10BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT10BD | Offer Sustainability | Mercury free | Yes
RMPT10BD | Offer Sustainability | RoHS exemption information | Yes
RMPT10BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT10BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT10BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT10BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT10BD | Contractual warranty | Warranty | 18 months
RMPT20BD | Main | range of product | Zelio Analog
RMPT20BD | Main | product or component type | Converter for Universal Pt100 probes
RMPT20BD | Main | analogue input type | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires
RMPT20BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT20BD | Complementary | protection type | Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on power supply ¦ Short-circuit protection on output
RMPT20BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT20BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT20BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT20BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT20BD | Complementary | local signalling | LED (green)power ON:
RMPT20BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT20BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT20BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT20BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT20BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMPT20BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT20BD | Complementary | marking | CE
RMPT20BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT20BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT20BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT20BD | Complementary | safety reliability data | MTTFd = 32.9 years ¦ B10d = 30437
RMPT20BD | Complementary | net weight | 0.12 kg
RMPT20BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT20BD | Environment | standards | DIN 43760 ¦ EN/IEC 60751 ¦ EN/IEC 60584-1 ¦ EN/IEC 60947-1
RMPT20BD | Environment | product certifications | GL ¦ CSA ¦ UL
RMPT20BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT20BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT20BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT20BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT20BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT20BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT20BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT20BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT20BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT20BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT20BD | Offer Sustainability | Mercury free | Yes
RMPT20BD | Offer Sustainability | RoHS exemption information | Yes
RMPT20BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT20BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT20BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT20BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT20BD | Contractual warranty | Warranty | 18 months
RMPT30BD | Main | range of product | Zelio Analog
RMPT30BD | Main | product or component type | Converter for Universal Pt100 probes
RMPT30BD | Main | analogue input type | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires
RMPT30BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT30BD | Complementary | protection type | Reverse polarity protection on power supply ¦ Short-circuit protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output
RMPT30BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT30BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT30BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT30BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT30BD | Complementary | local signalling | LED (green)power ON:
RMPT30BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT30BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT30BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT30BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT30BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMPT30BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT30BD | Complementary | marking | CE
RMPT30BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT30BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT30BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT30BD | Complementary | safety reliability data | MTTFd = 32.9 years ¦ B10d = 30437
RMPT30BD | Complementary | net weight | 0.12 kg
RMPT30BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT30BD | Environment | standards | DIN 43760 ¦ EN/IEC 60751 ¦ EN/IEC 60947-1 ¦ EN/IEC 60584-1
RMPT30BD | Environment | product certifications | GL ¦ UL ¦ CSA
RMPT30BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT30BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT30BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT30BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT30BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT30BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMPT30BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT30BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT30BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT30BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMPT30BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMPT30BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT30BD | Offer Sustainability | Mercury free | Yes
RMPT30BD | Offer Sustainability | RoHS exemption information | Yes
RMPT30BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT30BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT30BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT30BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT30BD | Contractual warranty | Warranty | 18 months
RMPT50BD | Main | range of product | Zelio Analog
RMPT50BD | Main | product or component type | Converter for Universal Pt100 probes
RMPT50BD | Main | analogue input type | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires
RMPT50BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT50BD | Complementary | protection type | Reverse polarity protection on output ¦ Short-circuit protection on output ¦ Reverse polarity protection on power supply ¦ Overvoltage protection on output (+/- 30 V)
RMPT50BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT50BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT50BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT50BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT50BD | Complementary | local signalling | LED (green)power ON:
RMPT50BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT50BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT50BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT50BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT50BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMPT50BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT50BD | Complementary | marking | CE
RMPT50BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT50BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT50BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT50BD | Complementary | safety reliability data | B10d = 30437 ¦ MTTFd = 32.9 years
RMPT50BD | Complementary | net weight | 0.12 kg
RMPT50BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT50BD | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60584-1 ¦ DIN 43760 ¦ EN/IEC 60751
RMPT50BD | Environment | product certifications | CSA ¦ UL ¦ GL
RMPT50BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT50BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT50BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT50BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT50BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT50BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT50BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT50BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT50BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT50BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMPT50BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMPT50BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT50BD | Offer Sustainability | Mercury free | Yes
RMPT50BD | Offer Sustainability | RoHS exemption information | Yes
RMPT50BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT50BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT50BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT50BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT50BD | Contractual warranty | Warranty | 18 months
RMPT70BD | Main | range of product | Zelio Analog
RMPT70BD | Main | product or component type | Converter for Universal Pt100 probes
RMPT70BD | Main | analogue input type | Temperature probe 0...500 °C/32...932 °F Pt 100 2, 3 or 4 wires
RMPT70BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT70BD | Complementary | protection type | Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on power supply ¦ Short-circuit protection on output
RMPT70BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT70BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT70BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT70BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT70BD | Complementary | local signalling | LED (green)power ON:
RMPT70BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT70BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT70BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT70BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT70BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMPT70BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT70BD | Complementary | marking | CE
RMPT70BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT70BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT70BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT70BD | Complementary | safety reliability data | MTTFd = 32.9 years ¦ B10d = 30437
RMPT70BD | Complementary | net weight | 0.12 kg
RMPT70BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT70BD | Environment | standards | EN/IEC 60751 ¦ DIN 43760 ¦ EN/IEC 60947-1 ¦ EN/IEC 60584-1
RMPT70BD | Environment | product certifications | UL ¦ CSA ¦ GL
RMPT70BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT70BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT70BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT70BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT70BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT70BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT70BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT70BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT70BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT70BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMPT70BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMPT70BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT70BD | Offer Sustainability | Mercury free | Yes
RMPT70BD | Offer Sustainability | RoHS exemption information | Yes
RMPT70BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT70BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT70BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT70BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT70BD | Contractual warranty | Warranty | 18 months
RMPT13BD | Main | range of product | Zelio Analog
RMPT13BD | Main | product or component type | Converter for Optimum Pt100 probes
RMPT13BD | Main | analogue input type | Temperature probe - 40...40 °C/- 40...104 °F Pt 100 2, 3 or 4 wires
RMPT13BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT13BD | Complementary | protection type | Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on power supply ¦ Short-circuit protection on output
RMPT13BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT13BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT13BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT13BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT13BD | Complementary | local signalling | LED (green)power ON:
RMPT13BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT13BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT13BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT13BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT13BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMPT13BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT13BD | Complementary | marking | CE
RMPT13BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT13BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT13BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT13BD | Complementary | safety reliability data | B10d = 40564 ¦ MTTFd = 43.9 years
RMPT13BD | Complementary | net weight | 0.12 kg
RMPT13BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT13BD | Environment | standards | EN/IEC 60751 ¦ EN/IEC 60584-1 ¦ DIN 43760 ¦ EN/IEC 60947-1
RMPT13BD | Environment | product certifications | CSA ¦ UL ¦ GL
RMPT13BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT13BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT13BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT13BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT13BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT13BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT13BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT13BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT13BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT13BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT13BD | Offer Sustainability | Mercury free | Yes
RMPT13BD | Offer Sustainability | RoHS exemption information | Yes
RMPT13BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT13BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT13BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT13BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT13BD | Contractual warranty | Warranty | 18 months
RMPT23BD | Main | range of product | Zelio Analog
RMPT23BD | Main | product or component type | Converter for Optimum Pt100 probes
RMPT23BD | Main | analogue input type | Temperature probe - 100...100 °C/- 148...212 °F Pt 100 2, 3 or 4 wires
RMPT23BD | Main | analogue output type | Voltage 0...10 V >= 100 kOhm
RMPT23BD | Complementary | protection type | Reverse polarity protection on power supply ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output
RMPT23BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT23BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT23BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT23BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT23BD | Complementary | local signalling | LED (green)power ON:
RMPT23BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT23BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT23BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT23BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT23BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMPT23BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT23BD | Complementary | marking | CE
RMPT23BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT23BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT23BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT23BD | Complementary | safety reliability data | B10d = 40564 ¦ MTTFd = 43.9 years
RMPT23BD | Complementary | net weight | 0.12 kg
RMPT23BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT23BD | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60584-1 ¦ DIN 43760 ¦ EN/IEC 60751
RMPT23BD | Environment | product certifications | CSA ¦ UL ¦ GL
RMPT23BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT23BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT23BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT23BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT23BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT23BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMPT23BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT23BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT23BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT23BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT23BD | Offer Sustainability | Mercury free | Yes
RMPT23BD | Offer Sustainability | RoHS exemption information | Yes
RMPT23BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT23BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT23BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT23BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT23BD | Contractual warranty | Warranty | 18 months
RMPT33BD | Main | range of product | Zelio Analog
RMPT33BD | Main | product or component type | Converter for Optimum Pt100 probes
RMPT33BD | Main | analogue input type | Temperature probe 0...100 °C/32..212 °F Pt 100 2, 3 or 4 wires
RMPT33BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT33BD | Complementary | protection type | Short-circuit protection on output ¦ Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on power supply
RMPT33BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT33BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT33BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT33BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT33BD | Complementary | local signalling | LED (green)power ON:
RMPT33BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT33BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT33BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT33BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT33BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMPT33BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT33BD | Complementary | marking | CE
RMPT33BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT33BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT33BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT33BD | Complementary | safety reliability data | MTTFd = 43.9 years ¦ B10d = 40564
RMPT33BD | Complementary | net weight | 0.12 kg
RMPT33BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT33BD | Environment | standards | DIN 43760 ¦ EN/IEC 60584-1 ¦ EN/IEC 60751 ¦ EN/IEC 60947-1
RMPT33BD | Environment | product certifications | UL ¦ GL ¦ CSA
RMPT33BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT33BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT33BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT33BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT33BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT33BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMPT33BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT33BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT33BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT33BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT33BD | Offer Sustainability | Mercury free | Yes
RMPT33BD | Offer Sustainability | RoHS exemption information | Yes
RMPT33BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT33BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT33BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT33BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT33BD | Contractual warranty | Warranty | 18 months
RMPT53BD | Main | range of product | Zelio Analog
RMPT53BD | Main | product or component type | Converter for Optimum Pt100 probes
RMPT53BD | Main | analogue input type | Temperature probe 0...250 °C/32...482 °F Pt 100 2, 3 or 4 wires
RMPT53BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT53BD | Complementary | protection type | Short-circuit protection on output ¦ Reverse polarity protection on power supply ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output
RMPT53BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT53BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT53BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT53BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT53BD | Complementary | local signalling | LED (green)power ON:
RMPT53BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT53BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT53BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT53BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT53BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMPT53BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT53BD | Complementary | marking | CE
RMPT53BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT53BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT53BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT53BD | Complementary | safety reliability data | MTTFd = 43.9 years ¦ B10d = 40564
RMPT53BD | Complementary | net weight | 0.12 kg
RMPT53BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT53BD | Environment | standards | DIN 43760 ¦ EN/IEC 60751 ¦ EN/IEC 60947-1 ¦ EN/IEC 60584-1
RMPT53BD | Environment | product certifications | UL ¦ CSA ¦ GL
RMPT53BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT53BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT53BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT53BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT53BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT53BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMPT53BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT53BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT53BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT53BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMPT53BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMPT53BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT53BD | Offer Sustainability | Mercury free | Yes
RMPT53BD | Offer Sustainability | RoHS exemption information | Yes
RMPT53BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT53BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT53BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT53BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT53BD | Contractual warranty | Warranty | 18 months
RMPT73BD | Main | range of product | Zelio Analog
RMPT73BD | Main | product or component type | Converter for Optimum Pt100 probes
RMPT73BD | Main | analogue input type | Temperature probe 0...500 °C/32...932 °F Pt 100 2, 3 or 4 wires
RMPT73BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMPT73BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on power supply ¦ Short-circuit protection on output ¦ Reverse polarity protection on output
RMPT73BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMPT73BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken ¦ 22…30 mA when no input or input wire broken
RMPT73BD | Complementary | [Us] rated supply voltage | 24 V DC non isolated +/- 20 %
RMPT73BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMPT73BD | Complementary | local signalling | LED (green)power ON:
RMPT73BD | Complementary | measurement error | +/- 0.5 % of full scale (3 or 4 wires) at 20 °C ¦ +/- 1 % of full scale (2 wires) at 20 °C ¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m)
RMPT73BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMPT73BD | Complementary | temperature coefficient | 150 ppm/°C
RMPT73BD | Complementary | maximum wiring resistance | 0.2 Ohm connection in 2 wires
RMPT73BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMPT73BD | Complementary | tightening torque | 0.6…1.1 N.m
RMPT73BD | Complementary | marking | CE
RMPT73BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMPT73BD | Complementary | [Ui] rated insulation voltage | 2000 V
RMPT73BD | Complementary | fixing mode | Clip-on (35 mm symmetrical DIN rail) ¦ Fixed (mounting plate)
RMPT73BD | Complementary | safety reliability data | MTTFd = 43.9 years ¦ B10d = 40564
RMPT73BD | Complementary | net weight | 0.12 kg
RMPT73BD | Environment | electromagnetic compatibility | Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 ¦ Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2
RMPT73BD | Environment | standards | DIN 43760 ¦ EN/IEC 60584-1 ¦ EN/IEC 60947-1 ¦ EN/IEC 60751
RMPT73BD | Environment | product certifications | GL ¦ UL ¦ CSA
RMPT73BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMPT73BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMPT73BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMPT73BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMPT73BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMPT73BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMPT73BD | Environment | ambient air temperature for storage | -40…85 °C
RMPT73BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMPT73BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMPT73BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMPT73BD | Offer Sustainability | Mercury free | Yes
RMPT73BD | Offer Sustainability | RoHS exemption information | Yes
RMPT73BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMPT73BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMPT73BD | Offer Sustainability | Circularity Profile | End of Life Information
RMPT73BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMPT73BD | Contractual warranty | Warranty | 18 months
RMTJ40BD | Main | range of product | Zelio Analog
RMTJ40BD | Main | product or component type | Converter for thermocouples
RMTJ40BD | Main | analogue input type | Thermocouple 0...150 °C/32...302 °F thermocouple J conforming to IEC 60584
RMTJ40BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMTJ40BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output
RMTJ40BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMTJ40BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
RMTJ40BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMTJ40BD | Complementary | current consumption | <= 60 mA for current output
RMTJ40BD | Complementary | local signalling | LED (green)power ON:
RMTJ40BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMTJ40BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C ¦ +/- 0.8 % full scale at 60 °C
RMTJ40BD | Complementary | temperature coefficient | 200 ppm/°C
RMTJ40BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
RMTJ40BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMTJ40BD | Complementary | tightening torque | 0.6…1.1 N.m
RMTJ40BD | Complementary | marking | CE
RMTJ40BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMTJ40BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMTJ40BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMTJ40BD | Complementary | safety reliability data | B10d = 45447 ¦ MTTFd = 49.2 years
RMTJ40BD | Complementary | net weight | 0.12 kg
RMTJ40BD | Environment | standards | IEC 60947-1 ¦ IEC 60584-1
RMTJ40BD | Environment | product certifications | CSA ¦ GL ¦ UL
RMTJ40BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMTJ40BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMTJ40BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMTJ40BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMTJ40BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMTJ40BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMTJ40BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMTJ40BD | Environment | ambient air temperature for storage | -40…85 °C
RMTJ40BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMTJ40BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMTJ40BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMTJ40BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMTJ40BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMTJ40BD | Offer Sustainability | Mercury free | Yes
RMTJ40BD | Offer Sustainability | RoHS exemption information | Yes
RMTJ40BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMTJ40BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMTJ40BD | Offer Sustainability | Circularity Profile | End of Life Information
RMTJ40BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMTJ40BD | Contractual warranty | Warranty | 18 months
RMTJ60BD | Main | range of product | Zelio Analog
RMTJ60BD | Main | product or component type | Converter for thermocouples
RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output
RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMTJ60BD | Complementary | local signalling | LED (green)power ON:
RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C ¦ +/- 0.8 % full scale at 60 °C
RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C
RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m
RMTJ60BD | Complementary | marking | CE
RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMTJ60BD | Complementary | safety reliability data | B10d = 45447 ¦ MTTFd = 49.2 years
RMTJ60BD | Complementary | net weight | 0.12 kg
RMTJ60BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMTJ60BD | Environment | product certifications | CSA ¦ GL ¦ UL
RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C
RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMTJ60BD | Offer Sustainability | Mercury free | Yes
RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes
RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information
RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMTJ60BD | Contractual warranty | Warranty | 18 months
RMTJ80BD | Main | range of product | Zelio Analog
RMTJ80BD | Main | product or component type | Converter for thermocouples
RMTJ80BD | Main | analogue input type | Thermocouple 0...600 °C/32...1112 °F thermocouple J conforming to IEC 60584
RMTJ80BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMTJ80BD | Complementary | protection type | Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Short-circuit protection on output
RMTJ80BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMTJ80BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
RMTJ80BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMTJ80BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMTJ80BD | Complementary | local signalling | LED (green)power ON:
RMTJ80BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMTJ80BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C ¦ +/- 0.8 % full scale at 60 °C
RMTJ80BD | Complementary | temperature coefficient | 200 ppm/°C
RMTJ80BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
RMTJ80BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMTJ80BD | Complementary | tightening torque | 0.6…1.1 N.m
RMTJ80BD | Complementary | marking | CE
RMTJ80BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMTJ80BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMTJ80BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMTJ80BD | Complementary | safety reliability data | MTTFd = 49.2 years ¦ B10d = 45447
RMTJ80BD | Complementary | net weight | 0.12 kg
RMTJ80BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMTJ80BD | Environment | product certifications | UL ¦ GL ¦ CSA
RMTJ80BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMTJ80BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMTJ80BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMTJ80BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMTJ80BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMTJ80BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMTJ80BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMTJ80BD | Environment | ambient air temperature for storage | -40…85 °C
RMTJ80BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMTJ80BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMTJ80BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMTJ80BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMTJ80BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMTJ80BD | Offer Sustainability | Mercury free | Yes
RMTJ80BD | Offer Sustainability | RoHS exemption information | Yes
RMTJ80BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMTJ80BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMTJ80BD | Offer Sustainability | Circularity Profile | End of Life Information
RMTJ80BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMTJ80BD | Contractual warranty | Warranty | 18 months
RMTK80BD | Main | range of product | Zelio Analog
RMTK80BD | Main | product or component type | Converter for thermocouples
RMTK80BD | Main | analogue input type | Thermocouple 0...600 °C/32...1112 °F thermocouple K conforming to IEC 60584
RMTK80BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMTK80BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output
RMTK80BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMTK80BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
RMTK80BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMTK80BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMTK80BD | Complementary | local signalling | LED (green)power ON:
RMTK80BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMTK80BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C ¦ +/- 0.8 % full scale at 60 °C
RMTK80BD | Complementary | temperature coefficient | 200 ppm/°C
RMTK80BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
RMTK80BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMTK80BD | Complementary | tightening torque | 0.6…1.1 N.m
RMTK80BD | Complementary | marking | CE
RMTK80BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMTK80BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMTK80BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMTK80BD | Complementary | safety reliability data | MTTFd = 49.2 years ¦ B10d = 45447
RMTK80BD | Complementary | net weight | 0.12 kg
RMTK80BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMTK80BD | Environment | product certifications | CSA ¦ UL ¦ GL
RMTK80BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMTK80BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMTK80BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMTK80BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMTK80BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMTK80BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMTK80BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMTK80BD | Environment | ambient air temperature for storage | -40…85 °C
RMTK80BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMTK80BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMTK80BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMTK80BD | Offer Sustainability | Mercury free | Yes
RMTK80BD | Offer Sustainability | RoHS exemption information | Yes
RMTK80BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMTK80BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMTK80BD | Offer Sustainability | Circularity Profile | End of Life Information
RMTK80BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMTK80BD | Contractual warranty | Warranty | 18 months
RMTK90BD | Main | range of product | Zelio Analog
RMTK90BD | Main | product or component type | Converter for thermocouples
RMTK90BD | Main | analogue input type | Thermocouple 0...1200 °C/32...2192 °F thermocouple K conforming to IEC 60584
RMTK90BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm ¦ Current 4...20 mA <= 500 Ohm ¦ Voltage 0...10 V >= 100 kOhm
RMTK90BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output ¦ Short-circuit protection on output
RMTK90BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken ¦ 11...15 V when no input or input wire broken
RMTK90BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
RMTK90BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMTK90BD | Complementary | current consumption | <= 40 mA for voltage ¦ <= 40 mA for voltage output ¦ <= 60 mA for current
RMTK90BD | Complementary | local signalling | LED (green)power ON:
RMTK90BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMTK90BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C ¦ +/- 0.8 % full scale at 60 °C
RMTK90BD | Complementary | temperature coefficient | 200 ppm/°C
RMTK90BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
RMTK90BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMTK90BD | Complementary | tightening torque | 0.6…1.1 N.m
RMTK90BD | Complementary | marking | CE
RMTK90BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMTK90BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMTK90BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMTK90BD | Complementary | safety reliability data | MTTFd = 49.2 years ¦ B10d = 45447
RMTK90BD | Complementary | net weight | 0.12 kg
RMTK90BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMTK90BD | Environment | product certifications | GL ¦ UL ¦ CSA
RMTK90BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMTK90BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMTK90BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMTK90BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMTK90BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMTK90BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMTK90BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMTK90BD | Environment | ambient air temperature for storage | -40…85 °C
RMTK90BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMTK90BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMTK90BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMTK90BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMTK90BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMTK90BD | Offer Sustainability | Mercury free | Yes
RMTK90BD | Offer Sustainability | RoHS exemption information | Yes
RMTK90BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMTK90BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMTK90BD | Offer Sustainability | Circularity Profile | End of Life Information
RMTK90BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMTK90BD | Contractual warranty | Warranty | 18 months
RMCN22BD | Main | range of product | Zelio Analog
RMCN22BD | Main | product or component type | Voltage/current converter
RMCN22BD | Main | analogue input type | Current 4...20 mA ¦ Voltage 0...10 V DC
RMCN22BD | Main | analogue output type | Current 4...20 mA <= 500 Ohm by cabling ¦ Voltage 0...10 V >= 100 kOhm by cabling
RMCN22BD | Complementary | protection type | Short-circuit protection on output ¦ Overvoltage protection on output (+/- 30 V) ¦ Reverse polarity protection on output
RMCN22BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
RMCN22BD | Complementary | abnormal analogue output current | 4…30 mA no input or input wire broken
RMCN22BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
RMCN22BD | Complementary | current consumption | <= 40 mA for voltage output ¦ <= 60 mA for current output
RMCN22BD | Complementary | local signalling | LED (green)power ON:
RMCN22BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMCN22BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMCN22BD | Complementary | temperature coefficient | 200 ppm/°C
RMCN22BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMCN22BD | Complementary | tightening torque | 0.6…1.1 N.m
RMCN22BD | Complementary | marking | CE
RMCN22BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMCN22BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMCN22BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMCN22BD | Complementary | safety reliability data | MTTFd = 73.2 years ¦ B10d = 67582
RMCN22BD | Complementary | net weight | 0.12 kg
RMCN22BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMCN22BD | Environment | product certifications | GL ¦ CSA ¦ UL
RMCN22BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMCN22BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMCN22BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMCN22BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMCN22BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMCN22BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMCN22BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMCN22BD | Environment | ambient air temperature for storage | -40…85 °C
RMCN22BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMCN22BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMCN22BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMCN22BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMCN22BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMCN22BD | Offer Sustainability | Mercury free | Yes
RMCN22BD | Offer Sustainability | RoHS exemption information | Yes
RMCN22BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMCN22BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMCN22BD | Offer Sustainability | Circularity Profile | End of Life Information
RMCN22BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMCN22BD | Contractual warranty | Warranty | 18 months
RMCL55BD | Main | range of product | Zelio Analog
RMCL55BD | Main | product or component type | Voltage/current converter
RMCL55BD | Main | analogue input type | Current 0...20 mA ¦ Current 4...20 mA ¦ Voltage +/- 10 V DC ¦ Voltage 0...10 V DC
RMCL55BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm switchable ¦ Current 4...20 mA <= 500 Ohm switchable ¦ Voltage +/- 10 V >= 100 kOhm switchable ¦ Voltage 0...10 V >= 100 kOhm switchable
RMCL55BD | Complementary | protection type | Reverse polarity protection on output ¦ Short-circuit protection on output ¦ Overvoltage protection on output (+/- 30 V)
RMCL55BD | Complementary | abnormal analogue output voltage | 11...15 V, output selected - 10...10 V no input or input wire broken voltage ¦ 11...15 V, output selected 0...10 V no input or input wire broken voltage ¦ -15...0 V, output selected 0...20 mA no input or input wire broken current ¦ -15...0 V, output selected 4...20 mA no input or input wire broken current
RMCL55BD | Complementary | abnormal analogue output current | 22…30 mA, output selected 0...20 mA no input or input wire broken voltage ¦ 22…30 mA, output selected 4...20 mA no input or input wire broken voltage ¦ -30…0 mA, output selected 0...20 mA no input or input wire broken current ¦ 4…30 mA, output selected 4...20 mA no input or input wire broken current
RMCL55BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
RMCL55BD | Complementary | current consumption | <= 70 mA for voltage output ¦ <= 90 mA for current output
RMCL55BD | Complementary | local signalling | LED (green)power ON:
RMCL55BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 1 % of full scale at 20 °C
RMCL55BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMCL55BD | Complementary | temperature coefficient | 200 ppm/°C
RMCL55BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMCL55BD | Complementary | tightening torque | 0.6…1.1 N.m
RMCL55BD | Complementary | marking | CE
RMCL55BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMCL55BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMCL55BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMCL55BD | Complementary | safety reliability data | B10d = 20000 ¦ MTTFd = 21.6 years
RMCL55BD | Complementary | net weight | 0.12 kg
RMCL55BD | Environment | standards | IEC 60947-1 ¦ IEC 60584-1
RMCL55BD | Environment | product certifications | UL ¦ GL ¦ CSA
RMCL55BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMCL55BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMCL55BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMCL55BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMCL55BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMCL55BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMCL55BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B ¦ CISPR 11
RMCL55BD | Environment | ambient air temperature for storage | -40…85 °C
RMCL55BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMCL55BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMCL55BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMCL55BD | Offer Sustainability | Mercury free | Yes
RMCL55BD | Offer Sustainability | RoHS exemption information | Yes
RMCL55BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMCL55BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMCL55BD | Offer Sustainability | Circularity Profile | End of Life Information
RMCL55BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMCL55BD | Contractual warranty | Warranty | 18 months
RMCV60BD | Main | range of product | Zelio Analog
RMCV60BD | Main | product or component type | Voltage/current converter
RMCV60BD | Main | analogue input type | Voltage 0...300 V AC/DC 50/60 Hz ¦ Voltage 0...50 V AC/DC 50/60 Hz ¦ Voltage 0...500 V AC/DC 50/60 Hz
RMCV60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm switchable ¦ Current 4...20 mA <= 500 Ohm switchable ¦ Voltage 0...10 V >= 100 kOhm switchable
RMCV60BD | Complementary | protection type | Short-circuit protection on output ¦ Reverse polarity protection on output ¦ Overvoltage protection on output (+/- 30 V)
RMCV60BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
RMCV60BD | Complementary | abnormal analogue output current | -30…0 mA, output selected 0...20 mA no input or input wire broken ¦ 4…30 mA, output selected 4...20 mA no input or input wire broken
RMCV60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
RMCV60BD | Complementary | current consumption | <= 70 mA for voltage output ¦ <= 90 mA for current output
RMCV60BD | Complementary | local signalling | LED (green)power ON:
RMCV60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 5 % of full scale at 20 °C
RMCV60BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMCV60BD | Complementary | temperature coefficient | 200 ppm/°C
RMCV60BD | Complementary | clamping connection capacity | 1 x 2.5 mm² ¦ 2 x 1.5 mm²
RMCV60BD | Complementary | tightening torque | 0.6…1.1 N.m
RMCV60BD | Complementary | marking | CE
RMCV60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMCV60BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMCV60BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMCV60BD | Complementary | safety reliability data | MTTFd = 21.6 years ¦ B10d = 20000
RMCV60BD | Complementary | net weight | 0.15 kg
RMCV60BD | Environment | standards | IEC 60584-1 ¦ IEC 60947-1
RMCV60BD | Environment | product certifications | UL ¦ GL ¦ CSA
RMCV60BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMCV60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMCV60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMCV60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMCV60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMCV60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMCV60BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMCV60BD | Environment | ambient air temperature for storage | -40…85 °C
RMCV60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMCV60BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMCV60BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMCV60BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMCV60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMCV60BD | Offer Sustainability | Mercury free | Yes
RMCV60BD | Offer Sustainability | RoHS exemption information | Yes
RMCV60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMCV60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMCV60BD | Offer Sustainability | Circularity Profile | End of Life Information
RMCV60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RMCV60BD | Contractual warranty | Warranty | 18 months
RMCA61BD | Main | range of product | Zelio Analog
RMCA61BD | Main | product or component type | Voltage/current converter
RMCA61BD | Main | analogue input type | Current 0...1.5 A AC/DC 50/60 Hz ¦ Current 0...15 A AC/DC 50/60 Hz ¦ Current 0...5 A AC/DC 50/60 Hz
RMCA61BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm by cabling ¦ Current 4...20 mA <= 500 Ohm by cabling ¦ Voltage 0...10 V >= 100 kOhm by cabling
RMCA61BD | Complementary | protection type | Reverse polarity protection on output ¦ Short-circuit protection on output ¦ Overvoltage protection on output (+/- 30 V)
RMCA61BD | Complementary | abnormal analogue output voltage | -15...0 V no input or input wire broken
RMCA61BD | Complementary | abnormal analogue output current | -30…0 mA, output selected 0...20 mA no input or input wire broken ¦ 4…30 mA, output selected 4...20 mA no input or input wire broken
RMCA61BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, isolated
RMCA61BD | Complementary | current consumption | <= 70 mA for voltage output ¦ <= 90 mA for current output
RMCA61BD | Complementary | local signalling | LED (green)power ON:
RMCA61BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) ¦ +/- 5 % of full scale at 20 °C
RMCA61BD | Complementary | repeat accuracy | +/- 0.2 % full scale at 20 °C ¦ +/- 0.6 % full scale at 60 °C
RMCA61BD | Complementary | temperature coefficient | 1000 ppm/°C, range: 0...5 A ¦ 2000 ppm/°C, range: 0...15 A ¦ 500 ppm/°C, range: 0...1.5 A
RMCA61BD | Complementary | clamping connection capacity | 2 x 1.5 mm² ¦ 1 x 2.5 mm²
RMCA61BD | Complementary | tightening torque | 0.6…1.1 N.m
RMCA61BD | Complementary | marking | CE
RMCA61BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
RMCA61BD | Complementary | [Ui] rated insulation voltage | 2 kV
RMCA61BD | Complementary | fixing mode | By screws (mounting plate) ¦ Clip-on (35 mm symmetrical DIN rail)
RMCA61BD | Complementary | safety reliability data | B10d = 22108 ¦ MTTFd = 23.9 years
RMCA61BD | Complementary | net weight | 0.15 kg
RMCA61BD | Environment | standards | IEC 60947-1 ¦ IEC 60584-1
RMCA61BD | Environment | product certifications | CSA ¦ UL ¦ GL
RMCA61BD | Environment | IP degree of protection | IP20 (terminal block) ¦ IP50 (housing)
RMCA61BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 ¦ 850 °C conforming to UL
RMCA61BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
RMCA61BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
RMCA61BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 ¦ 8 kV (in air) conforming to IEC 61000-4-2 level 3
RMCA61BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 ¦ 2 kV (on power supply) conforming to IEC 61000-4-4
RMCA61BD | Environment | disturbance radiated/conducted | CISPR 11 ¦ CISPR 22 group 1 - class B
RMCA61BD | Environment | ambient air temperature for storage | -40…85 °C
RMCA61BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side ¦ 0…60 °C 2 cm spacing
RMCA61BD | Environment | pollution degree | 2 conforming to IEC 60664-1
RMCA61BD | Offer Sustainability | Sustainable offer status | Green Premium product
RMCA61BD | Offer Sustainability | REACh Regulation | REACh Declaration
RMCA61BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RMCA61BD | Offer Sustainability | Mercury free | Yes
RMCA61BD | Offer Sustainability | RoHS exemption information | Yes
RMCA61BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RMCA61BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RMCA61BD | Offer Sustainability | Circularity Profile | End of Life Information
RMCA61BD | Contractual warranty | Warranty | 18 months
XVR3M04S | Main | range of product | Harmony XVR
XVR3M04S | Main | product or component type | Beacon
XVR3M04S | Main | device short name | XVR3
XVR3M04S | Main | beacon or indicator bank unit type | LED unit
XVR3M04S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
XVR3M04S | Main | mounting diameter | 100 mm
XVR3M04S | Main | light source | LED, red
XVR3M04S | Main | device application | Bulldozer ¦ Automated guided vehicle (AGV) ¦ Forklift
XVR3M04S | Complementary | signalling type | Rotating ¦ Buzzer ¦ Blinking ¦ Flashing
XVR3M04S | Complementary | assembly style | Ready assembled
XVR3M04S | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3M04S | Complementary | [Us] rated supply voltage | 100...230 V AC
XVR3M04S | Complementary | [Ue] rated operational voltage | 90...253 V AC
XVR3M04S | Complementary | inrush current | 0.5 A
XVR3M04S | Complementary | power consumption in W | 3.2 W
XVR3M04S | Complementary | marking | CE
XVR3M04S | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3M04S | Complementary | electrical insulation class | Class II
XVR3M04S | Complementary | current consumption | 500 mA
XVR3M04S | Complementary | length | 100 mm
XVR3M04S | Complementary | width | 100 mm
XVR3M04S | Complementary | height | 139 mm
XVR3M04S | Complementary | net weight | 0.538 kg
XVR3M04S | Environment | product certifications | CCC
XVR3M04S | Environment | ambient air temperature for operation | -10…50 °C
XVR3M04S | Environment | ambient air temperature for storage | -20…70 °C
XVR3M04S | Environment | relative humidity | 35…85 % without condensation
XVR3M04S | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 4.6 gn (upright)
XVR3M04S | Environment | IP degree of protection | IP23 (sideways) ¦ IP23 (inverted) ¦ IP23 (upright)
XVR3M05S | Main | range of product | Harmony XVR
XVR3M05S | Main | product or component type | Beacon
XVR3M05S | Main | device short name | XVR3
XVR3M05S | Main | beacon or indicator bank unit type | LED unit
XVR3M05S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
XVR3M05S | Main | mounting diameter | 100 mm
XVR3M05S | Main | light source | LED, orange
XVR3M05S | Main | device application | Forklift ¦ Bulldozer ¦ Automated guided vehicle (AGV)
XVR3M05S | Complementary | signalling type | Rotating ¦ Blinking ¦ Flashing
XVR3M05S | Complementary | assembly style | Ready assembled
XVR3M05S | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3M05S | Complementary | [Us] rated supply voltage | 100...230 V AC
XVR3M05S | Complementary | [Ue] rated operational voltage | 90...253 V AC
XVR3M05S | Complementary | inrush current | 0.5 A
XVR3M05S | Complementary | power consumption in W | 3.2 W
XVR3M05S | Complementary | marking | CE
XVR3M05S | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3M05S | Complementary | electrical insulation class | Class II
XVR3M05S | Complementary | current consumption | 500 mA
XVR3M05S | Complementary | length | 100 mm
XVR3M05S | Complementary | width | 100 mm
XVR3M05S | Complementary | height | 139 mm
XVR3M05S | Complementary | net weight | 0.538 kg
XVR3M05S | Environment | product certifications | CCC
XVR3M05S | Environment | ambient air temperature for operation | -10…50 °C
XVR3M05S | Environment | ambient air temperature for storage | -20…70 °C
XVR3M05S | Environment | relative humidity | 35…85 % without condensation
XVR3M05S | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 4.6 gn (upright)
XVR3M05S | Environment | IP degree of protection | IP23 (sideways) ¦ IP23 (inverted) ¦ IP23 (upright)
XVR3M06S | Main | range of product | Harmony XVR
XVR3M06S | Main | product or component type | Beacon
XVR3M06S | Main | device short name | XVR3
XVR3M06S | Main | beacon or indicator bank unit type | LED unit
XVR3M06S | Main | sound signalling | Buzzer: 70…90 dB at 1 m
XVR3M06S | Main | mounting diameter | 100 mm
XVR3M06S | Main | light source | LED, blue
XVR3M06S | Main | device application | Automated guided vehicle (AGV) ¦ Forklift ¦ Bulldozer
XVR3M06S | Complementary | signalling type | Blinking ¦ Rotating ¦ Flashing
XVR3M06S | Complementary | assembly style | Ready assembled
XVR3M06S | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3M06S | Complementary | [Us] rated supply voltage | 100...230 V AC
XVR3M06S | Complementary | [Ue] rated operational voltage | 90...253 V AC
XVR3M06S | Complementary | inrush current | 0.5 A
XVR3M06S | Complementary | power consumption in W | 3.2 W
XVR3M06S | Complementary | marking | CE
XVR3M06S | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3M06S | Complementary | electrical insulation class | Class II
XVR3M06S | Complementary | current consumption | 500 mA
XVR3M06S | Complementary | length | 100 mm
XVR3M06S | Complementary | width | 100 mm
XVR3M06S | Complementary | height | 139 mm
XVR3M06S | Complementary | net weight | 0.538 kg
XVR3M06S | Environment | product certifications | CCC
XVR3M06S | Environment | ambient air temperature for operation | -10…50 °C
XVR3M06S | Environment | ambient air temperature for storage | -20…70 °C
XVR3M06S | Environment | relative humidity | 35…85 % without condensation
XVR3M06S | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 4.6 gn (upright)
XVR3M06S | Environment | IP degree of protection | IP23 (sideways) ¦ IP23 (inverted) ¦ IP23 (upright)
XVR3E03 | Main | range of product | Harmony XVR
XVR3E03 | Main | product or component type | Beacon
XVR3E03 | Main | device short name | XVR3
XVR3E03 | Main | beacon or indicator bank unit type | LED unit
XVR3E03 | Main | mounting diameter | 100 mm
XVR3E03 | Main | light source | LED, green
XVR3E03 | Main | device application | Forklift ¦ Automated guided vehicle (AGV) ¦ Bulldozer
XVR3E03 | Complementary | signalling type | Flashing ¦ Blinking ¦ Rotating
XVR3E03 | Complementary | assembly style | Ready assembled
XVR3E03 | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3E03 | Complementary | [Us] rated supply voltage | 48 V DC
XVR3E03 | Complementary | [Ue] rated operational voltage | 35...60 V DC
XVR3E03 | Complementary | inrush current | 1 A
XVR3E03 | Complementary | power consumption in W | 3 W
XVR3E03 | Complementary | marking | CE
XVR3E03 | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3E03 | Complementary | electrical insulation class | Class II
XVR3E03 | Complementary | current consumption | 1000 mA
XVR3E03 | Complementary | length | 100 mm
XVR3E03 | Complementary | width | 100 mm
XVR3E03 | Complementary | height | 139 mm
XVR3E03 | Complementary | net weight | 0.484 kg
XVR3E03 | Environment | product certifications | CCC
XVR3E03 | Environment | ambient air temperature for operation | -20…50 °C
XVR3E03 | Environment | ambient air temperature for storage | -35…70 °C
XVR3E03 | Environment | relative humidity | 35…85 % without condensation
XVR3E03 | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 7.1 gn (upright)
XVR3E03 | Environment | IP degree of protection | IP65 (upright) ¦ IP23 (sideways) ¦ IP23 (inverted)
XVR3E04 | Main | range of product | Harmony XVR
XVR3E04 | Main | product or component type | Beacon
XVR3E04 | Main | device short name | XVR3
XVR3E04 | Main | beacon or indicator bank unit type | LED unit
XVR3E04 | Main | mounting diameter | 100 mm
XVR3E04 | Main | light source | LED, red
XVR3E04 | Main | device application | Forklift ¦ Automated guided vehicle (AGV) ¦ Bulldozer
XVR3E04 | Complementary | signalling type | Rotating ¦ Blinking ¦ Flashing
XVR3E04 | Complementary | assembly style | Ready assembled
XVR3E04 | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3E04 | Complementary | [Us] rated supply voltage | 48 V DC
XVR3E04 | Complementary | [Ue] rated operational voltage | 35...60 V DC
XVR3E04 | Complementary | inrush current | 1 A
XVR3E04 | Complementary | power consumption in W | 3 W
XVR3E04 | Complementary | marking | CE
XVR3E04 | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3E04 | Complementary | electrical insulation class | Class II
XVR3E04 | Complementary | current consumption | 1000 mA
XVR3E04 | Complementary | length | 100 mm
XVR3E04 | Complementary | width | 100 mm
XVR3E04 | Complementary | height | 139 mm
XVR3E04 | Complementary | net weight | 0.484 kg
XVR3E04 | Environment | product certifications | CCC
XVR3E04 | Environment | ambient air temperature for operation | -20…50 °C
XVR3E04 | Environment | ambient air temperature for storage | -35…70 °C
XVR3E04 | Environment | relative humidity | 35…85 % without condensation
XVR3E04 | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 7.1 gn (upright)
XVR3E04 | Environment | IP degree of protection | IP65 (upright) ¦ IP23 (sideways) ¦ IP23 (inverted)
XVR3E05 | Main | range of product | Harmony XVR
XVR3E05 | Main | product or component type | Beacon
XVR3E05 | Main | device short name | XVR3
XVR3E05 | Main | beacon or indicator bank unit type | LED unit
XVR3E05 | Main | mounting diameter | 100 mm
XVR3E05 | Main | light source | LED, orange
XVR3E05 | Main | device application | Forklift ¦ Automated guided vehicle (AGV) ¦ Bulldozer
XVR3E05 | Complementary | signalling type | Flashing ¦ Blinking ¦ Rotating
XVR3E05 | Complementary | assembly style | Ready assembled
XVR3E05 | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3E05 | Complementary | [Us] rated supply voltage | 48 V DC
XVR3E05 | Complementary | [Ue] rated operational voltage | 35...60 V DC
XVR3E05 | Complementary | inrush current | 1 A
XVR3E05 | Complementary | power consumption in W | 3 W
XVR3E05 | Complementary | marking | CE
XVR3E05 | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3E05 | Complementary | electrical insulation class | Class II
XVR3E05 | Complementary | current consumption | 1000 mA
XVR3E05 | Complementary | length | 100 mm
XVR3E05 | Complementary | width | 100 mm
XVR3E05 | Complementary | height | 139 mm
XVR3E05 | Complementary | net weight | 0.484 kg
XVR3E05 | Environment | product certifications | CCC
XVR3E05 | Environment | ambient air temperature for operation | -20…50 °C
XVR3E05 | Environment | ambient air temperature for storage | -35…70 °C
XVR3E05 | Environment | relative humidity | 35…85 % without condensation
XVR3E05 | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 7.1 gn (upright)
XVR3E05 | Environment | IP degree of protection | IP65 (upright) ¦ IP23 (sideways) ¦ IP23 (inverted)
XVR3E06 | Main | range of product | Harmony XVR
XVR3E06 | Main | product or component type | Beacon
XVR3E06 | Main | device short name | XVR3
XVR3E06 | Main | beacon or indicator bank unit type | LED unit
XVR3E06 | Main | mounting diameter | 100 mm
XVR3E06 | Main | light source | LED, blue
XVR3E06 | Main | device application | Forklift ¦ Automated guided vehicle (AGV) ¦ Bulldozer
XVR3E06 | Complementary | signalling type | Rotating ¦ Flashing ¦ Blinking
XVR3E06 | Complementary | assembly style | Ready assembled
XVR3E06 | Complementary | material | PC (polycarbonate): lenses ¦ PBT (polybutylene terephthalate) + PC (polycarbonate): body ¦ EPDM (ethylene propylene diene monomer): base
XVR3E06 | Complementary | [Us] rated supply voltage | 48 V DC
XVR3E06 | Complementary | [Ue] rated operational voltage | 35...60 V DC
XVR3E06 | Complementary | inrush current | 1 A
XVR3E06 | Complementary | power consumption in W | 3 W
XVR3E06 | Complementary | marking | CE
XVR3E06 | Complementary | installation direction | Upright indoor ¦ Sideways indoor ¦ Inverted indoor ¦ Upright outdoor
XVR3E06 | Complementary | electrical insulation class | Class II
XVR3E06 | Complementary | current consumption | 1000 mA
XVR3E06 | Complementary | length | 100 mm
XVR3E06 | Complementary | width | 100 mm
XVR3E06 | Complementary | height | 139 mm
XVR3E06 | Complementary | net weight | 0.484 kg
XVR3E06 | Environment | product certifications | CCC
XVR3E06 | Environment | ambient air temperature for operation | -20…50 °C
XVR3E06 | Environment | ambient air temperature for storage | -35…70 °C
XVR3E06 | Environment | relative humidity | 35…85 % without condensation
XVR3E06 | Environment | vibration resistance | 4.6 gn (sideways) ¦ 4.6 gn (inverted) ¦ 7.1 gn (upright)
XVR3E06 | Environment | IP degree of protection | IP65 (upright) ¦ IP23 (sideways) ¦ IP23 (inverted)
XVDLS33 | Main | range of product | Harmony XVD Optimum
XVDLS33 | Main | product or component type | Complete miniature beacon
XVDLS33 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS33 | Main | signalling type | Steady
XVDLS33 | Main | mounting diameter | 45 mm
XVDLS33 | Main | component name | XVDLS
XVDLS33 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS33 | Main | light source | Bulb not included, green
XVDLS33 | Main | bulb type | Incandescent with BA 15d base
XVDLS33 | Main | [Us] rated supply voltage | <= 230 V
XVDLS33 | Main | maximum power dissipation in W | 5 W
XVDLS33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS33 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS33 | Complementary | CAD overall width | 45 mm
XVDLS33 | Complementary | CAD overall height | 104 mm
XVDLS33 | Complementary | CAD overall depth | 45 mm
XVDLS33 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS33 | Complementary | net weight | 0.08 kg
XVDLS33 | Environment | product certifications | CSA ¦ UL
XVDLS33 | Environment | standards | EN/IEC 60947-5-1
XVDLS33 | Environment | protective treatment | TC
XVDLS33 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS33 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS33 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS33 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS33 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS33 | Offer Sustainability | Mercury free | Yes
XVDLS33 | Offer Sustainability | RoHS exemption information | Yes
XVDLS33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS33 | Contractual warranty | Warranty | 18 months
XVDLS34 | Main | range of product | Harmony XVD Optimum
XVDLS34 | Main | product or component type | Complete miniature beacon
XVDLS34 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS34 | Main | signalling type | Steady
XVDLS34 | Main | mounting diameter | 45 mm
XVDLS34 | Main | component name | XVDLS
XVDLS34 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS34 | Main | light source | Bulb not included, red
XVDLS34 | Main | bulb type | Incandescent with BA 15d base
XVDLS34 | Main | [Us] rated supply voltage | <= 230 V
XVDLS34 | Main | maximum power dissipation in W | 5 W
XVDLS34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS34 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS34 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS34 | Complementary | CAD overall width | 45 mm
XVDLS34 | Complementary | CAD overall height | 104 mm
XVDLS34 | Complementary | CAD overall depth | 45 mm
XVDLS34 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS34 | Complementary | net weight | 0.08 kg
XVDLS34 | Environment | product certifications | UL ¦ CSA
XVDLS34 | Environment | standards | EN/IEC 60947-5-1
XVDLS34 | Environment | protective treatment | TC
XVDLS34 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS34 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS34 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS34 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS34 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS34 | Offer Sustainability | Mercury free | Yes
XVDLS34 | Offer Sustainability | RoHS exemption information | Yes
XVDLS34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS34 | Contractual warranty | Warranty | 18 months
XVDLS35 | Main | range of product | Harmony XVD Optimum
XVDLS35 | Main | product or component type | Complete miniature beacon
XVDLS35 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS35 | Main | signalling type | Steady
XVDLS35 | Main | mounting diameter | 45 mm
XVDLS35 | Main | component name | XVDLS
XVDLS35 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS35 | Main | light source | Bulb not included, orange
XVDLS35 | Main | bulb type | Incandescent with BA 15d base
XVDLS35 | Main | [Us] rated supply voltage | <= 230 V
XVDLS35 | Main | maximum power dissipation in W | 5 W
XVDLS35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS35 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS35 | Complementary | CAD overall width | 45 mm
XVDLS35 | Complementary | CAD overall height | 104 mm
XVDLS35 | Complementary | CAD overall depth | 45 mm
XVDLS35 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS35 | Complementary | net weight | 0.08 kg
XVDLS35 | Environment | product certifications | CSA ¦ UL
XVDLS35 | Environment | standards | EN/IEC 60947-5-1
XVDLS35 | Environment | protective treatment | TC
XVDLS35 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS35 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS35 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS35 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS35 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS35 | Offer Sustainability | Mercury free | Yes
XVDLS35 | Offer Sustainability | RoHS exemption information | Yes
XVDLS35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS35 | Contractual warranty | Warranty | 18 months
XVDLS36 | Main | range of product | Harmony XVD Optimum
XVDLS36 | Main | product or component type | Complete miniature beacon
XVDLS36 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS36 | Main | signalling type | Steady
XVDLS36 | Main | mounting diameter | 45 mm
XVDLS36 | Main | component name | XVDLS
XVDLS36 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS36 | Main | light source | Bulb not included, blue
XVDLS36 | Main | bulb type | Incandescent with BA 15d base
XVDLS36 | Main | [Us] rated supply voltage | <= 230 V
XVDLS36 | Main | maximum power dissipation in W | 5 W
XVDLS36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS36 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS36 | Complementary | CAD overall width | 45 mm
XVDLS36 | Complementary | CAD overall height | 104 mm
XVDLS36 | Complementary | CAD overall depth | 45 mm
XVDLS36 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS36 | Complementary | net weight | 0.08 kg
XVDLS36 | Environment | product certifications | UL ¦ CSA
XVDLS36 | Environment | standards | EN/IEC 60947-5-1
XVDLS36 | Environment | protective treatment | TC
XVDLS36 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS36 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS36 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS36 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS36 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS36 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS36 | Offer Sustainability | Mercury free | Yes
XVDLS36 | Offer Sustainability | RoHS exemption information | Yes
XVDLS36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS36 | Contractual warranty | Warranty | 18 months
XVDLS37 | Main | range of product | Harmony XVD Optimum
XVDLS37 | Main | product or component type | Complete miniature beacon
XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS37 | Main | signalling type | Steady
XVDLS37 | Main | mounting diameter | 45 mm
XVDLS37 | Main | component name | XVDLS
XVDLS37 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS37 | Main | light source | Bulb not included, clear
XVDLS37 | Main | bulb type | Incandescent with BA 15d base
XVDLS37 | Main | [Us] rated supply voltage | <= 230 V
XVDLS37 | Main | maximum power dissipation in W | 5 W
XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS37 | Complementary | CAD overall width | 45 mm
XVDLS37 | Complementary | CAD overall height | 104 mm
XVDLS37 | Complementary | CAD overall depth | 45 mm
XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS37 | Complementary | net weight | 0.08 kg
XVDLS37 | Environment | product certifications | CSA ¦ UL
XVDLS37 | Environment | standards | EN/IEC 60947-5-1
XVDLS37 | Environment | protective treatment | TC
XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS37 | Offer Sustainability | Mercury free | Yes
XVDLS37 | Offer Sustainability | RoHS exemption information | Yes
XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS37 | Contractual warranty | Warranty | 18 months
XVDLS38 | Main | range of product | Harmony XVD Optimum
XVDLS38 | Main | product or component type | Complete miniature beacon
XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS38 | Main | signalling type | Steady
XVDLS38 | Main | mounting diameter | 45 mm
XVDLS38 | Main | component name | XVDLS
XVDLS38 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS38 | Main | light source | Bulb not included, yellow
XVDLS38 | Main | bulb type | Incandescent with BA 15d base
XVDLS38 | Main | [Us] rated supply voltage | <= 230 V
XVDLS38 | Main | maximum power dissipation in W | 5 W
XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS38 | Complementary | CAD overall width | 45 mm
XVDLS38 | Complementary | CAD overall height | 104 mm
XVDLS38 | Complementary | CAD overall depth | 45 mm
XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS38 | Complementary | net weight | 0.08 kg
XVDLS38 | Environment | product certifications | CSA ¦ UL
XVDLS38 | Environment | standards | EN/IEC 60947-5-1
XVDLS38 | Environment | protective treatment | TC
XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS38 | Offer Sustainability | Mercury free | Yes
XVDLS38 | Offer Sustainability | RoHS exemption information | Yes
XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS38 | Contractual warranty | Warranty | 18 months
DL1BEBS | Main | range compatibility | Harmony XVP
DL1BEBS | Main | accessory / separate part designation | Incandescent bulb
DL1BEBS | Main | accessory / separate part type | Incandescent bulb
DL1BEBS | Main | accessory / separate part category | Lighting accessories
DL1BEBS | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEBS | Main | [Us] rated supply voltage | 24 V
DL1BEBS | Main | signalling type | Steady
DL1BEBS | Main | power dissipation in W | 4 W
DL1BEBS | Main | sale per indivisible quantity | 10
DL1BEBS | Complementary | bulb base | BA 15d
DL1BEBS | Complementary | net weight | 0.09 kg
DL1BEBS | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEBS | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEBS | Offer Sustainability | Mercury free | Yes
DL1BEBS | Offer Sustainability | RoHS exemption information | Yes
DL1BEBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEBS | Contractual warranty | Warranty | 18 months
XVDLS6B3 | Main | range of product | Harmony XVD Optimum
XVDLS6B3 | Main | product or component type | Complete miniature beacon
XVDLS6B3 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B3 | Main | signalling type | Flashing
XVDLS6B3 | Main | mounting diameter | 45 mm
XVDLS6B3 | Main | component name | XVDLS
XVDLS6B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B3 | Main | light source | Integral flash discharge tube, green
XVDLS6B3 | Main | bulb type | Flash discharge tube
XVDLS6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B3 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B3 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B3 | Complementary | flash energy | 1 J
XVDLS6B3 | Complementary | CAD overall width | 45 mm
XVDLS6B3 | Complementary | CAD overall height | 104 mm
XVDLS6B3 | Complementary | CAD overall depth | 45 mm
XVDLS6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6B3 | Complementary | net weight | 0.085 kg
XVDLS6B3 | Environment | product certifications | CSA ¦ UL
XVDLS6B3 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B3 | Environment | protective treatment | TC
XVDLS6B3 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B3 | Offer Sustainability | Mercury free | Yes
XVDLS6B3 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B3 | Contractual warranty | Warranty | 18 months
XVDLS6B4 | Main | range of product | Harmony XVD Optimum
XVDLS6B4 | Main | product or component type | Complete miniature beacon
XVDLS6B4 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B4 | Main | signalling type | Flashing
XVDLS6B4 | Main | mounting diameter | 45 mm
XVDLS6B4 | Main | component name | XVDLS
XVDLS6B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B4 | Main | light source | Integral flash discharge tube, red
XVDLS6B4 | Main | bulb type | Flash discharge tube
XVDLS6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B4 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B4 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B4 | Complementary | flash energy | 1 J
XVDLS6B4 | Complementary | CAD overall width | 45 mm
XVDLS6B4 | Complementary | CAD overall height | 104 mm
XVDLS6B4 | Complementary | CAD overall depth | 45 mm
XVDLS6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B4 | Complementary | net weight | 0.085 kg
XVDLS6B4 | Environment | product certifications | UL ¦ CSA
XVDLS6B4 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B4 | Environment | protective treatment | TC
XVDLS6B4 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B4 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B4 | Offer Sustainability | Mercury free | Yes
XVDLS6B4 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B4 | Contractual warranty | Warranty | 18 months
XVDLS6B5 | Main | range of product | Harmony XVD Optimum
XVDLS6B5 | Main | product or component type | Complete miniature beacon
XVDLS6B5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B5 | Main | signalling type | Flashing
XVDLS6B5 | Main | mounting diameter | 45 mm
XVDLS6B5 | Main | component name | XVDLS
XVDLS6B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B5 | Main | light source | Integral flash discharge tube, orange
XVDLS6B5 | Main | bulb type | Flash discharge tube
XVDLS6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B5 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6B5 | Complementary | flash energy | 1 J
XVDLS6B5 | Complementary | CAD overall width | 45 mm
XVDLS6B5 | Complementary | CAD overall height | 104 mm
XVDLS6B5 | Complementary | CAD overall depth | 45 mm
XVDLS6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6B5 | Complementary | net weight | 0.085 kg
XVDLS6B5 | Environment | product certifications | CSA ¦ UL
XVDLS6B5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B5 | Environment | protective treatment | TC
XVDLS6B5 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B5 | Offer Sustainability | Mercury free | Yes
XVDLS6B5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B5 | Contractual warranty | Warranty | 18 months
XVDLS6B6 | Main | range of product | Harmony XVD Optimum
XVDLS6B6 | Main | product or component type | Complete miniature beacon
XVDLS6B6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B6 | Main | signalling type | Flashing
XVDLS6B6 | Main | mounting diameter | 45 mm
XVDLS6B6 | Main | component name | XVDLS
XVDLS6B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B6 | Main | light source | Integral flash discharge tube, blue
XVDLS6B6 | Main | bulb type | Flash discharge tube
XVDLS6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B6 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B6 | Complementary | flash energy | 1 J
XVDLS6B6 | Complementary | CAD overall width | 45 mm
XVDLS6B6 | Complementary | CAD overall height | 104 mm
XVDLS6B6 | Complementary | CAD overall depth | 45 mm
XVDLS6B6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B6 | Complementary | net weight | 0.085 kg
XVDLS6B6 | Environment | product certifications | CSA ¦ UL
XVDLS6B6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B6 | Environment | protective treatment | TC
XVDLS6B6 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B6 | Offer Sustainability | Mercury free | Yes
XVDLS6B6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B6 | Contractual warranty | Warranty | 18 months
XVDLS6B7 | Main | range of product | Harmony XVD Optimum
XVDLS6B7 | Main | product or component type | Complete miniature beacon
XVDLS6B7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B7 | Main | signalling type | Flashing
XVDLS6B7 | Main | mounting diameter | 45 mm
XVDLS6B7 | Main | component name | XVDLS
XVDLS6B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B7 | Main | light source | Integral flash discharge tube, clear
XVDLS6B7 | Main | bulb type | Flash discharge tube
XVDLS6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B7 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B7 | Complementary | flash energy | 1 J
XVDLS6B7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6B7 | Complementary | CAD overall width | 45 mm
XVDLS6B7 | Complementary | CAD overall height | 104 mm
XVDLS6B7 | Complementary | CAD overall depth | 45 mm
XVDLS6B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B7 | Complementary | net weight | 0.085 kg
XVDLS6B7 | Environment | product certifications | UL ¦ CSA
XVDLS6B7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B7 | Environment | protective treatment | TC
XVDLS6B7 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B7 | Offer Sustainability | Mercury free | Yes
XVDLS6B7 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B7 | Contractual warranty | Warranty | 18 months
XVDLS6B8 | Main | range of product | Harmony XVD Optimum
XVDLS6B8 | Main | product or component type | Complete miniature beacon
XVDLS6B8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B8 | Main | signalling type | Flashing
XVDLS6B8 | Main | mounting diameter | 45 mm
XVDLS6B8 | Main | component name | XVDLS
XVDLS6B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6B8 | Main | bulb type | Flash discharge tube
XVDLS6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B8 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6B8 | Complementary | flash energy | 1 J
XVDLS6B8 | Complementary | CAD overall width | 45 mm
XVDLS6B8 | Complementary | CAD overall height | 104 mm
XVDLS6B8 | Complementary | CAD overall depth | 45 mm
XVDLS6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B8 | Complementary | net weight | 0.085 kg
XVDLS6B8 | Environment | product certifications | CSA ¦ UL
XVDLS6B8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B8 | Environment | protective treatment | TC
XVDLS6B8 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B8 | Offer Sustainability | Mercury free | Yes
XVDLS6B8 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B8 | Contractual warranty | Warranty | 18 months
XVDLS6G4 | Main | range of product | Harmony XVD Optimum
XVDLS6G4 | Main | product or component type | Complete miniature beacon
XVDLS6G4 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G4 | Main | signalling type | Flashing
XVDLS6G4 | Main | mounting diameter | 45 mm
XVDLS6G4 | Main | component name | XVDLS
XVDLS6G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G4 | Main | light source | Integral flash discharge tube, red
XVDLS6G4 | Main | bulb type | Flash discharge tube
XVDLS6G4 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G4 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G4 | Complementary | current consumption | < 35 mA AC
XVDLS6G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G4 | Complementary | flash energy | 1 J
XVDLS6G4 | Complementary | CAD overall width | 45 mm
XVDLS6G4 | Complementary | CAD overall height | 104 mm
XVDLS6G4 | Complementary | CAD overall depth | 45 mm
XVDLS6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G4 | Complementary | net weight | 0.085 kg
XVDLS6G4 | Environment | product certifications | CSA ¦ UL
XVDLS6G4 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G4 | Environment | protective treatment | TC
XVDLS6G4 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G4 | Offer Sustainability | Mercury free | Yes
XVDLS6G4 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G4 | Contractual warranty | Warranty | 18 months
XVDLS6G5 | Main | range of product | Harmony XVD Optimum
XVDLS6G5 | Main | product or component type | Complete miniature beacon
XVDLS6G5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G5 | Main | signalling type | Flashing
XVDLS6G5 | Main | mounting diameter | 45 mm
XVDLS6G5 | Main | component name | XVDLS
XVDLS6G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G5 | Main | light source | Integral flash discharge tube, orange
XVDLS6G5 | Main | bulb type | Flash discharge tube
XVDLS6G5 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G5 | Complementary | current consumption | < 35 mA AC
XVDLS6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6G5 | Complementary | flash energy | 1 J
XVDLS6G5 | Complementary | CAD overall width | 45 mm
XVDLS6G5 | Complementary | CAD overall height | 104 mm
XVDLS6G5 | Complementary | CAD overall depth | 45 mm
XVDLS6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6G5 | Complementary | net weight | 0.085 kg
XVDLS6G5 | Environment | product certifications | CSA ¦ UL
XVDLS6G5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G5 | Environment | protective treatment | TC
XVDLS6G5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G5 | Offer Sustainability | Mercury free | Yes
XVDLS6G5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G5 | Contractual warranty | Warranty | 18 months
XVDLS6G6 | Main | range of product | Harmony XVD Optimum
XVDLS6G6 | Main | product or component type | Complete miniature beacon
XVDLS6G6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G6 | Main | signalling type | Flashing
XVDLS6G6 | Main | mounting diameter | 45 mm
XVDLS6G6 | Main | component name | XVDLS
XVDLS6G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G6 | Main | light source | Integral flash discharge tube, blue
XVDLS6G6 | Main | bulb type | Flash discharge tube
XVDLS6G6 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G6 | Complementary | current consumption | < 35 mA AC
XVDLS6G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G6 | Complementary | flash energy | 1 J
XVDLS6G6 | Complementary | CAD overall width | 45 mm
XVDLS6G6 | Complementary | CAD overall height | 104 mm
XVDLS6G6 | Complementary | CAD overall depth | 45 mm
XVDLS6G6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G6 | Complementary | net weight | 0.085 kg
XVDLS6G6 | Environment | product certifications | CSA ¦ UL
XVDLS6G6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G6 | Environment | protective treatment | TC
XVDLS6G6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G6 | Offer Sustainability | Mercury free | Yes
XVDLS6G6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G6 | Contractual warranty | Warranty | 18 months
XVDLS6G7 | Main | range of product | Harmony XVD Optimum
XVDLS6G7 | Main | product or component type | Complete miniature beacon
XVDLS6G7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G7 | Main | signalling type | Flashing
XVDLS6G7 | Main | mounting diameter | 45 mm
XVDLS6G7 | Main | component name | XVDLS
XVDLS6G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G7 | Main | light source | Integral flash discharge tube, clear
XVDLS6G7 | Main | bulb type | Flash discharge tube
XVDLS6G7 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G7 | Complementary | current consumption | < 35 mA AC
XVDLS6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G7 | Complementary | flash energy | 1 J
XVDLS6G7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6G7 | Complementary | CAD overall width | 45 mm
XVDLS6G7 | Complementary | CAD overall height | 104 mm
XVDLS6G7 | Complementary | CAD overall depth | 45 mm
XVDLS6G7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6G7 | Complementary | net weight | 0.085 kg
XVDLS6G7 | Environment | product certifications | CSA ¦ UL
XVDLS6G7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G7 | Environment | protective treatment | TC
XVDLS6G7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G7 | Contractual warranty | Warranty | 18 months
XVDLS6G8 | Main | range of product | Harmony XVD Optimum
XVDLS6G8 | Main | product or component type | Complete miniature beacon
XVDLS6G8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G8 | Main | signalling type | Flashing
XVDLS6G8 | Main | mounting diameter | 45 mm
XVDLS6G8 | Main | component name | XVDLS
XVDLS6G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6G8 | Main | bulb type | Flash discharge tube
XVDLS6G8 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G8 | Complementary | current consumption | < 35 mA AC
XVDLS6G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G8 | Complementary | flash energy | 1 J
XVDLS6G8 | Complementary | CAD overall width | 45 mm
XVDLS6G8 | Complementary | CAD overall height | 104 mm
XVDLS6G8 | Complementary | CAD overall depth | 45 mm
XVDLS6G8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G8 | Complementary | net weight | 0.085 kg
XVDLS6G8 | Environment | product certifications | UL ¦ CSA
XVDLS6G8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G8 | Environment | protective treatment | TC
XVDLS6G8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G8 | Contractual warranty | Warranty | 18 months
XVDLS6M3 | Main | range of product | Harmony XVD Optimum
XVDLS6M3 | Main | product or component type | Complete miniature beacon
XVDLS6M3 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M3 | Main | signalling type | Flashing
XVDLS6M3 | Main | mounting diameter | 45 mm
XVDLS6M3 | Main | component name | XVDLS
XVDLS6M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M3 | Main | light source | Integral flash discharge tube, green
XVDLS6M3 | Main | bulb type | Flash discharge tube
XVDLS6M3 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M3 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M3 | Complementary | current consumption | < 25 mA AC
XVDLS6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M3 | Complementary | flash energy | 1 J
XVDLS6M3 | Complementary | CAD overall width | 45 mm
XVDLS6M3 | Complementary | CAD overall height | 104 mm
XVDLS6M3 | Complementary | CAD overall depth | 45 mm
XVDLS6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M3 | Complementary | net weight | 0.085 kg
XVDLS6M3 | Environment | product certifications | CSA ¦ UL
XVDLS6M3 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M3 | Environment | protective treatment | TC
XVDLS6M3 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M3 | Offer Sustainability | Mercury free | Yes
XVDLS6M3 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M3 | Contractual warranty | Warranty | 18 months
XVDLS6M5 | Main | range of product | Harmony XVD Optimum
XVDLS6M5 | Main | product or component type | Complete miniature beacon
XVDLS6M5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M5 | Main | signalling type | Flashing
XVDLS6M5 | Main | mounting diameter | 45 mm
XVDLS6M5 | Main | component name | XVDLS
XVDLS6M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M5 | Main | light source | Integral flash discharge tube, orange
XVDLS6M5 | Main | bulb type | Flash discharge tube
XVDLS6M5 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M5 | Complementary | current consumption | < 25 mA AC
XVDLS6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6M5 | Complementary | flash energy | 1 J
XVDLS6M5 | Complementary | CAD overall width | 45 mm
XVDLS6M5 | Complementary | CAD overall height | 104 mm
XVDLS6M5 | Complementary | CAD overall depth | 45 mm
XVDLS6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M5 | Complementary | net weight | 0.085 kg
XVDLS6M5 | Environment | product certifications | CSA ¦ UL
XVDLS6M5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M5 | Environment | protective treatment | TC
XVDLS6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M5 | Offer Sustainability | Mercury free | Yes
XVDLS6M5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M5 | Contractual warranty | Warranty | 18 months
XVDLS6M6 | Main | range of product | Harmony XVD Optimum
XVDLS6M6 | Main | product or component type | Complete miniature beacon
XVDLS6M6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M6 | Main | signalling type | Flashing
XVDLS6M6 | Main | mounting diameter | 45 mm
XVDLS6M6 | Main | component name | XVDLS
XVDLS6M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M6 | Main | light source | Integral flash discharge tube, blue
XVDLS6M6 | Main | bulb type | Flash discharge tube
XVDLS6M6 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M6 | Complementary | current consumption | < 25 mA AC
XVDLS6M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M6 | Complementary | flash energy | 1 J
XVDLS6M6 | Complementary | CAD overall width | 45 mm
XVDLS6M6 | Complementary | CAD overall height | 104 mm
XVDLS6M6 | Complementary | CAD overall depth | 45 mm
XVDLS6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6M6 | Complementary | net weight | 0.085 kg
XVDLS6M6 | Environment | product certifications | CSA ¦ UL
XVDLS6M6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M6 | Environment | protective treatment | TC
XVDLS6M6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M6 | Offer Sustainability | Mercury free | Yes
XVDLS6M6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M6 | Contractual warranty | Warranty | 18 months
XVDLS6M7 | Main | range of product | Harmony XVD Optimum
XVDLS6M7 | Main | product or component type | Complete miniature beacon
XVDLS6M7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M7 | Main | signalling type | Flashing
XVDLS6M7 | Main | mounting diameter | 45 mm
XVDLS6M7 | Main | component name | XVDLS
XVDLS6M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M7 | Main | light source | Integral flash discharge tube, clear
XVDLS6M7 | Main | bulb type | Flash discharge tube
XVDLS6M7 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M7 | Complementary | current consumption | < 25 mA AC
XVDLS6M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M7 | Complementary | flash energy | 1 J
XVDLS6M7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6M7 | Complementary | CAD overall width | 45 mm
XVDLS6M7 | Complementary | CAD overall height | 104 mm
XVDLS6M7 | Complementary | CAD overall depth | 45 mm
XVDLS6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M7 | Complementary | net weight | 0.085 kg
XVDLS6M7 | Environment | product certifications | UL ¦ CSA
XVDLS6M7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M7 | Environment | protective treatment | TC
XVDLS6M7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M7 | Offer Sustainability | Mercury free | Yes
XVDLS6M7 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M7 | Contractual warranty | Warranty | 18 months
XVDLS6M8 | Main | range of product | Harmony XVD Optimum
XVDLS6M8 | Main | product or component type | Complete miniature beacon
XVDLS6M8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M8 | Main | signalling type | Flashing
XVDLS6M8 | Main | mounting diameter | 45 mm
XVDLS6M8 | Main | component name | XVDLS
XVDLS6M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6M8 | Main | bulb type | Flash discharge tube
XVDLS6M8 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M8 | Complementary | current consumption | < 25 mA AC
XVDLS6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M8 | Complementary | flash energy | 1 J
XVDLS6M8 | Complementary | CAD overall width | 45 mm
XVDLS6M8 | Complementary | CAD overall height | 104 mm
XVDLS6M8 | Complementary | CAD overall depth | 45 mm
XVDLS6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M8 | Complementary | net weight | 0.085 kg
XVDLS6M8 | Environment | product certifications | CSA ¦ UL
XVDLS6M8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M8 | Environment | protective treatment | TC
XVDLS6M8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M8 | Offer Sustainability | Mercury free | Yes
XVDLS6M8 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M8 | Contractual warranty | Warranty | 18 months
XVSV7BWN | Main | range of product | Harmony XVS
XVSV7BWN | Main | product or component type | Editable electronic alarm
XVSV7BWN | Main | beacon or indicator bank unit type | Sound unit
XVSV7BWN | Main | device short name | XVSV
XVSV7BWN | Complementary | colour | White
XVSV7BWN | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV7BWN | Complementary | assembly style | Ready assembled
XVSV7BWN | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV7BWN | Complementary | net weight | 0.142 kg
XVSV7BWN | Complementary | marking | CE
XVSV7BWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV7BWN | Complementary | mounting support | 72 mm DIN rail
XVSV7BWN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVSV7BWN | Complementary | [Ue] rated operational voltage | 10...30 V DC
XVSV7BWN | Complementary | inrush current | 30 A
XVSV7BWN | Complementary | associated fuse rating | 1 A
XVSV7BWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV7BWN | Complementary | power consumption in W | 1.8 W
XVSV7BWN | Complementary | current consumption | 75 mA at 24 V DC
XVSV7BWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV7BWN | Complementary | device application | Subway ¦ Packaging ¦ Printing
XVSV7BWN | Complementary | mounting diameter | 80 mm
XVSV7BWN | Complementary | width | 80 mm
XVSV7BWN | Complementary | height | 80 mm
XVSV7BWN | Complementary | depth | 24.9 mm
XVSV7BWN | Environment | discrete output type | NPN
XVSV7BWN | Environment | signalling type | Adjustable vocal sound
XVSV7BWN | Environment | protective treatment | TC
XVSV7BWN | Environment | ambient air temperature for storage | -20…60 °C
XVSV7BWN | Environment | ambient air temperature for operation | -10…55 °C
XVSV7BWN | Environment | relative humidity | 35…85 % without condensation
XVSV7BWN | Environment | vibration resistance | 7 gn
XVSV7BWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV7BWN | Environment | noise level | 0…89 dB (stop or suppress) at 1 m
XVSV7BWN | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV7BWN | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV7BWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV7BWN | Offer Sustainability | Mercury free | Yes
XVSV7BWN | Offer Sustainability | RoHS exemption information | Yes
XVSV7BWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV7BWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV7BWN | Offer Sustainability | Circularity Profile | End of Life Information
XVSV7BBP | Main | range of product | Harmony XVS
XVSV7BBP | Main | product or component type | Editable electronic alarm
XVSV7BBP | Main | beacon or indicator bank unit type | Sound unit
XVSV7BBP | Main | device short name | XVSV
XVSV7BBP | Complementary | colour | Dark grey
XVSV7BBP | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV7BBP | Complementary | assembly style | Ready assembled
XVSV7BBP | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV7BBP | Complementary | net weight | 0.142 kg
XVSV7BBP | Complementary | marking | CE
XVSV7BBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV7BBP | Complementary | mounting support | 72 mm DIN rail
XVSV7BBP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVSV7BBP | Complementary | [Ue] rated operational voltage | 10...30 V DC
XVSV7BBP | Complementary | inrush current | 30 A
XVSV7BBP | Complementary | associated fuse rating | 1 A
XVSV7BBP | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV7BBP | Complementary | power consumption in W | 1.8 W
XVSV7BBP | Complementary | current consumption | 75 mA at 24 V DC
XVSV7BBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV7BBP | Complementary | device application | Printing ¦ Packaging ¦ Subway
XVSV7BBP | Complementary | mounting diameter | 80 mm
XVSV7BBP | Complementary | width | 80 mm
XVSV7BBP | Complementary | height | 80 mm
XVSV7BBP | Complementary | depth | 24.9 mm
XVSV7BBP | Environment | discrete output type | PNP
XVSV7BBP | Environment | signalling type | Adjustable vocal sound
XVSV7BBP | Environment | protective treatment | TC
XVSV7BBP | Environment | ambient air temperature for storage | -20…60 °C
XVSV7BBP | Environment | ambient air temperature for operation | -10…55 °C
XVSV7BBP | Environment | relative humidity | 35…85 % without condensation
XVSV7BBP | Environment | vibration resistance | 7 gn
XVSV7BBP | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV7BBP | Environment | noise level | 0…89 dB (stop or suppress) at 1 m
XVSV7BBP | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV7BBP | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV7BBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV7BBP | Offer Sustainability | Mercury free | Yes
XVSV7BBP | Offer Sustainability | RoHS exemption information | Yes
XVSV7BBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV7BBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV7BBP | Offer Sustainability | Circularity Profile | End of Life Information
XVSV9BBN | Main | range of product | Harmony XVS
XVSV9BBN | Main | product or component type | Editable electronic alarm
XVSV9BBN | Main | beacon or indicator bank unit type | Sound unit
XVSV9BBN | Main | device short name | XVSV
XVSV9BBN | Complementary | colour | Dark grey
XVSV9BBN | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV9BBN | Complementary | assembly style | Ready assembled
XVSV9BBN | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV9BBN | Complementary | net weight | 0.268 kg
XVSV9BBN | Complementary | marking | CE
XVSV9BBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV9BBN | Complementary | mounting support | 96 mm DIN rail
XVSV9BBN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVSV9BBN | Complementary | [Ue] rated operational voltage | 10...30 V DC
XVSV9BBN | Complementary | inrush current | 30 A
XVSV9BBN | Complementary | associated fuse rating | 1 A
XVSV9BBN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV9BBN | Complementary | power consumption in W | 3.8 W
XVSV9BBN | Complementary | current consumption | 160 mA at 24 V DC
XVSV9BBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV9BBN | Complementary | device application | Subway ¦ Printing ¦ Packaging
XVSV9BBN | Complementary | mounting diameter | 105 mm
XVSV9BBN | Complementary | width | 105 mm
XVSV9BBN | Complementary | height | 105 mm
XVSV9BBN | Complementary | depth | 50.1 mm
XVSV9BBN | Environment | discrete output type | NPN
XVSV9BBN | Environment | signalling type | Adjustable vocal sound
XVSV9BBN | Environment | protective treatment | TC
XVSV9BBN | Environment | ambient air temperature for storage | -20…60 °C
XVSV9BBN | Environment | ambient air temperature for operation | -10…55 °C
XVSV9BBN | Environment | relative humidity | 35…85 % without condensation
XVSV9BBN | Environment | vibration resistance | 7 gn
XVSV9BBN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV9BBN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
XVSV9BBN | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV9BBN | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV9BBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV9BBN | Offer Sustainability | Mercury free | Yes
XVSV9BBN | Offer Sustainability | RoHS exemption information | Yes
XVSV9BBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV9BBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV9BBN | Offer Sustainability | Circularity Profile | End of Life Information
XVSV9BWN | Main | range of product | Harmony XVS
XVSV9BWN | Main | product or component type | Editable electronic alarm
XVSV9BWN | Main | beacon or indicator bank unit type | Sound unit
XVSV9BWN | Main | device short name | XVSV
XVSV9BWN | Complementary | colour | White
XVSV9BWN | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV9BWN | Complementary | assembly style | Ready assembled
XVSV9BWN | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV9BWN | Complementary | net weight | 0.268 kg
XVSV9BWN | Complementary | marking | CE
XVSV9BWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV9BWN | Complementary | mounting support | 96 mm DIN rail
XVSV9BWN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVSV9BWN | Complementary | [Ue] rated operational voltage | 10...30 V DC
XVSV9BWN | Complementary | inrush current | 30 A
XVSV9BWN | Complementary | associated fuse rating | 1 A
XVSV9BWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV9BWN | Complementary | power consumption in W | 3.8 W
XVSV9BWN | Complementary | current consumption | 160 mA at 24 V DC
XVSV9BWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV9BWN | Complementary | device application | Packaging ¦ Printing ¦ Subway
XVSV9BWN | Complementary | mounting diameter | 105 mm
XVSV9BWN | Complementary | width | 105 mm
XVSV9BWN | Complementary | height | 105 mm
XVSV9BWN | Complementary | depth | 50.1 mm
XVSV9BWN | Environment | discrete output type | NPN
XVSV9BWN | Environment | signalling type | Adjustable vocal sound
XVSV9BWN | Environment | protective treatment | TC
XVSV9BWN | Environment | ambient air temperature for storage | -20…60 °C
XVSV9BWN | Environment | ambient air temperature for operation | -10…55 °C
XVSV9BWN | Environment | relative humidity | 35…85 % without condensation
XVSV9BWN | Environment | vibration resistance | 7 gn
XVSV9BWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV9BWN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
XVSV9BWN | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV9BWN | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV9BWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV9BWN | Offer Sustainability | Mercury free | Yes
XVSV9BWN | Offer Sustainability | RoHS exemption information | Yes
XVSV9BWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV9BWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV9BWN | Offer Sustainability | Circularity Profile | End of Life Information
XVSV9BBP | Main | range of product | Harmony XVS
XVSV9BBP | Main | product or component type | Editable electronic alarm
XVSV9BBP | Main | beacon or indicator bank unit type | Sound unit
XVSV9BBP | Main | device short name | XVSV
XVSV9BBP | Complementary | colour | Dark grey
XVSV9BBP | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV9BBP | Complementary | assembly style | Ready assembled
XVSV9BBP | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV9BBP | Complementary | net weight | 0.268 kg
XVSV9BBP | Complementary | marking | CE
XVSV9BBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV9BBP | Complementary | mounting support | 96 mm DIN rail
XVSV9BBP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVSV9BBP | Complementary | [Ue] rated operational voltage | 10...30 V DC
XVSV9BBP | Complementary | inrush current | 30 A
XVSV9BBP | Complementary | associated fuse rating | 1 A
XVSV9BBP | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV9BBP | Complementary | power consumption in W | 3.8 W
XVSV9BBP | Complementary | current consumption | 160 mA at 24 V DC
XVSV9BBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV9BBP | Complementary | device application | Printing ¦ Packaging ¦ Subway
XVSV9BBP | Complementary | mounting diameter | 105 mm
XVSV9BBP | Complementary | width | 105 mm
XVSV9BBP | Complementary | height | 105 mm
XVSV9BBP | Complementary | depth | 50.1 mm
XVSV9BBP | Environment | discrete output type | PNP
XVSV9BBP | Environment | signalling type | Adjustable vocal sound
XVSV9BBP | Environment | protective treatment | TC
XVSV9BBP | Environment | ambient air temperature for storage | -20…60 °C
XVSV9BBP | Environment | ambient air temperature for operation | -10…55 °C
XVSV9BBP | Environment | relative humidity | 35…85 % without condensation
XVSV9BBP | Environment | vibration resistance | 7 gn
XVSV9BBP | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV9BBP | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
XVSV9BBP | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV9BBP | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV9BBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV9BBP | Offer Sustainability | Mercury free | Yes
XVSV9BBP | Offer Sustainability | RoHS exemption information | Yes
XVSV9BBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV9BBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV9BBP | Offer Sustainability | Circularity Profile | End of Life Information
XVSV9MBN | Main | range of product | Harmony XVS
XVSV9MBN | Main | product or component type | Editable electronic alarm
XVSV9MBN | Main | beacon or indicator bank unit type | Sound unit
XVSV9MBN | Main | device short name | XVSV
XVSV9MBN | Complementary | colour | Dark grey
XVSV9MBN | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV9MBN | Complementary | assembly style | Ready assembled
XVSV9MBN | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV9MBN | Complementary | net weight | 0.287 kg
XVSV9MBN | Complementary | marking | CE
XVSV9MBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV9MBN | Complementary | mounting support | 96 mm DIN rail
XVSV9MBN | Complementary | [Us] rated supply voltage | 100...230 V AC
XVSV9MBN | Complementary | [Ue] rated operational voltage | 90...264 V AC
XVSV9MBN | Complementary | inrush current | 30 A
XVSV9MBN | Complementary | associated fuse rating | 1 A
XVSV9MBN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV9MBN | Complementary | power consumption in W | 10 W
XVSV9MBN | Complementary | current consumption | 100 mA at 100 V AC
XVSV9MBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV9MBN | Complementary | device application | Subway ¦ Packaging ¦ Printing
XVSV9MBN | Complementary | mounting diameter | 105 mm
XVSV9MBN | Complementary | width | 105 mm
XVSV9MBN | Complementary | height | 105 mm
XVSV9MBN | Complementary | depth | 50.1 mm
XVSV9MBN | Environment | discrete output type | NPN
XVSV9MBN | Environment | signalling type | Adjustable vocal sound
XVSV9MBN | Environment | protective treatment | TC
XVSV9MBN | Environment | ambient air temperature for storage | -20…60 °C
XVSV9MBN | Environment | ambient air temperature for operation | 0…50 °C
XVSV9MBN | Environment | relative humidity | 35…85 % without condensation
XVSV9MBN | Environment | vibration resistance | 7 gn
XVSV9MBN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV9MBN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
XVSV9MBN | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV9MBN | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV9MBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV9MBN | Offer Sustainability | Mercury free | Yes
XVSV9MBN | Offer Sustainability | RoHS exemption information | Yes
XVSV9MBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV9MBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV9MBN | Offer Sustainability | Circularity Profile | End of Life Information
XVSV9MWN | Main | range of product | Harmony XVS
XVSV9MWN | Main | product or component type | Editable electronic alarm
XVSV9MWN | Main | beacon or indicator bank unit type | Sound unit
XVSV9MWN | Main | device short name | XVSV
XVSV9MWN | Complementary | colour | White
XVSV9MWN | Complementary | input type | Bit: 6 channel input ¦ Binary: 63 channel input
XVSV9MWN | Complementary | assembly style | Ready assembled
XVSV9MWN | Complementary | material | PC (polycarbonate): body ¦ PC (polycarbonate): back cover ¦ TPE (thermoplastic elastomer): front panel ¦ NBR (nitrile butadiene rubber)
XVSV9MWN | Complementary | net weight | 0.287 kg
XVSV9MWN | Complementary | marking | CE
XVSV9MWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVSV9MWN | Complementary | mounting support | 96 mm DIN rail
XVSV9MWN | Complementary | [Us] rated supply voltage | 100...230 V AC
XVSV9MWN | Complementary | [Ue] rated operational voltage | 90...264 V AC
XVSV9MWN | Complementary | inrush current | 30 A
XVSV9MWN | Complementary | associated fuse rating | 1 A
XVSV9MWN | Complementary | [Uimp] rated impulse withstand voltage | 1 kV
XVSV9MWN | Complementary | power consumption in W | 10 W
XVSV9MWN | Complementary | current consumption | 100 mA at 100 V AC
XVSV9MWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVSV9MWN | Complementary | device application | Packaging ¦ Subway ¦ Printing
XVSV9MWN | Complementary | mounting diameter | 105 mm
XVSV9MWN | Complementary | width | 105 mm
XVSV9MWN | Complementary | height | 105 mm
XVSV9MWN | Complementary | depth | 50.1 mm
XVSV9MWN | Environment | discrete output type | NPN
XVSV9MWN | Environment | signalling type | Adjustable vocal sound
XVSV9MWN | Environment | protective treatment | TC
XVSV9MWN | Environment | ambient air temperature for storage | -20…60 °C
XVSV9MWN | Environment | ambient air temperature for operation | 0…50 °C
XVSV9MWN | Environment | relative humidity | 35…85 % without condensation
XVSV9MWN | Environment | vibration resistance | 7 gn
XVSV9MWN | Environment | IP degree of protection | Panel mounted: IP65 conforming to EN/IEC 60529 ¦ Wall mounted: IP20
XVSV9MWN | Environment | noise level | 0…97 dB (stop or suppress) at 1 m
XVSV9MWN | Offer Sustainability | Sustainable offer status | Green Premium product
XVSV9MWN | Offer Sustainability | REACh Regulation | REACh Declaration
XVSV9MWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVSV9MWN | Offer Sustainability | Mercury free | Yes
XVSV9MWN | Offer Sustainability | RoHS exemption information | Yes
XVSV9MWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVSV9MWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVSV9MWN | Offer Sustainability | Circularity Profile | End of Life Information
XVS10BMW | Main | range of product | Harmony XVS
XVS10BMW | Main | product or component type | Siren
XVS10BMW | Main | device short name | XVS
XVS10BMW | Main | colour | White
XVS10BMW | Main | signalling type | 2 tones siren
XVS10BMW | Main | [Us] rated supply voltage | 12 V AC/DC ¦ 24 V AC/DC
XVS10BMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
XVS10BMW | Complementary | material | PC: body
XVS10BMW | Complementary | net weight | 0.8 kg
XVS10BMW | Complementary | marking | CE
XVS10BMW | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS10BMW | Complementary | current consumption | 300 mA at 24 V ¦ 500 mA
XVS10BMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS10BMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
XVS10BMW | Complementary | width | 114 mm
XVS10BMW | Complementary | height | 114 mm
XVS10BMW | Complementary | depth | 153.2 mm
XVS10BMW | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVS10BMW | Environment | protective treatment | TC
XVS10BMW | Environment | ambient air temperature for storage | -35…70 °C
XVS10BMW | Environment | ambient air temperature for operation | -30…50 °C
XVS10BMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
XVS10BMW | Environment | IP degree of protection | IP53
XVS10BMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS10BMW | Offer Sustainability | Mercury free | Yes
XVS10BMW | Offer Sustainability | RoHS exemption information | Yes
XVS10BMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS10BMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS10BMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS10BMW | Contractual warranty | Warranty | 18 months
XVS10GMW | Main | range of product | Harmony XVS
XVS10GMW | Main | product or component type | Siren
XVS10GMW | Main | device short name | XVS
XVS10GMW | Main | colour | White
XVS10GMW | Main | signalling type | 2 tones siren
XVS10GMW | Main | [Us] rated supply voltage | 120 V AC
XVS10GMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
XVS10GMW | Complementary | material | PC: body
XVS10GMW | Complementary | net weight | 1 kg
XVS10GMW | Complementary | marking | CE
XVS10GMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
XVS10GMW | Complementary | current consumption | 80 mA at 120 V
XVS10GMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS10GMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
XVS10GMW | Complementary | width | 114 mm
XVS10GMW | Complementary | height | 114 mm
XVS10GMW | Complementary | depth | 153.2 mm
XVS10GMW | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVS10GMW | Environment | protective treatment | TC
XVS10GMW | Environment | ambient air temperature for storage | -35…70 °C
XVS10GMW | Environment | ambient air temperature for operation | -30…50 °C
XVS10GMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
XVS10GMW | Environment | IP degree of protection | IP53
XVS10GMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS10GMW | Offer Sustainability | Mercury free | Yes
XVS10GMW | Offer Sustainability | RoHS exemption information | Yes
XVS10GMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS10GMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS10GMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS10GMW | Contractual warranty | Warranty | 18 months
XVS10MMW | Main | range of product | Harmony XVS
XVS10MMW | Main | product or component type | Siren
XVS10MMW | Main | device short name | XVS
XVS10MMW | Main | colour | White
XVS10MMW | Main | signalling type | 2 tones siren
XVS10MMW | Main | [Us] rated supply voltage | 230 V AC
XVS10MMW | Main | noise level | 106 dB (continuous or intermittent tone) at 1 m
XVS10MMW | Complementary | material | PC: body
XVS10MMW | Complementary | net weight | 1 kg
XVS10MMW | Complementary | marking | CE
XVS10MMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
XVS10MMW | Complementary | current consumption | 40 mA at 230 V
XVS10MMW | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS10MMW | Complementary | electrical connection | Cable: 6.5…8.5 mm
XVS10MMW | Complementary | width | 114 mm
XVS10MMW | Complementary | height | 114 mm
XVS10MMW | Complementary | depth | 153.2 mm
XVS10MMW | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVS10MMW | Environment | protective treatment | TC
XVS10MMW | Environment | ambient air temperature for storage | -35…70 °C
XVS10MMW | Environment | ambient air temperature for operation | -30…50 °C
XVS10MMW | Environment | electrical shock protection class | Class II conforming to EN/IEC 61140
XVS10MMW | Environment | IP degree of protection | IP53
XVS10MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS10MMW | Offer Sustainability | Mercury free | Yes
XVS10MMW | Offer Sustainability | RoHS exemption information | Yes
XVS10MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS10MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS10MMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS10MMW | Contractual warranty | Warranty | 18 months
XVS14BMW | Main | range of product | Harmony XVS
XVS14BMW | Main | product or component type | Multisound siren
XVS14BMW | Main | device short name | XVS
XVS14BMW | Complementary | colour | White
XVS14BMW | Complementary | material | ASA (Acrylonitrile Styrene Acrylate): front ¦ ASA (Acrylonitrile Styrene Acrylate): back ¦ PC (polycarbonate): back cover
XVS14BMW | Complementary | net weight | 1 kg
XVS14BMW | Complementary | marking | CE
XVS14BMW | Complementary | mounting support | Bracket
XVS14BMW | Complementary | fixing mode | 3 holes Ø 9 mm
XVS14BMW | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS14BMW | Complementary | current consumption | 350 mA at 24 V ¦ 250 mA at 12 V
XVS14BMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) ¦ Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
XVS14BMW | Complementary | width | 140 mm
XVS14BMW | Complementary | height | 114 mm
XVS14BMW | Complementary | depth | 223 mm
XVS14BMW | Environment | signalling type | 43 tones siren
XVS14BMW | Environment | standards | EN 61000-6-2 ¦ EN 55014-2 ¦ EN 55022 ¦ EN 61000-6-3
XVS14BMW | Environment | product certifications | UL
XVS14BMW | Environment | protective treatment | TC
XVS14BMW | Environment | ambient air temperature for storage | -35…70 °C
XVS14BMW | Environment | ambient air temperature for operation | -10…50 °C
XVS14BMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
XVS14BMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
XVS14BMW | Environment | [Us] rated supply voltage | 12 V DC ¦ 24 V DC
XVS14BMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
XVS14BMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS14BMW | Offer Sustainability | Mercury free | Yes
XVS14BMW | Offer Sustainability | RoHS exemption information | Yes
XVS14BMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS14BMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS14BMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS14BMW | Contractual warranty | Warranty | 18 months
XVS14GMW | Main | range of product | Harmony XVS
XVS14GMW | Main | product or component type | Multisound siren
XVS14GMW | Main | device short name | XVS
XVS14GMW | Complementary | colour | White
XVS14GMW | Complementary | material | PC (polycarbonate): back cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back
XVS14GMW | Complementary | net weight | 1.2 kg
XVS14GMW | Complementary | marking | CE
XVS14GMW | Complementary | mounting support | Bracket
XVS14GMW | Complementary | fixing mode | 3 holes Ø 9 mm
XVS14GMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
XVS14GMW | Complementary | current consumption | 100 mA at 120 V
XVS14GMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) ¦ Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
XVS14GMW | Complementary | width | 140 mm
XVS14GMW | Complementary | height | 114 mm
XVS14GMW | Complementary | depth | 223 mm
XVS14GMW | Environment | signalling type | 43 tones siren
XVS14GMW | Environment | standards | EN 61000-6-2 ¦ EN 61000-6-3 ¦ EN 60947 ¦ EN 60947-5
XVS14GMW | Environment | product certifications | UL
XVS14GMW | Environment | protective treatment | TC
XVS14GMW | Environment | ambient air temperature for storage | -35…70 °C
XVS14GMW | Environment | ambient air temperature for operation | -10…50 °C
XVS14GMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
XVS14GMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
XVS14GMW | Environment | [Us] rated supply voltage | 120 V AC
XVS14GMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
XVS14GMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS14GMW | Offer Sustainability | Mercury free | Yes
XVS14GMW | Offer Sustainability | RoHS exemption information | Yes
XVS14GMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS14GMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS14GMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS14GMW | Contractual warranty | Warranty | 18 months
XVS14MMW | Main | range of product | Harmony XVS
XVS14MMW | Main | product or component type | Multisound siren
XVS14MMW | Main | device short name | XVS
XVS14MMW | Complementary | colour | White
XVS14MMW | Complementary | material | PC (polycarbonate): back cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): front ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): back
XVS14MMW | Complementary | net weight | 1.2 kg
XVS14MMW | Complementary | marking | CE
XVS14MMW | Complementary | mounting support | Bracket
XVS14MMW | Complementary | fixing mode | 3 holes Ø 9 mm
XVS14MMW | Complementary | [Uimp] rated impulse withstand voltage | 4 kV
XVS14MMW | Complementary | current consumption | 50 mA at 240 V
XVS14MMW | Complementary | electrical connection | Cable: 6.5…8.5 mm, 0.33 mm² / AWG 22 (signalling circuit) ¦ Cable: 6.5…8.5 mm, 0.52 mm² / AWG 20 (power circuit)
XVS14MMW | Complementary | width | 140 mm
XVS14MMW | Complementary | height | 114 mm
XVS14MMW | Complementary | depth | 223 mm
XVS14MMW | Environment | signalling type | 43 tones siren
XVS14MMW | Environment | standards | EN 61000-6-3 ¦ EN 60947-5-1 ¦ EN 60947-01 ¦ EN 61000-6-2
XVS14MMW | Environment | product certifications | UL
XVS14MMW | Environment | protective treatment | TC
XVS14MMW | Environment | ambient air temperature for storage | -35…70 °C
XVS14MMW | Environment | ambient air temperature for operation | -10…50 °C
XVS14MMW | Environment | overvoltage category | Class II conforming to EN/IEC 61140
XVS14MMW | Environment | IP degree of protection | IP53 conforming to EN/IEC 60529
XVS14MMW | Environment | [Us] rated supply voltage | 240 V AC
XVS14MMW | Environment | noise level | 0…105 dB (continuous or intermittent tone) at 1 m
XVS14MMW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS14MMW | Offer Sustainability | Mercury free | Yes
XVS14MMW | Offer Sustainability | RoHS exemption information | Yes
XVS14MMW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS14MMW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS14MMW | Offer Sustainability | Circularity Profile | End of Life Information
XVS14MMW | Contractual warranty | Warranty | 18 months
XVS72BMBP | Main | range of product | Harmony XVS
XVS72BMBP | Main | product or component type | Electronic alarm
XVS72BMBP | Main | device short name | XVS
XVS72BMBP | Complementary | colour | Black
XVS72BMBP | Complementary | material | ABS (acrylonitrile butadiene-styrene): body ¦ PC (polycarbonate): terminal cover
XVS72BMBP | Complementary | net weight | 0.18 kg
XVS72BMBP | Complementary | marking | CE
XVS72BMBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS72BMBP | Complementary | mounting support | 72 mm DIN rail
XVS72BMBP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS72BMBP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS72BMBP | Complementary | current consumption | 117 mA at 12 V ¦ 125 mA at 24 V ¦ 158 mA at 12 V ¦ 200 mA at 24 V
XVS72BMBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS72BMBP | Complementary | width | 72 mm
XVS72BMBP | Complementary | height | 72 mm
XVS72BMBP | Complementary | depth | 69.3 mm
XVS72BMBP | Environment | discrete output type | PNP
XVS72BMBP | Environment | signalling type | 16 tones alarm
XVS72BMBP | Environment | standards | UL 464 ¦ EN/IEC 61000-6-3 ¦ EN/IEC 61000-6-2
XVS72BMBP | Environment | product certifications | UR
XVS72BMBP | Environment | protective treatment | TC
XVS72BMBP | Environment | ambient air temperature for storage | -35…70 °C
XVS72BMBP | Environment | ambient air temperature for operation | -10…50 °C
XVS72BMBP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS72BMBP | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
XVS72BMBP | Offer Sustainability | Sustainable offer status | Green Premium product
XVS72BMBP | Offer Sustainability | REACh Regulation | REACh Declaration
XVS72BMBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS72BMBP | Offer Sustainability | Mercury free | Yes
XVS72BMBP | Offer Sustainability | RoHS exemption information | Yes
XVS72BMBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS72BMBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS72BMBP | Offer Sustainability | Circularity Profile | End of Life Information
XVS72BMBP | Contractual warranty | Warranty | 18 months
XVS72BMWP | Main | range of product | Harmony XVS
XVS72BMWP | Main | product or component type | Electronic alarm
XVS72BMWP | Main | device short name | XVS
XVS72BMWP | Complementary | colour | White
XVS72BMWP | Complementary | material | ABS (acrylonitrile butadiene-styrene): body ¦ PC (polycarbonate): terminal cover
XVS72BMWP | Complementary | net weight | 0.18 kg
XVS72BMWP | Complementary | marking | CE
XVS72BMWP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS72BMWP | Complementary | mounting support | 72 mm DIN rail
XVS72BMWP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS72BMWP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS72BMWP | Complementary | current consumption | 117 mA at 12 V ¦ 125 mA at 24 V ¦ 158 mA at 12 V ¦ 200 mA at 24 V
XVS72BMWP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS72BMWP | Complementary | width | 72 mm
XVS72BMWP | Complementary | height | 72 mm
XVS72BMWP | Complementary | depth | 69.3 mm
XVS72BMWP | Environment | discrete output type | PNP
XVS72BMWP | Environment | signalling type | 16 tones alarm
XVS72BMWP | Environment | standards | EN/IEC 61000-6-3 ¦ EN/IEC 61000-6-2 ¦ UL 464
XVS72BMWP | Environment | product certifications | UR
XVS72BMWP | Environment | protective treatment | TC
XVS72BMWP | Environment | ambient air temperature for storage | -35…70 °C
XVS72BMWP | Environment | ambient air temperature for operation | -10…50 °C
XVS72BMWP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS72BMWP | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
XVS72BMWP | Offer Sustainability | Sustainable offer status | Green Premium product
XVS72BMWP | Offer Sustainability | REACh Regulation | REACh Declaration
XVS72BMWP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS72BMWP | Offer Sustainability | Mercury free | Yes
XVS72BMWP | Offer Sustainability | RoHS exemption information | Yes
XVS72BMWP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS72BMWP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS72BMWP | Offer Sustainability | Circularity Profile | End of Life Information
XVS72BMWP | Contractual warranty | Warranty | 18 months
XVS72BMBN | Main | range of product | Harmony XVS
XVS72BMBN | Main | product or component type | Electronic alarm
XVS72BMBN | Main | device short name | XVS
XVS72BMBN | Complementary | colour | Black
XVS72BMBN | Complementary | material | ABS (acrylonitrile butadiene-styrene): body ¦ PC (polycarbonate): terminal cover
XVS72BMBN | Complementary | net weight | 0.18 kg
XVS72BMBN | Complementary | marking | CE
XVS72BMBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS72BMBN | Complementary | mounting support | 72 mm DIN rail
XVS72BMBN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS72BMBN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS72BMBN | Complementary | current consumption | 117 mA at 12 V ¦ 125 mA at 24 V ¦ 158 mA at 12 V ¦ 200 mA at 24 V
XVS72BMBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS72BMBN | Complementary | width | 72 mm
XVS72BMBN | Complementary | height | 72 mm
XVS72BMBN | Complementary | depth | 69.3 mm
XVS72BMBN | Environment | discrete output type | NPN
XVS72BMBN | Environment | signalling type | 16 tones alarm
XVS72BMBN | Environment | standards | UL 464 ¦ EN/IEC 61000-6-3 ¦ EN/IEC 61000-6-2
XVS72BMBN | Environment | product certifications | UR
XVS72BMBN | Environment | protective treatment | TC
XVS72BMBN | Environment | ambient air temperature for storage | -35…70 °C
XVS72BMBN | Environment | ambient air temperature for operation | -10…50 °C
XVS72BMBN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS72BMBN | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
XVS72BMBN | Offer Sustainability | Sustainable offer status | Green Premium product
XVS72BMBN | Offer Sustainability | REACh Regulation | REACh Declaration
XVS72BMBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS72BMBN | Offer Sustainability | Mercury free | Yes
XVS72BMBN | Offer Sustainability | RoHS exemption information | Yes
XVS72BMBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS72BMBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS72BMBN | Offer Sustainability | Circularity Profile | End of Life Information
XVS72BMBN | Contractual warranty | Warranty | 18 months
XVS72BMWN | Main | range of product | Harmony XVS
XVS72BMWN | Main | product or component type | Electronic alarm
XVS72BMWN | Main | device short name | XVS
XVS72BMWN | Complementary | colour | White
XVS72BMWN | Complementary | material | ABS (acrylonitrile butadiene-styrene): body ¦ PC (polycarbonate): terminal cover
XVS72BMWN | Complementary | net weight | 0.18 kg
XVS72BMWN | Complementary | marking | CE
XVS72BMWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS72BMWN | Complementary | mounting support | 72 mm DIN rail
XVS72BMWN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS72BMWN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS72BMWN | Complementary | current consumption | 117 mA at 12 V ¦ 125 mA at 24 V ¦ 158 mA at 12 V ¦ 200 mA at 24 V
XVS72BMWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS72BMWN | Complementary | width | 72 mm
XVS72BMWN | Complementary | height | 72 mm
XVS72BMWN | Complementary | depth | 69.3 mm
XVS72BMWN | Environment | discrete output type | NPN
XVS72BMWN | Environment | signalling type | 16 tones alarm
XVS72BMWN | Environment | standards | EN/IEC 61000-6-2 ¦ UL 464 ¦ EN/IEC 61000-6-3
XVS72BMWN | Environment | product certifications | UR
XVS72BMWN | Environment | protective treatment | TC
XVS72BMWN | Environment | ambient air temperature for storage | -35…70 °C
XVS72BMWN | Environment | ambient air temperature for operation | -10…50 °C
XVS72BMWN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS72BMWN | Environment | noise level | 0…90 dB (continuous or intermittent tone) at 1 m
XVS72BMWN | Offer Sustainability | Sustainable offer status | Green Premium product
XVS72BMWN | Offer Sustainability | REACh Regulation | REACh Declaration
XVS72BMWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS72BMWN | Offer Sustainability | Mercury free | Yes
XVS72BMWN | Offer Sustainability | RoHS exemption information | Yes
XVS72BMWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS72BMWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS72BMWN | Offer Sustainability | Circularity Profile | End of Life Information
XVS72BMWN | Contractual warranty | Warranty | 18 months
XVS96BMBP | Main | range of product | Harmony XVS
XVS96BMBP | Main | product or component type | Electronic alarm
XVS96BMBP | Main | device short name | XVS
XVS96BMBP | Complementary | colour | Black
XVS96BMBP | Complementary | material | PC (polycarbonate): terminal cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
XVS96BMBP | Complementary | net weight | 0.4 kg
XVS96BMBP | Complementary | marking | CE
XVS96BMBP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS96BMBP | Complementary | mounting support | 96 mm DIN rail
XVS96BMBP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS96BMBP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS96BMBP | Complementary | current consumption | 250 mA at 12 V ¦ 292 mA at 12 V ¦ 292 mA at 24 V ¦ 354 mA at 24 V
XVS96BMBP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS96BMBP | Complementary | width | 96 mm
XVS96BMBP | Complementary | height | 96 mm
XVS96BMBP | Complementary | depth | 58.1 mm
XVS96BMBP | Environment | discrete output type | PNP
XVS96BMBP | Environment | signalling type | 16 tones alarm
XVS96BMBP | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVS96BMBP | Environment | protective treatment | TC
XVS96BMBP | Environment | ambient air temperature for storage | -35…70 °C
XVS96BMBP | Environment | ambient air temperature for operation | -20…50 °C
XVS96BMBP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS96BMBP | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
XVS96BMBP | Offer Sustainability | Sustainable offer status | Green Premium product
XVS96BMBP | Offer Sustainability | REACh Regulation | REACh Declaration
XVS96BMBP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS96BMBP | Offer Sustainability | Mercury free | Yes
XVS96BMBP | Offer Sustainability | RoHS exemption information | Yes
XVS96BMBP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS96BMBP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS96BMBP | Offer Sustainability | Circularity Profile | End of Life Information
XVS96BMBP | Contractual warranty | Warranty | 18 months
XVS96BMWP | Main | range of product | Harmony XVS
XVS96BMWP | Main | product or component type | Electronic alarm
XVS96BMWP | Main | device short name | XVS
XVS96BMWP | Complementary | colour | White
XVS96BMWP | Complementary | material | PC (polycarbonate): terminal cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
XVS96BMWP | Complementary | net weight | 0.4 kg
XVS96BMWP | Complementary | marking | CE
XVS96BMWP | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS96BMWP | Complementary | mounting support | 96 mm DIN rail
XVS96BMWP | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS96BMWP | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS96BMWP | Complementary | current consumption | 250 mA at 12 V ¦ 292 mA at 12 V ¦ 292 mA at 24 V ¦ 354 mA at 24 V
XVS96BMWP | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS96BMWP | Complementary | width | 96 mm
XVS96BMWP | Complementary | height | 96 mm
XVS96BMWP | Complementary | depth | 58.1 mm
XVS96BMWP | Environment | discrete output type | PNP
XVS96BMWP | Environment | signalling type | 16 tones alarm
XVS96BMWP | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVS96BMWP | Environment | protective treatment | TC
XVS96BMWP | Environment | ambient air temperature for storage | -35…70 °C
XVS96BMWP | Environment | ambient air temperature for operation | -20…50 °C
XVS96BMWP | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS96BMWP | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
XVS96BMWP | Offer Sustainability | Sustainable offer status | Green Premium product
XVS96BMWP | Offer Sustainability | REACh Regulation | REACh Declaration
XVS96BMWP | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS96BMWP | Offer Sustainability | Mercury free | Yes
XVS96BMWP | Offer Sustainability | RoHS exemption information | Yes
XVS96BMWP | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS96BMWP | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS96BMWP | Offer Sustainability | Circularity Profile | End of Life Information
XVS96BMWP | Contractual warranty | Warranty | 18 months
XVS96BMBN | Main | range of product | Harmony XVS
XVS96BMBN | Main | product or component type | Electronic alarm
XVS96BMBN | Main | device short name | XVS
XVS96BMBN | Complementary | colour | Black
XVS96BMBN | Complementary | material | PC (polycarbonate): terminal cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
XVS96BMBN | Complementary | net weight | 0.4 kg
XVS96BMBN | Complementary | marking | CE
XVS96BMBN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS96BMBN | Complementary | mounting support | 96 mm DIN rail
XVS96BMBN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS96BMBN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS96BMBN | Complementary | current consumption | 250 mA at 12 V ¦ 292 mA at 12 V ¦ 292 mA at 24 V ¦ 354 mA at 24 V
XVS96BMBN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS96BMBN | Complementary | width | 96 mm
XVS96BMBN | Complementary | height | 96 mm
XVS96BMBN | Complementary | depth | 58.1 mm
XVS96BMBN | Environment | discrete output type | NPN
XVS96BMBN | Environment | signalling type | 16 tones alarm
XVS96BMBN | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVS96BMBN | Environment | protective treatment | TC
XVS96BMBN | Environment | ambient air temperature for storage | -35…70 °C
XVS96BMBN | Environment | ambient air temperature for operation | -20…50 °C
XVS96BMBN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS96BMBN | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
XVS96BMBN | Offer Sustainability | Sustainable offer status | Green Premium product
XVS96BMBN | Offer Sustainability | REACh Regulation | REACh Declaration
XVS96BMBN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS96BMBN | Offer Sustainability | Mercury free | Yes
XVS96BMBN | Offer Sustainability | RoHS exemption information | Yes
XVS96BMBN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS96BMBN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS96BMBN | Offer Sustainability | Circularity Profile | End of Life Information
XVS96BMBN | Contractual warranty | Warranty | 18 months
XVS96BMWN | Main | range of product | Harmony XVS
XVS96BMWN | Main | product or component type | Electronic alarm
XVS96BMWN | Main | device short name | XVS
XVS96BMWN | Complementary | colour | White
XVS96BMWN | Complementary | material | PC (polycarbonate): terminal cover ¦ PC (polycarbonate)/ABS (acrylonitrile butadiene-styrene): body
XVS96BMWN | Complementary | net weight | 0.4 kg
XVS96BMWN | Complementary | marking | CE
XVS96BMWN | Complementary | overvoltage category | Class II conforming to EN/IEC 61140
XVS96BMWN | Complementary | mounting support | 96 mm DIN rail
XVS96BMWN | Complementary | [Us] rated supply voltage | 12...24 V DC
XVS96BMWN | Complementary | [Uimp] rated impulse withstand voltage | 0.8 kV
XVS96BMWN | Complementary | current consumption | 250 mA at 12 V ¦ 292 mA at 12 V ¦ 292 mA at 24 V ¦ 354 mA at 24 V
XVS96BMWN | Complementary | clamping connection capacity | <= 1 x 1.5 mm²
XVS96BMWN | Complementary | width | 96 mm
XVS96BMWN | Complementary | height | 96 mm
XVS96BMWN | Complementary | depth | 58.1 mm
XVS96BMWN | Environment | discrete output type | NPN
XVS96BMWN | Environment | signalling type | 16 tones alarm
XVS96BMWN | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVS96BMWN | Environment | protective treatment | TC
XVS96BMWN | Environment | ambient air temperature for storage | -35…70 °C
XVS96BMWN | Environment | ambient air temperature for operation | -20…50 °C
XVS96BMWN | Environment | IP degree of protection | Panel mounted: IP54 conforming to EN/IEC 60529
XVS96BMWN | Environment | noise level | 0…96 dB (continuous or intermittent tone) at 1 m
XVS96BMWN | Offer Sustainability | Sustainable offer status | Green Premium product
XVS96BMWN | Offer Sustainability | REACh Regulation | REACh Declaration
XVS96BMWN | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVS96BMWN | Offer Sustainability | Mercury free | Yes
XVS96BMWN | Offer Sustainability | RoHS exemption information | Yes
XVS96BMWN | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVS96BMWN | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVS96BMWN | Offer Sustainability | Circularity Profile | End of Life Information
XVS96BMWN | Contractual warranty | Warranty | 18 months
DL1EDBS | Main | range compatibility | Harmony XVM Optimum
DL1EDBS | Main | accessory / separate part category | Lighting accessory
DL1EDBS | Main | accessory / separate part type | Incandescent bulb
DL1EDBS | Main | accessory / separate part designation | Incandescent bulb
DL1EDBS | Main | accessory / separate part destination | Beacon and indicator bank
DL1EDBS | Main | bulb base | BA 15d
DL1EDBS | Main | signalling type | Steady
DL1EDBS | Main | [Us] rated supply voltage | 24 V AC/DC
DL1EDBS | Main | luminance | 650 cd/m²
DL1EDBS | Main | sale per indivisible quantity | 10
DL1EDBS | Complementary | maximum power dissipation in W | 5 W
DL1EDBS | Complementary | net weight | 0.007 kg
DL1EDBS | Offer Sustainability | Sustainable offer status | Green Premium product
DL1EDBS | Offer Sustainability | REACh Regulation | REACh Declaration
DL1EDBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1EDBS | Offer Sustainability | Mercury free | Yes
DL1EDBS | Offer Sustainability | RoHS exemption information | Yes
DL1EDBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1EDBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1EDBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1EDBS | Contractual warranty | Warranty | 18 months
DL1EDGS | Main | range compatibility | Harmony XVM Optimum
DL1EDGS | Main | accessory / separate part category | Lighting accessory
DL1EDGS | Main | accessory / separate part type | Incandescent bulb
DL1EDGS | Main | accessory / separate part designation | Incandescent bulb
DL1EDGS | Main | accessory / separate part destination | Beacon and indicator bank
DL1EDGS | Main | bulb base | BA 15d
DL1EDGS | Main | signalling type | Steady
DL1EDGS | Main | [Us] rated supply voltage | 120 V AC/DC
DL1EDGS | Main | luminance | 650 cd/m²
DL1EDGS | Main | sale per indivisible quantity | 10
DL1EDGS | Complementary | maximum power dissipation in W | 5 W
DL1EDGS | Complementary | net weight | 0.007 kg
DL1EDGS | Offer Sustainability | Sustainable offer status | Green Premium product
DL1EDGS | Offer Sustainability | REACh Regulation | REACh Declaration
DL1EDGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1EDGS | Offer Sustainability | Mercury free | Yes
DL1EDGS | Offer Sustainability | RoHS exemption information | Yes
DL1EDGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1EDGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1EDGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1EDGS | Contractual warranty | Warranty | 18 months
DL1EDMS | Main | range compatibility | Harmony XVM Optimum
DL1EDMS | Main | accessory / separate part category | Lighting accessory
DL1EDMS | Main | accessory / separate part type | Incandescent bulb
DL1EDMS | Main | accessory / separate part designation | Incandescent bulb
DL1EDMS | Main | accessory / separate part destination | Beacon and indicator bank
DL1EDMS | Main | bulb base | BA 15d
DL1EDMS | Main | signalling type | Steady
DL1EDMS | Main | [Us] rated supply voltage | 230 V AC/DC
DL1EDMS | Main | luminance | 650 cd/m²
DL1EDMS | Main | sale per indivisible quantity | 10
DL1EDMS | Complementary | maximum power dissipation in W | 5 W
DL1EDMS | Complementary | net weight | 0.007 kg
DL1EDMS | Offer Sustainability | Sustainable offer status | Green Premium product
DL1EDMS | Offer Sustainability | REACh Regulation | REACh Declaration
DL1EDMS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1EDMS | Offer Sustainability | Mercury free | Yes
DL1EDMS | Offer Sustainability | RoHS exemption information | Yes
DL1EDMS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1EDMS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1EDMS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1EDMS | Contractual warranty | Warranty | 18 months
DL2EDB1SB | Main | range compatibility | Harmony XVM Optimum
DL2EDB1SB | Main | accessory / separate part category | Lighting accessory
DL2EDB1SB | Main | accessory / separate part type | Super bright LED
DL2EDB1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDB1SB | Main | bulb base | BA 15d
DL2EDB1SB | Main | signalling type | Steady
DL2EDB1SB | Main | signalling colour | White
DL2EDB1SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EDB1SB | Main | luminance | 900 cd/m²
DL2EDB1SB | Main | sale per indivisible quantity | 1
DL2EDB1SB | Complementary | net weight | 0.009 kg
DL2EDB1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDB1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDB1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDB1SB | Offer Sustainability | Mercury free | Yes
DL2EDB1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDB1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDB1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDB1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDB1SB | Contractual warranty | Warranty | 18 months
DL2EDB3SB | Main | range compatibility | Harmony XVM Optimum
DL2EDB3SB | Main | accessory / separate part category | Lighting accessory
DL2EDB3SB | Main | accessory / separate part type | Super bright LED
DL2EDB3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDB3SB | Main | bulb base | BA 15d
DL2EDB3SB | Main | signalling type | Steady
DL2EDB3SB | Main | signalling colour | Green
DL2EDB3SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EDB3SB | Main | luminance | 900 cd/m²
DL2EDB3SB | Main | sale per indivisible quantity | 1
DL2EDB3SB | Complementary | net weight | 0.009 kg
DL2EDB3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDB3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDB3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDB3SB | Offer Sustainability | Mercury free | Yes
DL2EDB3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDB3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDB3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDB3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDB3SB | Contractual warranty | Warranty | 18 months
DL2EDB4SB | Main | range compatibility | Harmony XVM Optimum
DL2EDB4SB | Main | accessory / separate part category | Lighting accessory
DL2EDB4SB | Main | accessory / separate part type | Super bright LED
DL2EDB4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDB4SB | Main | bulb base | BA 15d
DL2EDB4SB | Main | signalling type | Steady
DL2EDB4SB | Main | signalling colour | Red
DL2EDB4SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EDB4SB | Main | luminance | 900 cd/m²
DL2EDB4SB | Main | sale per indivisible quantity | 1
DL2EDB4SB | Complementary | net weight | 0.009 kg
DL2EDB4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDB4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDB4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDB4SB | Offer Sustainability | Mercury free | Yes
DL2EDB4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDB4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDB4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDB4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDB4SB | Contractual warranty | Warranty | 18 months
DL2EDB6SB | Main | range compatibility | Harmony XVM Optimum
DL2EDB6SB | Main | accessory / separate part category | Lighting accessory
DL2EDB6SB | Main | accessory / separate part type | Super bright LED
DL2EDB6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDB6SB | Main | bulb base | BA 15d
DL2EDB6SB | Main | signalling type | Steady
DL2EDB6SB | Main | signalling colour | Blue
DL2EDB6SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EDB6SB | Main | luminance | 900 cd/m²
DL2EDB6SB | Main | sale per indivisible quantity | 1
DL2EDB6SB | Complementary | net weight | 0.009 kg
DL2EDB6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDB6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDB6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDB6SB | Offer Sustainability | Mercury free | Yes
DL2EDB6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDB6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDB6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDB6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDB6SB | Contractual warranty | Warranty | 18 months
DL2EDB8SB | Main | range compatibility | Harmony XVM Optimum
DL2EDB8SB | Main | accessory / separate part category | Lighting accessory
DL2EDB8SB | Main | accessory / separate part type | Super bright LED
DL2EDB8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDB8SB | Main | bulb base | BA 15d
DL2EDB8SB | Main | signalling type | Steady
DL2EDB8SB | Main | signalling colour | Orange
DL2EDB8SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EDB8SB | Main | luminance | 900 cd/m²
DL2EDB8SB | Main | sale per indivisible quantity | 1
DL2EDB8SB | Complementary | net weight | 0.009 kg
DL2EDB8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDB8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDB8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDB8SB | Offer Sustainability | Mercury free | Yes
DL2EDB8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDB8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDB8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDB8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDB8SB | Contractual warranty | Warranty | 18 months
DL2EDG1SB | Main | range compatibility | Harmony XVM Optimum
DL2EDG1SB | Main | accessory / separate part category | Lighting accessory
DL2EDG1SB | Main | accessory / separate part type | Super bright LED
DL2EDG1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDG1SB | Main | bulb base | BA 15d
DL2EDG1SB | Main | signalling type | Steady
DL2EDG1SB | Main | signalling colour | White
DL2EDG1SB | Main | [Us] rated supply voltage | 120 V AC
DL2EDG1SB | Main | luminance | 900 cd/m²
DL2EDG1SB | Main | sale per indivisible quantity | 1
DL2EDG1SB | Complementary | net weight | 0.009 kg
DL2EDG1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDG1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDG1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDG1SB | Offer Sustainability | Mercury free | Yes
DL2EDG1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDG1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDG1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDG1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDG1SB | Contractual warranty | Warranty | 18 months
DL2EDG3SB | Main | range compatibility | Harmony XVM Optimum
DL2EDG3SB | Main | accessory / separate part category | Lighting accessory
DL2EDG3SB | Main | accessory / separate part type | Super bright LED
DL2EDG3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDG3SB | Main | bulb base | BA 15d
DL2EDG3SB | Main | signalling type | Steady
DL2EDG3SB | Main | signalling colour | Green
DL2EDG3SB | Main | [Us] rated supply voltage | 120 V AC
DL2EDG3SB | Main | luminance | 900 cd/m²
DL2EDG3SB | Main | sale per indivisible quantity | 1
DL2EDG3SB | Complementary | net weight | 0.009 kg
DL2EDG3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDG3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDG3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDG3SB | Offer Sustainability | Mercury free | Yes
DL2EDG3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDG3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDG3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDG3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDG3SB | Contractual warranty | Warranty | 18 months
DL2EDG4SB | Main | range compatibility | Harmony XVM Optimum
DL2EDG4SB | Main | accessory / separate part category | Lighting accessory
DL2EDG4SB | Main | accessory / separate part type | Super bright LED
DL2EDG4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDG4SB | Main | bulb base | BA 15d
DL2EDG4SB | Main | signalling type | Steady
DL2EDG4SB | Main | signalling colour | Red
DL2EDG4SB | Main | [Us] rated supply voltage | 120 V AC
DL2EDG4SB | Main | luminance | 900 cd/m²
DL2EDG4SB | Main | sale per indivisible quantity | 1
DL2EDG4SB | Complementary | net weight | 0.009 kg
DL2EDG4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDG4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDG4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDG4SB | Offer Sustainability | Mercury free | Yes
DL2EDG4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDG4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDG4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDG4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDG4SB | Contractual warranty | Warranty | 18 months
DL2EDG6SB | Main | range compatibility | Harmony XVM Optimum
DL2EDG6SB | Main | accessory / separate part category | Lighting accessory
DL2EDG6SB | Main | accessory / separate part type | Super bright LED
DL2EDG6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDG6SB | Main | bulb base | BA 15d
DL2EDG6SB | Main | signalling type | Steady
DL2EDG6SB | Main | signalling colour | Blue
DL2EDG6SB | Main | [Us] rated supply voltage | 120 V AC
DL2EDG6SB | Main | luminance | 900 cd/m²
DL2EDG6SB | Main | sale per indivisible quantity | 1
DL2EDG6SB | Complementary | net weight | 0.009 kg
DL2EDG6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDG6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDG6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDG6SB | Offer Sustainability | Mercury free | Yes
DL2EDG6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDG6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDG6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDG6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDG6SB | Contractual warranty | Warranty | 18 months
DL2EDG8SB | Main | range compatibility | Harmony XVM Optimum
DL2EDG8SB | Main | accessory / separate part category | Lighting accessory
DL2EDG8SB | Main | accessory / separate part type | Super bright LED
DL2EDG8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDG8SB | Main | bulb base | BA 15d
DL2EDG8SB | Main | signalling type | Steady
DL2EDG8SB | Main | signalling colour | Orange
DL2EDG8SB | Main | [Us] rated supply voltage | 120 V AC
DL2EDG8SB | Main | luminance | 900 cd/m²
DL2EDG8SB | Main | sale per indivisible quantity | 1
DL2EDG8SB | Complementary | net weight | 0.009 kg
DL2EDG8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDG8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDG8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDG8SB | Offer Sustainability | Mercury free | Yes
DL2EDG8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDG8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDG8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDG8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDG8SB | Contractual warranty | Warranty | 18 months
DL2EDM1SB | Main | range compatibility | Harmony XVM Optimum
DL2EDM1SB | Main | accessory / separate part category | Lighting accessory
DL2EDM1SB | Main | accessory / separate part type | Super bright LED
DL2EDM1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDM1SB | Main | bulb base | BA 15d
DL2EDM1SB | Main | signalling type | Steady
DL2EDM1SB | Main | signalling colour | White
DL2EDM1SB | Main | [Us] rated supply voltage | 230 V AC
DL2EDM1SB | Main | luminance | 900 cd/m²
DL2EDM1SB | Main | sale per indivisible quantity | 1
DL2EDM1SB | Complementary | net weight | 0.009 kg
DL2EDM1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDM1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDM1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDM1SB | Offer Sustainability | Mercury free | Yes
DL2EDM1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDM1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDM1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDM1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDM1SB | Contractual warranty | Warranty | 18 months
DL2EDM3SB | Main | range compatibility | Harmony XVM Optimum
DL2EDM3SB | Main | accessory / separate part category | Lighting accessory
DL2EDM3SB | Main | accessory / separate part type | Super bright LED
DL2EDM3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDM3SB | Main | bulb base | BA 15d
DL2EDM3SB | Main | signalling type | Steady
DL2EDM3SB | Main | signalling colour | Green
DL2EDM3SB | Main | [Us] rated supply voltage | 230 V AC
DL2EDM3SB | Main | luminance | 900 cd/m²
DL2EDM3SB | Main | sale per indivisible quantity | 1
DL2EDM3SB | Complementary | net weight | 0.009 kg
DL2EDM3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDM3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDM3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDM3SB | Offer Sustainability | Mercury free | Yes
DL2EDM3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDM3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDM3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDM3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDM3SB | Contractual warranty | Warranty | 18 months
DL2EDM4SB | Main | range compatibility | Harmony XVM Optimum
DL2EDM4SB | Main | accessory / separate part category | Lighting accessory
DL2EDM4SB | Main | accessory / separate part type | Super bright LED
DL2EDM4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDM4SB | Main | bulb base | BA 15d
DL2EDM4SB | Main | signalling type | Steady
DL2EDM4SB | Main | signalling colour | Red
DL2EDM4SB | Main | [Us] rated supply voltage | 230 V AC
DL2EDM4SB | Main | luminance | 900 cd/m²
DL2EDM4SB | Main | sale per indivisible quantity | 1
DL2EDM4SB | Complementary | net weight | 0.009 kg
DL2EDM4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDM4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDM4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDM4SB | Offer Sustainability | Mercury free | Yes
DL2EDM4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDM4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDM4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDM4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDM4SB | Contractual warranty | Warranty | 18 months
DL2EDM6SB | Main | range compatibility | Harmony XVM Optimum
DL2EDM6SB | Main | accessory / separate part category | Lighting accessory
DL2EDM6SB | Main | accessory / separate part type | Super bright LED
DL2EDM6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDM6SB | Main | bulb base | BA 15d
DL2EDM6SB | Main | signalling type | Steady
DL2EDM6SB | Main | signalling colour | Blue
DL2EDM6SB | Main | [Us] rated supply voltage | 230 V AC
DL2EDM6SB | Main | luminance | 900 cd/m²
DL2EDM6SB | Main | sale per indivisible quantity | 1
DL2EDM6SB | Complementary | net weight | 0.009 kg
DL2EDM6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDM6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDM6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDM6SB | Offer Sustainability | Mercury free | Yes
DL2EDM6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDM6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDM6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDM6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDM6SB | Contractual warranty | Warranty | 18 months
DL2EDM8SB | Main | range compatibility | Harmony XVM Optimum
DL2EDM8SB | Main | accessory / separate part category | Lighting accessory
DL2EDM8SB | Main | accessory / separate part type | Super bright LED
DL2EDM8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EDM8SB | Main | bulb base | BA 15d
DL2EDM8SB | Main | signalling type | Steady
DL2EDM8SB | Main | signalling colour | Orange
DL2EDM8SB | Main | [Us] rated supply voltage | 230 V AC
DL2EDM8SB | Main | luminance | 900 cd/m²
DL2EDM8SB | Main | sale per indivisible quantity | 1
DL2EDM8SB | Complementary | net weight | 0.009 kg
DL2EDM8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EDM8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EDM8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EDM8SB | Offer Sustainability | Mercury free | Yes
DL2EDM8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EDM8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EDM8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EDM8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EDM8SB | Contractual warranty | Warranty | 18 months
DL2EKB1SB | Main | range compatibility | Harmony XVM Optimum
DL2EKB1SB | Main | accessory / separate part category | Lighting accessory
DL2EKB1SB | Main | accessory / separate part type | Super bright LED
DL2EKB1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKB1SB | Main | bulb base | BA 15d
DL2EKB1SB | Main | signalling type | Flashing
DL2EKB1SB | Main | signalling colour | White
DL2EKB1SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EKB1SB | Main | luminance | 900 cd/m²
DL2EKB1SB | Main | sale per indivisible quantity | 1
DL2EKB1SB | Complementary | flashing frequency | 1 Hz
DL2EKB1SB | Complementary | net weight | 0.009 kg
DL2EKB1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKB1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKB1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKB1SB | Offer Sustainability | Mercury free | Yes
DL2EKB1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKB1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKB1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKB1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKB1SB | Contractual warranty | Warranty | 18 months
DL2EKB3SB | Main | range compatibility | Harmony XVM Optimum
DL2EKB3SB | Main | accessory / separate part category | Lighting accessory
DL2EKB3SB | Main | accessory / separate part type | Super bright LED
DL2EKB3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKB3SB | Main | bulb base | BA 15d
DL2EKB3SB | Main | signalling type | Flashing
DL2EKB3SB | Main | signalling colour | Green
DL2EKB3SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EKB3SB | Main | luminance | 900 cd/m²
DL2EKB3SB | Main | sale per indivisible quantity | 1
DL2EKB3SB | Complementary | flashing frequency | 1 Hz
DL2EKB3SB | Complementary | net weight | 0.009 kg
DL2EKB3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKB3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKB3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKB3SB | Offer Sustainability | Mercury free | Yes
DL2EKB3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKB3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKB3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKB3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKB3SB | Contractual warranty | Warranty | 18 months
DL2EKB4SB | Main | range compatibility | Harmony XVM Optimum
DL2EKB4SB | Main | accessory / separate part category | Lighting accessory
DL2EKB4SB | Main | accessory / separate part type | Super bright LED
DL2EKB4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKB4SB | Main | bulb base | BA 15d
DL2EKB4SB | Main | signalling type | Flashing
DL2EKB4SB | Main | signalling colour | Red
DL2EKB4SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EKB4SB | Main | luminance | 900 cd/m²
DL2EKB4SB | Main | sale per indivisible quantity | 1
DL2EKB4SB | Complementary | flashing frequency | 1 Hz
DL2EKB4SB | Complementary | net weight | 0.009 kg
DL2EKB4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKB4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKB4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKB4SB | Offer Sustainability | Mercury free | Yes
DL2EKB4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKB4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKB4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKB4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKB4SB | Contractual warranty | Warranty | 18 months
DL2EKB6SB | Main | range compatibility | Harmony XVM Optimum
DL2EKB6SB | Main | accessory / separate part category | Lighting accessory
DL2EKB6SB | Main | accessory / separate part type | Super bright LED
DL2EKB6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKB6SB | Main | bulb base | BA 15d
DL2EKB6SB | Main | signalling type | Flashing
DL2EKB6SB | Main | signalling colour | Blue
DL2EKB6SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EKB6SB | Main | luminance | 900 cd/m²
DL2EKB6SB | Main | sale per indivisible quantity | 1
DL2EKB6SB | Complementary | flashing frequency | 1 Hz
DL2EKB6SB | Complementary | net weight | 0.009 kg
DL2EKB6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKB6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKB6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKB6SB | Offer Sustainability | Mercury free | Yes
DL2EKB6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKB6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKB6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKB6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKB6SB | Contractual warranty | Warranty | 18 months
DL2EKB8SB | Main | range compatibility | Harmony XVM Optimum
DL2EKB8SB | Main | accessory / separate part category | Lighting accessory
DL2EKB8SB | Main | accessory / separate part type | Super bright LED
DL2EKB8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKB8SB | Main | bulb base | BA 15d
DL2EKB8SB | Main | signalling type | Flashing
DL2EKB8SB | Main | signalling colour | Orange
DL2EKB8SB | Main | [Us] rated supply voltage | 24 V AC/DC
DL2EKB8SB | Main | luminance | 900 cd/m²
DL2EKB8SB | Main | sale per indivisible quantity | 1
DL2EKB8SB | Complementary | flashing frequency | 1 Hz
DL2EKB8SB | Complementary | net weight | 0.009 kg
DL2EKB8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKB8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKB8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKB8SB | Offer Sustainability | Mercury free | Yes
DL2EKB8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKB8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKB8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKB8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKB8SB | Contractual warranty | Warranty | 18 months
DL2EKG1SB | Main | range compatibility | Harmony XVM Optimum
DL2EKG1SB | Main | accessory / separate part category | Lighting accessory
DL2EKG1SB | Main | accessory / separate part type | Super bright LED
DL2EKG1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKG1SB | Main | bulb base | BA 15d
DL2EKG1SB | Main | signalling type | Flashing
DL2EKG1SB | Main | signalling colour | White
DL2EKG1SB | Main | [Us] rated supply voltage | 120 V AC
DL2EKG1SB | Main | luminance | 900 cd/m²
DL2EKG1SB | Main | sale per indivisible quantity | 1
DL2EKG1SB | Complementary | flashing frequency | 1 Hz
DL2EKG1SB | Complementary | net weight | 0.009 kg
DL2EKG1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKG1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKG1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKG1SB | Offer Sustainability | Mercury free | Yes
DL2EKG1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKG1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKG1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKG1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKG1SB | Contractual warranty | Warranty | 18 months
DL2EKG3SB | Main | range compatibility | Harmony XVM Optimum
DL2EKG3SB | Main | accessory / separate part category | Lighting accessory
DL2EKG3SB | Main | accessory / separate part type | Super bright LED
DL2EKG3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKG3SB | Main | bulb base | BA 15d
DL2EKG3SB | Main | signalling type | Flashing
DL2EKG3SB | Main | signalling colour | Green
DL2EKG3SB | Main | [Us] rated supply voltage | 120 V AC
DL2EKG3SB | Main | luminance | 900 cd/m²
DL2EKG3SB | Main | sale per indivisible quantity | 1
DL2EKG3SB | Complementary | flashing frequency | 1 Hz
DL2EKG3SB | Complementary | net weight | 0.009 kg
DL2EKG3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKG3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKG3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKG3SB | Offer Sustainability | Mercury free | Yes
DL2EKG3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKG3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKG3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKG3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKG3SB | Contractual warranty | Warranty | 18 months
DL2EKG4SB | Main | range compatibility | Harmony XVM Optimum
DL2EKG4SB | Main | accessory / separate part category | Lighting accessory
DL2EKG4SB | Main | accessory / separate part type | Super bright LED
DL2EKG4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKG4SB | Main | bulb base | BA 15d
DL2EKG4SB | Main | signalling type | Flashing
DL2EKG4SB | Main | signalling colour | Red
DL2EKG4SB | Main | [Us] rated supply voltage | 120 V AC
DL2EKG4SB | Main | luminance | 900 cd/m²
DL2EKG4SB | Main | sale per indivisible quantity | 1
DL2EKG4SB | Complementary | flashing frequency | 1 Hz
DL2EKG4SB | Complementary | net weight | 0.009 kg
DL2EKG4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKG4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKG4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKG4SB | Offer Sustainability | Mercury free | Yes
DL2EKG4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKG4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKG4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKG4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKG4SB | Contractual warranty | Warranty | 18 months
DL2EKG6SB | Main | range compatibility | Harmony XVM Optimum
DL2EKG6SB | Main | accessory / separate part category | Lighting accessory
DL2EKG6SB | Main | accessory / separate part type | Super bright LED
DL2EKG6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKG6SB | Main | bulb base | BA 15d
DL2EKG6SB | Main | signalling type | Flashing
DL2EKG6SB | Main | signalling colour | Blue
DL2EKG6SB | Main | [Us] rated supply voltage | 120 V AC
DL2EKG6SB | Main | luminance | 900 cd/m²
DL2EKG6SB | Main | sale per indivisible quantity | 1
DL2EKG6SB | Complementary | flashing frequency | 1 Hz
DL2EKG6SB | Complementary | net weight | 0.009 kg
DL2EKG6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKG6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKG6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKG6SB | Offer Sustainability | Mercury free | Yes
DL2EKG6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKG6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKG6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKG6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKG6SB | Contractual warranty | Warranty | 18 months
DL2EKG8SB | Main | range compatibility | Harmony XVM Optimum
DL2EKG8SB | Main | accessory / separate part category | Lighting accessory
DL2EKG8SB | Main | accessory / separate part type | Super bright LED
DL2EKG8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKG8SB | Main | bulb base | BA 15d
DL2EKG8SB | Main | signalling type | Flashing
DL2EKG8SB | Main | signalling colour | Orange
DL2EKG8SB | Main | [Us] rated supply voltage | 120 V AC
DL2EKG8SB | Main | luminance | 900 cd/m²
DL2EKG8SB | Main | sale per indivisible quantity | 1
DL2EKG8SB | Complementary | flashing frequency | 1 Hz
DL2EKG8SB | Complementary | net weight | 0.009 kg
DL2EKG8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKG8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKG8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKG8SB | Offer Sustainability | Mercury free | Yes
DL2EKG8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKG8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKG8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKG8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKG8SB | Contractual warranty | Warranty | 18 months
DL2EKM1SB | Main | range compatibility | Harmony XVM Optimum
DL2EKM1SB | Main | accessory / separate part category | Lighting accessory
DL2EKM1SB | Main | accessory / separate part type | Super bright LED
DL2EKM1SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKM1SB | Main | bulb base | BA 15d
DL2EKM1SB | Main | signalling type | Flashing
DL2EKM1SB | Main | signalling colour | White
DL2EKM1SB | Main | [Us] rated supply voltage | 230 V AC
DL2EKM1SB | Main | luminance | 900 cd/m²
DL2EKM1SB | Main | sale per indivisible quantity | 1
DL2EKM1SB | Complementary | flashing frequency | 1 Hz
DL2EKM1SB | Complementary | net weight | 0.009 kg
DL2EKM1SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKM1SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKM1SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKM1SB | Offer Sustainability | Mercury free | Yes
DL2EKM1SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKM1SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKM1SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKM1SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKM1SB | Contractual warranty | Warranty | 18 months
DL2EKM3SB | Main | range compatibility | Harmony XVM Optimum
DL2EKM3SB | Main | accessory / separate part category | Lighting accessory
DL2EKM3SB | Main | accessory / separate part type | Super bright LED
DL2EKM3SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKM3SB | Main | bulb base | BA 15d
DL2EKM3SB | Main | signalling type | Flashing
DL2EKM3SB | Main | signalling colour | Green
DL2EKM3SB | Main | [Us] rated supply voltage | 230 V AC
DL2EKM3SB | Main | luminance | 900 cd/m²
DL2EKM3SB | Main | sale per indivisible quantity | 1
DL2EKM3SB | Complementary | flashing frequency | 1 Hz
DL2EKM3SB | Complementary | net weight | 0.009 kg
DL2EKM3SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKM3SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKM3SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKM3SB | Offer Sustainability | Mercury free | Yes
DL2EKM3SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKM3SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKM3SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKM3SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKM3SB | Contractual warranty | Warranty | 18 months
DL2EKM4SB | Main | range compatibility | Harmony XVM Optimum
DL2EKM4SB | Main | accessory / separate part category | Lighting accessory
DL2EKM4SB | Main | accessory / separate part type | Super bright LED
DL2EKM4SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKM4SB | Main | bulb base | BA 15d
DL2EKM4SB | Main | signalling type | Flashing
DL2EKM4SB | Main | signalling colour | Red
DL2EKM4SB | Main | [Us] rated supply voltage | 230 V AC
DL2EKM4SB | Main | luminance | 900 cd/m²
DL2EKM4SB | Main | sale per indivisible quantity | 1
DL2EKM4SB | Complementary | flashing frequency | 1 Hz
DL2EKM4SB | Complementary | net weight | 0.009 kg
DL2EKM4SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKM4SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKM4SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKM4SB | Offer Sustainability | Mercury free | Yes
DL2EKM4SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKM4SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKM4SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKM4SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKM4SB | Contractual warranty | Warranty | 18 months
DL2EKM6SB | Main | range compatibility | Harmony XVM Optimum
DL2EKM6SB | Main | accessory / separate part category | Lighting accessory
DL2EKM6SB | Main | accessory / separate part type | Super bright LED
DL2EKM6SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKM6SB | Main | bulb base | BA 15d
DL2EKM6SB | Main | signalling type | Flashing
DL2EKM6SB | Main | signalling colour | Blue
DL2EKM6SB | Main | [Us] rated supply voltage | 230 V AC
DL2EKM6SB | Main | luminance | 900 cd/m²
DL2EKM6SB | Main | sale per indivisible quantity | 1
DL2EKM6SB | Complementary | flashing frequency | 1 Hz
DL2EKM6SB | Complementary | net weight | 0.009 kg
DL2EKM6SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKM6SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKM6SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKM6SB | Offer Sustainability | Mercury free | Yes
DL2EKM6SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKM6SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKM6SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKM6SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKM6SB | Contractual warranty | Warranty | 18 months
DL2EKM8SB | Main | range compatibility | Harmony XVM Optimum
DL2EKM8SB | Main | accessory / separate part category | Lighting accessory
DL2EKM8SB | Main | accessory / separate part type | Super bright LED
DL2EKM8SB | Main | accessory / separate part destination | Beacon and indicator bank
DL2EKM8SB | Main | bulb base | BA 15d
DL2EKM8SB | Main | signalling type | Flashing
DL2EKM8SB | Main | signalling colour | Orange
DL2EKM8SB | Main | [Us] rated supply voltage | 230 V AC
DL2EKM8SB | Main | luminance | 900 cd/m²
DL2EKM8SB | Main | sale per indivisible quantity | 1
DL2EKM8SB | Complementary | flashing frequency | 1 Hz
DL2EKM8SB | Complementary | net weight | 0.009 kg
DL2EKM8SB | Offer Sustainability | Sustainable offer status | Green Premium product
DL2EKM8SB | Offer Sustainability | REACh Regulation | REACh Declaration
DL2EKM8SB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL2EKM8SB | Offer Sustainability | Mercury free | Yes
DL2EKM8SB | Offer Sustainability | RoHS exemption information | Yes
DL2EKM8SB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL2EKM8SB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL2EKM8SB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL2EKM8SB | Contractual warranty | Warranty | 18 months
DL6BB | Main | range compatibility | Harmony XVM Optimum
DL6BB | Main | accessory / separate part category | Lighting accessory
DL6BB | Main | accessory / separate part type | Flash discharge tube
DL6BB | Main | accessory / separate part designation | Flash discharge tube
DL6BB | Main | accessory / separate part destination | Beacon and indicator bank
DL6BB | Main | bulb base | BA 15d
DL6BB | Main | signalling type | Flashing
DL6BB | Main | [Us] rated supply voltage | 24 V AC/DC
DL6BB | Main | sale per indivisible quantity | 1
DL6BB | Complementary | flash energy | 0.8 J
DL6BB | Complementary | flashing frequency | 0.8 Hz
DL6BB | Complementary | net weight | 0.022 kg
DL6BB | Offer Sustainability | Sustainable offer status | Green Premium product
DL6BB | Offer Sustainability | REACh Regulation | REACh Declaration
DL6BB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL6BB | Offer Sustainability | Mercury free | Yes
DL6BB | Offer Sustainability | RoHS exemption information | Yes
DL6BB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL6BB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL6BB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL6BB | Contractual warranty | Warranty | 18 months
DL6BG | Main | range compatibility | Harmony XVM Optimum
DL6BG | Main | accessory / separate part category | Lighting accessory
DL6BG | Main | accessory / separate part type | Flash discharge tube
DL6BG | Main | accessory / separate part designation | Flash discharge tube
DL6BG | Main | accessory / separate part destination | Beacon and indicator bank
DL6BG | Main | bulb base | BA 15d
DL6BG | Main | signalling type | Flashing
DL6BG | Main | [Us] rated supply voltage | 120 V AC
DL6BG | Main | sale per indivisible quantity | 1
DL6BG | Complementary | flash energy | 0.8 J
DL6BG | Complementary | flashing frequency | 0.8 Hz
DL6BG | Complementary | net weight | 0.022 kg
DL6BG | Offer Sustainability | Sustainable offer status | Green Premium product
DL6BG | Offer Sustainability | REACh Regulation | REACh Declaration
DL6BG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL6BG | Offer Sustainability | Mercury free | Yes
DL6BG | Offer Sustainability | RoHS exemption information | Yes
DL6BG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL6BG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL6BG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL6BG | Contractual warranty | Warranty | 18 months
DL6BM | Main | range compatibility | Harmony XVM Optimum
DL6BM | Main | accessory / separate part category | Lighting accessory
DL6BM | Main | accessory / separate part type | Flash discharge tube
DL6BM | Main | accessory / separate part designation | Flash discharge tube
DL6BM | Main | accessory / separate part destination | Beacon and indicator bank
DL6BM | Main | bulb base | BA 15d
DL6BM | Main | signalling type | Flashing
DL6BM | Main | [Us] rated supply voltage | 230 V AC
DL6BM | Main | sale per indivisible quantity | 1
DL6BM | Complementary | flash energy | 0.8 J
DL6BM | Complementary | flashing frequency | 0.8 Hz
DL6BM | Complementary | net weight | 0.022 kg
DL6BM | Offer Sustainability | Sustainable offer status | Green Premium product
DL6BM | Offer Sustainability | REACh Regulation | REACh Declaration
DL6BM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL6BM | Offer Sustainability | Mercury free | Yes
DL6BM | Offer Sustainability | RoHS exemption information | Yes
DL6BM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL6BM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL6BM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL6BM | Contractual warranty | Warranty | 18 months
XVMC21 | Main | range of product | Harmony XVM
XVMC21 | Main | product or component type | Base unit with cover
XVMC21 | Main | kit composition | Cover ¦ Base unit
XVMC21 | Main | component name | XVM
XVMC21 | Main | indicator bank base type | Base without buzzer
XVMC21 | Complementary | mounting diameter | 45 mm
XVMC21 | Complementary | housing colour | White
XVMC21 | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
XVMC21 | Complementary | marking | CE
XVMC21 | Complementary | net weight | 0.055 kg
XVMC21 | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMC21 | Environment | product certifications | CCC
XVMC21 | Environment | ambient air temperature for storage | -25…70 °C
XVMC21 | Environment | ambient air temperature for operation | -10…50 °C
XVMC21 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 ¦ Class I aluminium tube mounting conforming to IEC 60947-5-1 ¦ Class I aluminium tube mounting conforming to IEC 61140
XVMC21 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVMC21 | Environment | protective treatment | TC
XVMC21 | Offer Sustainability | Sustainable offer status | Green Premium product
XVMC21 | Offer Sustainability | REACh Regulation | REACh Declaration
XVMC21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMC21 | Offer Sustainability | Mercury free | Yes
XVMC21 | Offer Sustainability | RoHS exemption information | Yes
XVMC21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMC21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMC21 | Contractual warranty | Warranty | 18 months
XVMC29B | Main | range of product | Harmony XVM
XVMC29B | Main | product or component type | Base unit with cover
XVMC29B | Main | kit composition | Base unit ¦ Cover
XVMC29B | Main | component name | XVM
XVMC29B | Main | indicator bank base type | Base with integrated buzzer
XVMC29B | Main | [Us] rated supply voltage | 24 V
XVMC29B | Complementary | mounting diameter | 45 mm
XVMC29B | Complementary | signalling type | Continuous or intermittent buzzer
XVMC29B | Complementary | supply circuit type | AC/DC
XVMC29B | Complementary | housing colour | White
XVMC29B | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
XVMC29B | Complementary | marking | CE
XVMC29B | Complementary | current consumption | < 15 mA
XVMC29B | Complementary | fundamental frequency | 4 kHz
XVMC29B | Complementary | net weight | 0.065 kg
XVMC29B | Environment | noise level | 0…80 dB at 1 m
XVMC29B | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMC29B | Environment | product certifications | CCC
XVMC29B | Environment | ambient air temperature for storage | -25…70 °C
XVMC29B | Environment | ambient air temperature for operation | -10…50 °C
XVMC29B | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 ¦ Class I aluminium tube mounting conforming to IEC 60947-5-1 ¦ Class I aluminium tube mounting conforming to IEC 61140
XVMC29B | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVMC29B | Environment | protective treatment | TC
XVMC29B | Offer Sustainability | Sustainable offer status | Green Premium product
XVMC29B | Offer Sustainability | REACh Regulation | REACh Declaration
XVMC29B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMC29B | Offer Sustainability | Mercury free | Yes
XVMC29B | Offer Sustainability | RoHS exemption information | Yes
XVMC29B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMC29B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMC29B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMC29B | Contractual warranty | Warranty | 18 months
XVMC29G | Main | range of product | Harmony XVM
XVMC29G | Main | product or component type | Base unit with cover
XVMC29G | Main | kit composition | Base unit ¦ Cover
XVMC29G | Main | component name | XVM
XVMC29G | Main | indicator bank base type | Base with integrated buzzer
XVMC29G | Main | [Us] rated supply voltage | 120 V
XVMC29G | Complementary | mounting diameter | 45 mm
XVMC29G | Complementary | signalling type | Continuous or intermittent buzzer
XVMC29G | Complementary | supply circuit type | AC
XVMC29G | Complementary | housing colour | White
XVMC29G | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
XVMC29G | Complementary | marking | CE
XVMC29G | Complementary | current consumption | < 18 mA
XVMC29G | Complementary | fundamental frequency | 4 kHz
XVMC29G | Complementary | net weight | 0.065 kg
XVMC29G | Environment | noise level | 0…80 dB at 1 m
XVMC29G | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMC29G | Environment | product certifications | CCC
XVMC29G | Environment | ambient air temperature for storage | -25…70 °C
XVMC29G | Environment | ambient air temperature for operation | -10…50 °C
XVMC29G | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 ¦ Class I aluminium tube mounting conforming to IEC 60947-5-1 ¦ Class I aluminium tube mounting conforming to IEC 61140
XVMC29G | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVMC29G | Environment | protective treatment | TC
XVMC29G | Offer Sustainability | Sustainable offer status | Green Premium product
XVMC29G | Offer Sustainability | REACh Regulation | REACh Declaration
XVMC29G | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMC29G | Offer Sustainability | Mercury free | Yes
XVMC29G | Offer Sustainability | RoHS exemption information | Yes
XVMC29G | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMC29G | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMC29G | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMC29G | Contractual warranty | Warranty | 18 months
XVMC29M | Main | range of product | Harmony XVM
XVMC29M | Main | product or component type | Base unit with cover
XVMC29M | Main | kit composition | Cover ¦ Base unit
XVMC29M | Main | component name | XVM
XVMC29M | Main | indicator bank base type | Base with integrated buzzer
XVMC29M | Main | [Us] rated supply voltage | 230 V
XVMC29M | Complementary | mounting diameter | 45 mm
XVMC29M | Complementary | signalling type | Continuous or intermittent buzzer
XVMC29M | Complementary | supply circuit type | AC
XVMC29M | Complementary | housing colour | White
XVMC29M | Complementary | connections - terminals | Screw terminals, 1 x 0.325...1 x 1.5 mm²
XVMC29M | Complementary | marking | CE
XVMC29M | Complementary | current consumption | < 18 mA
XVMC29M | Complementary | fundamental frequency | 4 kHz
XVMC29M | Complementary | net weight | 0.065 kg
XVMC29M | Environment | noise level | 0…80 dB at 1 m
XVMC29M | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMC29M | Environment | product certifications | CCC
XVMC29M | Environment | ambient air temperature for storage | -25…70 °C
XVMC29M | Environment | ambient air temperature for operation | -10…50 °C
XVMC29M | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 60947-1 ¦ Class I aluminium tube mounting conforming to IEC 60947-5-1 ¦ Class I aluminium tube mounting conforming to IEC 61140
XVMC29M | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVMC29M | Environment | protective treatment | TC
XVMC29M | Offer Sustainability | Sustainable offer status | Green Premium product
XVMC29M | Offer Sustainability | REACh Regulation | REACh Declaration
XVMC29M | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMC29M | Offer Sustainability | Mercury free | Yes
XVMC29M | Offer Sustainability | RoHS exemption information | Yes
XVMC29M | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMC29M | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMC29M | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMC29M | Contractual warranty | Warranty | 18 months
DL1BEJ | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BEJ | Main | accessory / separate part designation | Incandescent bulb
DL1BEJ | Main | accessory / separate part type | Incandescent bulb
DL1BEJ | Main | accessory / separate part category | Lighting accessories
DL1BEJ | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEJ | Main | [Us] rated supply voltage | 12 V
DL1BEJ | Main | signalling type | Steady
DL1BEJ | Main | power dissipation in W | 7 W
DL1BEJ | Main | sale per indivisible quantity | 10
DL1BEJ | Complementary | bulb base | BA 15d
DL1BEJ | Complementary | net weight | 0.09 kg
DL1BEJ | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEJ | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEJ | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEJ | Offer Sustainability | Mercury free | Yes
DL1BEJ | Offer Sustainability | RoHS exemption information | Yes
DL1BEJ | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEJ | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEJ | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEJ | Contractual warranty | Warranty | 18 months
DL1BEB | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BEB | Main | accessory / separate part designation | Incandescent bulb
DL1BEB | Main | accessory / separate part type | Incandescent bulb
DL1BEB | Main | accessory / separate part category | Lighting accessories
DL1BEB | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEB | Main | [Us] rated supply voltage | 24 V
DL1BEB | Main | signalling type | Steady
DL1BEB | Main | power dissipation in W | 6.5 W
DL1BEB | Main | sale per indivisible quantity | 10
DL1BEB | Complementary | bulb base | BA 15d
DL1BEB | Complementary | net weight | 0.09 kg
DL1BEB | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEB | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEB | Offer Sustainability | Mercury free | Yes
DL1BEB | Offer Sustainability | RoHS exemption information | Yes
DL1BEB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEB | Contractual warranty | Warranty | 18 months
DL1BEE | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BEE | Main | accessory / separate part designation | Incandescent bulb
DL1BEE | Main | accessory / separate part type | Incandescent bulb
DL1BEE | Main | accessory / separate part category | Lighting accessories
DL1BEE | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEE | Main | [Us] rated supply voltage | 48 V
DL1BEE | Main | signalling type | Steady
DL1BEE | Main | power dissipation in W | 6 W
DL1BEE | Main | sale per indivisible quantity | 10
DL1BEE | Complementary | bulb base | BA 15d
DL1BEE | Complementary | net weight | 0.09 kg
DL1BEE | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEE | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEE | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEE | Offer Sustainability | Mercury free | Yes
DL1BEE | Offer Sustainability | RoHS exemption information | Yes
DL1BEE | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEE | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEE | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEE | Contractual warranty | Warranty | 18 months
DL1BEG | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BEG | Main | accessory / separate part designation | Incandescent bulb
DL1BEG | Main | accessory / separate part type | Incandescent bulb
DL1BEG | Main | accessory / separate part category | Lighting accessories
DL1BEG | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEG | Main | [Us] rated supply voltage | 120 V
DL1BEG | Main | signalling type | Steady
DL1BEG | Main | power dissipation in W | 7 W
DL1BEG | Main | sale per indivisible quantity | 10
DL1BEG | Complementary | bulb base | BA 15d
DL1BEG | Complementary | net weight | 0.09 kg
DL1BEG | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEG | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEG | Offer Sustainability | Mercury free | Yes
DL1BEG | Offer Sustainability | RoHS exemption information | Yes
DL1BEG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEG | Contractual warranty | Warranty | 18 months
DL1BEM | Main | range compatibility | Harmony XVB ¦ Harmony XVD ¦ Harmony XVP
DL1BEM | Main | accessory / separate part designation | Incandescent bulb
DL1BEM | Main | accessory / separate part type | Incandescent bulb
DL1BEM | Main | accessory / separate part category | Lighting accessories
DL1BEM | Main | accessory / separate part destination | Beacon and indicator bank
DL1BEM | Main | [Us] rated supply voltage | 230 V
DL1BEM | Main | signalling type | Steady
DL1BEM | Main | power dissipation in W | 7 W
DL1BEM | Main | sale per indivisible quantity | 10
DL1BEM | Complementary | bulb base | BA 15d
DL1BEM | Complementary | net weight | 0.09 kg
DL1BEM | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BEM | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BEM | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BEM | Offer Sustainability | Mercury free | Yes
DL1BEM | Offer Sustainability | RoHS exemption information | Yes
DL1BEM | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BEM | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BEM | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BEM | Contractual warranty | Warranty | 18 months
DL1BDB1 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDB1 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB1 | Main | accessory / separate part type | LED bulb
DL1BDB1 | Main | accessory / separate part category | Lighting accessories
DL1BDB1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB1 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB1 | Main | signalling type | Steady
DL1BDB1 | Main | signalling colour | White
DL1BDB1 | Main | sale per indivisible quantity | 1
DL1BDB1 | Complementary | current consumption | 47 mA
DL1BDB1 | Complementary | bulb base | BA 15d
DL1BDB1 | Complementary | net weight | 0.015 kg
DL1BDB1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB1 | Offer Sustainability | Mercury free | Yes
DL1BDB1 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB1 | Contractual warranty | Warranty | 18 months
DL1BDB3 | Main | range compatibility | Harmony XVB ¦ Harmony XVD ¦ Harmony XVP
DL1BDB3 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB3 | Main | accessory / separate part type | LED bulb
DL1BDB3 | Main | accessory / separate part category | Lighting accessories
DL1BDB3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB3 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB3 | Main | signalling type | Steady
DL1BDB3 | Main | signalling colour | Green
DL1BDB3 | Main | sale per indivisible quantity | 1
DL1BDB3 | Complementary | current consumption | 47 mA
DL1BDB3 | Complementary | bulb base | BA 15d
DL1BDB3 | Complementary | net weight | 0.015 kg
DL1BDB3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB3 | Offer Sustainability | Mercury free | Yes
DL1BDB3 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB3 | Contractual warranty | Warranty | 18 months
DL1BDB4 | Main | range compatibility | Harmony XVP ¦ Harmony XVD ¦ Harmony XVB
DL1BDB4 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB4 | Main | accessory / separate part type | LED bulb
DL1BDB4 | Main | accessory / separate part category | Lighting accessories
DL1BDB4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB4 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB4 | Main | signalling type | Steady
DL1BDB4 | Main | signalling colour | Red
DL1BDB4 | Main | sale per indivisible quantity | 1
DL1BDB4 | Complementary | current consumption | 47 mA
DL1BDB4 | Complementary | bulb base | BA 15d
DL1BDB4 | Complementary | net weight | 0.015 kg
DL1BDB4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB4 | Offer Sustainability | Mercury free | Yes
DL1BDB4 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB4 | Contractual warranty | Warranty | 18 months
DL1BDB5 | Main | range compatibility | Harmony XVD ¦ Harmony XVP ¦ Harmony XVB
DL1BDB5 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB5 | Main | accessory / separate part type | LED bulb
DL1BDB5 | Main | accessory / separate part category | Lighting accessories
DL1BDB5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB5 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB5 | Main | signalling type | Steady
DL1BDB5 | Main | signalling colour | Orange
DL1BDB5 | Main | sale per indivisible quantity | 1
DL1BDB5 | Complementary | current consumption | 47 mA
DL1BDB5 | Complementary | bulb base | BA 15d
DL1BDB5 | Complementary | net weight | 0.015 kg
DL1BDB5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB5 | Offer Sustainability | Mercury free | Yes
DL1BDB5 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB5 | Contractual warranty | Warranty | 18 months
DL1BDB6 | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BDB6 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB6 | Main | accessory / separate part type | LED bulb
DL1BDB6 | Main | accessory / separate part category | Lighting accessories
DL1BDB6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB6 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB6 | Main | signalling type | Steady
DL1BDB6 | Main | signalling colour | Blue
DL1BDB6 | Main | sale per indivisible quantity | 1
DL1BDB6 | Complementary | current consumption | 47 mA
DL1BDB6 | Complementary | bulb base | BA 15d
DL1BDB6 | Complementary | net weight | 0.015 kg
DL1BDB6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB6 | Offer Sustainability | Mercury free | Yes
DL1BDB6 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB6 | Contractual warranty | Warranty | 18 months
DL1BDB8 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BDB8 | Main | accessory / separate part designation | Protected LED bulb
DL1BDB8 | Main | accessory / separate part type | LED bulb
DL1BDB8 | Main | accessory / separate part category | Lighting accessories
DL1BDB8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDB8 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BDB8 | Main | signalling type | Steady
DL1BDB8 | Main | signalling colour | Yellow
DL1BDB8 | Main | sale per indivisible quantity | 1
DL1BDB8 | Complementary | current consumption | 47 mA
DL1BDB8 | Complementary | bulb base | BA 15d
DL1BDB8 | Complementary | net weight | 0.015 kg
DL1BDB8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDB8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDB8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDB8 | Offer Sustainability | Mercury free | Yes
DL1BDB8 | Offer Sustainability | RoHS exemption information | Yes
DL1BDB8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDB8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDB8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDB8 | Contractual warranty | Warranty | 18 months
DL1BDG1 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDG1 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG1 | Main | accessory / separate part type | LED bulb
DL1BDG1 | Main | accessory / separate part category | Lighting accessories
DL1BDG1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG1 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG1 | Main | signalling type | Steady
DL1BDG1 | Main | signalling colour | White
DL1BDG1 | Main | sale per indivisible quantity | 1
DL1BDG1 | Complementary | current consumption | 17 mA
DL1BDG1 | Complementary | bulb base | BA 15d
DL1BDG1 | Complementary | net weight | 0.015 kg
DL1BDG1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG1 | Offer Sustainability | Mercury free | Yes
DL1BDG1 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG1 | Contractual warranty | Warranty | 18 months
DL1BDG3 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDG3 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG3 | Main | accessory / separate part type | LED bulb
DL1BDG3 | Main | accessory / separate part category | Lighting accessories
DL1BDG3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG3 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG3 | Main | signalling type | Steady
DL1BDG3 | Main | signalling colour | Green
DL1BDG3 | Main | sale per indivisible quantity | 1
DL1BDG3 | Complementary | current consumption | 17 mA
DL1BDG3 | Complementary | bulb base | BA 15d
DL1BDG3 | Complementary | net weight | 0.015 kg
DL1BDG3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG3 | Offer Sustainability | Mercury free | Yes
DL1BDG3 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG3 | Contractual warranty | Warranty | 18 months
DL1BDG4 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDG4 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG4 | Main | accessory / separate part type | LED bulb
DL1BDG4 | Main | accessory / separate part category | Lighting accessories
DL1BDG4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG4 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG4 | Main | signalling type | Steady
DL1BDG4 | Main | signalling colour | Red
DL1BDG4 | Main | sale per indivisible quantity | 1
DL1BDG4 | Complementary | current consumption | 17 mA
DL1BDG4 | Complementary | bulb base | BA 15d
DL1BDG4 | Complementary | net weight | 0.015 kg
DL1BDG4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG4 | Offer Sustainability | REACh free of SVHC | Yes
DL1BDG4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG4 | Offer Sustainability | Toxic heavy metal free | Yes
DL1BDG4 | Offer Sustainability | Mercury free | Yes
DL1BDG4 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG4 | Offer Sustainability | Circularity Profile | End of Life Information
DL1BDG4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG4 | Contractual warranty | Warranty | 18 months
DL1BDG5 | Main | range compatibility | Harmony XVB ¦ Harmony XVD ¦ Harmony XVP
DL1BDG5 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG5 | Main | accessory / separate part type | LED bulb
DL1BDG5 | Main | accessory / separate part category | Lighting accessories
DL1BDG5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG5 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG5 | Main | signalling type | Steady
DL1BDG5 | Main | signalling colour | Orange
DL1BDG5 | Main | sale per indivisible quantity | 1
DL1BDG5 | Complementary | current consumption | 17 mA
DL1BDG5 | Complementary | bulb base | BA 15d
DL1BDG5 | Complementary | net weight | 0.015 kg
DL1BDG5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG5 | Offer Sustainability | Mercury free | Yes
DL1BDG5 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG5 | Contractual warranty | Warranty | 18 months
DL1BDG6 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDG6 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG6 | Main | accessory / separate part type | LED bulb
DL1BDG6 | Main | accessory / separate part category | Lighting accessories
DL1BDG6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG6 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG6 | Main | signalling type | Steady
DL1BDG6 | Main | signalling colour | Blue
DL1BDG6 | Main | sale per indivisible quantity | 1
DL1BDG6 | Complementary | current consumption | 17 mA
DL1BDG6 | Complementary | bulb base | BA 15d
DL1BDG6 | Complementary | net weight | 0.015 kg
DL1BDG6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG6 | Offer Sustainability | Mercury free | Yes
DL1BDG6 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG6 | Contractual warranty | Warranty | 18 months
DL1BDG8 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BDG8 | Main | accessory / separate part designation | Protected LED bulb
DL1BDG8 | Main | accessory / separate part type | LED bulb
DL1BDG8 | Main | accessory / separate part category | Lighting accessories
DL1BDG8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDG8 | Main | [Us] rated supply voltage | 120 V AC
DL1BDG8 | Main | signalling type | Steady
DL1BDG8 | Main | signalling colour | Yellow
DL1BDG8 | Main | sale per indivisible quantity | 1
DL1BDG8 | Complementary | current consumption | 17 mA
DL1BDG8 | Complementary | bulb base | BA 15d
DL1BDG8 | Complementary | net weight | 0.015 kg
DL1BDG8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDG8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDG8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDG8 | Offer Sustainability | Mercury free | Yes
DL1BDG8 | Offer Sustainability | RoHS exemption information | Yes
DL1BDG8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDG8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDG8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDG8 | Contractual warranty | Warranty | 18 months
DL1BDM1 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDM1 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM1 | Main | accessory / separate part type | LED bulb
DL1BDM1 | Main | accessory / separate part category | Lighting accessories
DL1BDM1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM1 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM1 | Main | signalling type | Steady
DL1BDM1 | Main | signalling colour | White
DL1BDM1 | Main | sale per indivisible quantity | 1
DL1BDM1 | Complementary | current consumption | 17 mA
DL1BDM1 | Complementary | bulb base | BA 15d
DL1BDM1 | Complementary | net weight | 0.015 kg
DL1BDM1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM1 | Offer Sustainability | Mercury free | Yes
DL1BDM1 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM1 | Contractual warranty | Warranty | 18 months
DL1BDM3 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDM3 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM3 | Main | accessory / separate part type | LED bulb
DL1BDM3 | Main | accessory / separate part category | Lighting accessories
DL1BDM3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM3 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM3 | Main | signalling type | Steady
DL1BDM3 | Main | signalling colour | Green
DL1BDM3 | Main | sale per indivisible quantity | 1
DL1BDM3 | Complementary | current consumption | 17 mA
DL1BDM3 | Complementary | bulb base | BA 15d
DL1BDM3 | Complementary | net weight | 0.015 kg
DL1BDM3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM3 | Offer Sustainability | Mercury free | Yes
DL1BDM3 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM3 | Contractual warranty | Warranty | 18 months
DL1BDM4 | Main | range compatibility | Harmony XVB ¦ Harmony XVD ¦ Harmony XVP
DL1BDM4 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM4 | Main | accessory / separate part type | LED bulb
DL1BDM4 | Main | accessory / separate part category | Lighting accessories
DL1BDM4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM4 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM4 | Main | signalling type | Steady
DL1BDM4 | Main | signalling colour | Red
DL1BDM4 | Main | sale per indivisible quantity | 1
DL1BDM4 | Complementary | current consumption | 17 mA
DL1BDM4 | Complementary | bulb base | BA 15d
DL1BDM4 | Complementary | net weight | 0.015 kg
DL1BDM4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM4 | Offer Sustainability | Mercury free | Yes
DL1BDM4 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM4 | Contractual warranty | Warranty | 18 months
DL1BDM5 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BDM5 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM5 | Main | accessory / separate part type | LED bulb
DL1BDM5 | Main | accessory / separate part category | Lighting accessories
DL1BDM5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM5 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM5 | Main | signalling type | Steady
DL1BDM5 | Main | signalling colour | Orange
DL1BDM5 | Main | sale per indivisible quantity | 1
DL1BDM5 | Complementary | current consumption | 17 mA
DL1BDM5 | Complementary | bulb base | BA 15d
DL1BDM5 | Complementary | net weight | 0.015 kg
DL1BDM5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM5 | Offer Sustainability | Mercury free | Yes
DL1BDM5 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM5 | Contractual warranty | Warranty | 18 months
DL1BDM6 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BDM6 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM6 | Main | accessory / separate part type | LED bulb
DL1BDM6 | Main | accessory / separate part category | Lighting accessories
DL1BDM6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM6 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM6 | Main | signalling type | Steady
DL1BDM6 | Main | signalling colour | Blue
DL1BDM6 | Main | sale per indivisible quantity | 1
DL1BDM6 | Complementary | current consumption | 17 mA
DL1BDM6 | Complementary | bulb base | BA 15d
DL1BDM6 | Complementary | net weight | 0.015 kg
DL1BDM6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM6 | Offer Sustainability | Mercury free | Yes
DL1BDM6 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM6 | Contractual warranty | Warranty | 18 months
DL1BDM8 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BDM8 | Main | accessory / separate part designation | Protected LED bulb
DL1BDM8 | Main | accessory / separate part type | LED bulb
DL1BDM8 | Main | accessory / separate part category | Lighting accessories
DL1BDM8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BDM8 | Main | [Us] rated supply voltage | 230 V AC
DL1BDM8 | Main | signalling type | Steady
DL1BDM8 | Main | signalling colour | Yellow
DL1BDM8 | Main | sale per indivisible quantity | 1
DL1BDM8 | Complementary | current consumption | 17 mA
DL1BDM8 | Complementary | bulb base | BA 15d
DL1BDM8 | Complementary | net weight | 0.015 kg
DL1BDM8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BDM8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BDM8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BDM8 | Offer Sustainability | Mercury free | Yes
DL1BDM8 | Offer Sustainability | RoHS exemption information | Yes
DL1BDM8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BDM8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BDM8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BDM8 | Contractual warranty | Warranty | 18 months
DL1BKB1 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKB1 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB1 | Main | accessory / separate part type | LED bulb
DL1BKB1 | Main | accessory / separate part category | Lighting accessories
DL1BKB1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB1 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB1 | Main | signalling type | Flashing
DL1BKB1 | Main | signalling colour | White
DL1BKB1 | Main | sale per indivisible quantity | 1
DL1BKB1 | Complementary | current consumption | 47 mA
DL1BKB1 | Complementary | bulb base | BA 15d
DL1BKB1 | Complementary | net weight | 0.015 kg
DL1BKB1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB1 | Offer Sustainability | Mercury free | Yes
DL1BKB1 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB1 | Contractual warranty | Warranty | 18 months
DL1BKB3 | Main | range compatibility | Harmony XVD ¦ Harmony XVP ¦ Harmony XVB
DL1BKB3 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB3 | Main | accessory / separate part type | LED bulb
DL1BKB3 | Main | accessory / separate part category | Lighting accessories
DL1BKB3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB3 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB3 | Main | signalling type | Flashing
DL1BKB3 | Main | signalling colour | Green
DL1BKB3 | Main | sale per indivisible quantity | 1
DL1BKB3 | Complementary | current consumption | 47 mA
DL1BKB3 | Complementary | bulb base | BA 15d
DL1BKB3 | Complementary | net weight | 0.015 kg
DL1BKB3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB3 | Offer Sustainability | Mercury free | Yes
DL1BKB3 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB3 | Contractual warranty | Warranty | 18 months
DL1BKB4 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BKB4 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB4 | Main | accessory / separate part type | LED bulb
DL1BKB4 | Main | accessory / separate part category | Lighting accessories
DL1BKB4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB4 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB4 | Main | signalling type | Flashing
DL1BKB4 | Main | signalling colour | Red
DL1BKB4 | Main | sale per indivisible quantity | 1
DL1BKB4 | Complementary | current consumption | 47 mA
DL1BKB4 | Complementary | bulb base | BA 15d
DL1BKB4 | Complementary | net weight | 0.015 kg
DL1BKB4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB4 | Offer Sustainability | Mercury free | Yes
DL1BKB4 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB4 | Contractual warranty | Warranty | 18 months
DL1BKB5 | Main | range compatibility | Harmony XVB ¦ Harmony XVD ¦ Harmony XVP
DL1BKB5 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB5 | Main | accessory / separate part type | LED bulb
DL1BKB5 | Main | accessory / separate part category | Lighting accessories
DL1BKB5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB5 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB5 | Main | signalling type | Flashing
DL1BKB5 | Main | signalling colour | Orange
DL1BKB5 | Main | sale per indivisible quantity | 1
DL1BKB5 | Complementary | current consumption | 47 mA
DL1BKB5 | Complementary | bulb base | BA 15d
DL1BKB5 | Complementary | net weight | 0.015 kg
DL1BKB5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB5 | Offer Sustainability | Mercury free | Yes
DL1BKB5 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB5 | Contractual warranty | Warranty | 18 months
DL1BKB6 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKB6 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB6 | Main | accessory / separate part type | LED bulb
DL1BKB6 | Main | accessory / separate part category | Lighting accessories
DL1BKB6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB6 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB6 | Main | signalling type | Flashing
DL1BKB6 | Main | signalling colour | Blue
DL1BKB6 | Main | sale per indivisible quantity | 1
DL1BKB6 | Complementary | current consumption | 47 mA
DL1BKB6 | Complementary | bulb base | BA 15d
DL1BKB6 | Complementary | net weight | 0.015 kg
DL1BKB6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB6 | Offer Sustainability | Mercury free | Yes
DL1BKB6 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB6 | Contractual warranty | Warranty | 18 months
DL1BKB8 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKB8 | Main | accessory / separate part designation | Protected LED bulb
DL1BKB8 | Main | accessory / separate part type | LED bulb
DL1BKB8 | Main | accessory / separate part category | Lighting accessories
DL1BKB8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKB8 | Main | [Us] rated supply voltage | 24 V AC/DC
DL1BKB8 | Main | signalling type | Flashing
DL1BKB8 | Main | signalling colour | Yellow
DL1BKB8 | Main | sale per indivisible quantity | 1
DL1BKB8 | Complementary | current consumption | 47 mA
DL1BKB8 | Complementary | bulb base | BA 15d
DL1BKB8 | Complementary | net weight | 0.015 kg
DL1BKB8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKB8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKB8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKB8 | Offer Sustainability | Mercury free | Yes
DL1BKB8 | Offer Sustainability | RoHS exemption information | Yes
DL1BKB8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKB8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKB8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKB8 | Contractual warranty | Warranty | 18 months
DL1BKG1 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BKG1 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG1 | Main | accessory / separate part type | LED bulb
DL1BKG1 | Main | accessory / separate part category | Lighting accessories
DL1BKG1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG1 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG1 | Main | signalling type | Flashing
DL1BKG1 | Main | signalling colour | White
DL1BKG1 | Main | sale per indivisible quantity | 1
DL1BKG1 | Complementary | current consumption | 17 mA
DL1BKG1 | Complementary | bulb base | BA 15d
DL1BKG1 | Complementary | net weight | 0.015 kg
DL1BKG1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG1 | Offer Sustainability | Mercury free | Yes
DL1BKG1 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG1 | Contractual warranty | Warranty | 18 months
DL1BKG3 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKG3 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG3 | Main | accessory / separate part type | LED bulb
DL1BKG3 | Main | accessory / separate part category | Lighting accessories
DL1BKG3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG3 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG3 | Main | signalling type | Flashing
DL1BKG3 | Main | signalling colour | Green
DL1BKG3 | Main | sale per indivisible quantity | 1
DL1BKG3 | Complementary | current consumption | 17 mA
DL1BKG3 | Complementary | bulb base | BA 15d
DL1BKG3 | Complementary | net weight | 0.015 kg
DL1BKG3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG3 | Offer Sustainability | Mercury free | Yes
DL1BKG3 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG3 | Contractual warranty | Warranty | 18 months
DL1BKG4 | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BKG4 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG4 | Main | accessory / separate part type | LED bulb
DL1BKG4 | Main | accessory / separate part category | Lighting accessories
DL1BKG4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG4 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG4 | Main | signalling type | Flashing
DL1BKG4 | Main | signalling colour | Red
DL1BKG4 | Main | sale per indivisible quantity | 1
DL1BKG4 | Complementary | current consumption | 17 mA
DL1BKG4 | Complementary | bulb base | BA 15d
DL1BKG4 | Complementary | net weight | 0.015 kg
DL1BKG4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG4 | Offer Sustainability | Mercury free | Yes
DL1BKG4 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG4 | Contractual warranty | Warranty | 18 months
DL1BKG5 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKG5 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG5 | Main | accessory / separate part type | LED bulb
DL1BKG5 | Main | accessory / separate part category | Lighting accessories
DL1BKG5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG5 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG5 | Main | signalling type | Flashing
DL1BKG5 | Main | signalling colour | Orange
DL1BKG5 | Main | sale per indivisible quantity | 1
DL1BKG5 | Complementary | current consumption | 17 mA
DL1BKG5 | Complementary | bulb base | BA 15d
DL1BKG5 | Complementary | net weight | 0.015 kg
DL1BKG5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG5 | Offer Sustainability | Mercury free | Yes
DL1BKG5 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG5 | Contractual warranty | Warranty | 18 months
DL1BKG6 | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BKG6 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG6 | Main | accessory / separate part type | LED bulb
DL1BKG6 | Main | accessory / separate part category | Lighting accessories
DL1BKG6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG6 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG6 | Main | signalling type | Flashing
DL1BKG6 | Main | signalling colour | Blue
DL1BKG6 | Main | sale per indivisible quantity | 1
DL1BKG6 | Complementary | current consumption | 17 mA
DL1BKG6 | Complementary | bulb base | BA 15d
DL1BKG6 | Complementary | net weight | 0.015 kg
DL1BKG6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG6 | Offer Sustainability | Mercury free | Yes
DL1BKG6 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG6 | Contractual warranty | Warranty | 18 months
DL1BKG8 | Main | range compatibility | Harmony XVP ¦ Harmony XVD ¦ Harmony XVB
DL1BKG8 | Main | accessory / separate part designation | Protected LED bulb
DL1BKG8 | Main | accessory / separate part type | LED bulb
DL1BKG8 | Main | accessory / separate part category | Lighting accessories
DL1BKG8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKG8 | Main | [Us] rated supply voltage | 120 V AC
DL1BKG8 | Main | signalling type | Flashing
DL1BKG8 | Main | signalling colour | Yellow
DL1BKG8 | Main | sale per indivisible quantity | 1
DL1BKG8 | Complementary | current consumption | 17 mA
DL1BKG8 | Complementary | bulb base | BA 15d
DL1BKG8 | Complementary | net weight | 0.015 kg
DL1BKG8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKG8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKG8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKG8 | Offer Sustainability | Mercury free | Yes
DL1BKG8 | Offer Sustainability | RoHS exemption information | Yes
DL1BKG8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKG8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKG8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKG8 | Contractual warranty | Warranty | 18 months
DL1BKM1 | Main | range compatibility | Harmony XVD ¦ Harmony XVP ¦ Harmony XVB
DL1BKM1 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM1 | Main | accessory / separate part type | LED bulb
DL1BKM1 | Main | accessory / separate part category | Lighting accessories
DL1BKM1 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM1 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM1 | Main | signalling type | Flashing
DL1BKM1 | Main | signalling colour | White
DL1BKM1 | Main | sale per indivisible quantity | 1
DL1BKM1 | Complementary | current consumption | 17 mA
DL1BKM1 | Complementary | bulb base | BA 15d
DL1BKM1 | Complementary | net weight | 0.015 kg
DL1BKM1 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM1 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM1 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM1 | Offer Sustainability | Mercury free | Yes
DL1BKM1 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM1 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM1 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM1 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM1 | Contractual warranty | Warranty | 18 months
DL1BKM3 | Main | range compatibility | Harmony XVD ¦ Harmony XVB ¦ Harmony XVP
DL1BKM3 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM3 | Main | accessory / separate part type | LED bulb
DL1BKM3 | Main | accessory / separate part category | Lighting accessories
DL1BKM3 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM3 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM3 | Main | signalling type | Flashing
DL1BKM3 | Main | signalling colour | Green
DL1BKM3 | Main | sale per indivisible quantity | 1
DL1BKM3 | Complementary | current consumption | 17 mA
DL1BKM3 | Complementary | bulb base | BA 15d
DL1BKM3 | Complementary | net weight | 0.015 kg
DL1BKM3 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM3 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM3 | Offer Sustainability | Mercury free | Yes
DL1BKM3 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM3 | Contractual warranty | Warranty | 18 months
DL1BKM4 | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BKM4 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM4 | Main | accessory / separate part type | LED bulb
DL1BKM4 | Main | accessory / separate part category | Lighting accessories
DL1BKM4 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM4 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM4 | Main | signalling type | Flashing
DL1BKM4 | Main | signalling colour | Red
DL1BKM4 | Main | sale per indivisible quantity | 1
DL1BKM4 | Complementary | current consumption | 17 mA
DL1BKM4 | Complementary | bulb base | BA 15d
DL1BKM4 | Complementary | net weight | 0.015 kg
DL1BKM4 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM4 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM4 | Offer Sustainability | Mercury free | Yes
DL1BKM4 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM4 | Contractual warranty | Warranty | 18 months
DL1BKM5 | Main | range compatibility | Harmony XVB ¦ Harmony XVP ¦ Harmony XVD
DL1BKM5 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM5 | Main | accessory / separate part type | LED bulb
DL1BKM5 | Main | accessory / separate part category | Lighting accessories
DL1BKM5 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM5 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM5 | Main | signalling type | Flashing
DL1BKM5 | Main | signalling colour | Orange
DL1BKM5 | Main | sale per indivisible quantity | 1
DL1BKM5 | Complementary | current consumption | 17 mA
DL1BKM5 | Complementary | bulb base | BA 15d
DL1BKM5 | Complementary | net weight | 0.015 kg
DL1BKM5 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM5 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM5 | Offer Sustainability | Mercury free | Yes
DL1BKM5 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM5 | Contractual warranty | Warranty | 18 months
DL1BKM6 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BKM6 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM6 | Main | accessory / separate part type | LED bulb
DL1BKM6 | Main | accessory / separate part category | Lighting accessories
DL1BKM6 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM6 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM6 | Main | signalling type | Flashing
DL1BKM6 | Main | signalling colour | Blue
DL1BKM6 | Main | sale per indivisible quantity | 1
DL1BKM6 | Complementary | current consumption | 17 mA
DL1BKM6 | Complementary | bulb base | BA 15d
DL1BKM6 | Complementary | net weight | 0.015 kg
DL1BKM6 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM6 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM6 | Offer Sustainability | Mercury free | Yes
DL1BKM6 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM6 | Contractual warranty | Warranty | 18 months
DL1BKM8 | Main | range compatibility | Harmony XVP ¦ Harmony XVB ¦ Harmony XVD
DL1BKM8 | Main | accessory / separate part designation | Protected LED bulb
DL1BKM8 | Main | accessory / separate part type | LED bulb
DL1BKM8 | Main | accessory / separate part category | Lighting accessories
DL1BKM8 | Main | accessory / separate part destination | Beacon and indicator bank
DL1BKM8 | Main | [Us] rated supply voltage | 230 V AC
DL1BKM8 | Main | signalling type | Flashing
DL1BKM8 | Main | signalling colour | Yellow
DL1BKM8 | Main | sale per indivisible quantity | 1
DL1BKM8 | Complementary | current consumption | 17 mA
DL1BKM8 | Complementary | bulb base | BA 15d
DL1BKM8 | Complementary | net weight | 0.015 kg
DL1BKM8 | Offer Sustainability | Sustainable offer status | Green Premium product
DL1BKM8 | Offer Sustainability | REACh Regulation | REACh Declaration
DL1BKM8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
DL1BKM8 | Offer Sustainability | Mercury free | Yes
DL1BKM8 | Offer Sustainability | RoHS exemption information | Yes
DL1BKM8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
DL1BKM8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
DL1BKM8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
DL1BKM8 | Contractual warranty | Warranty | 18 months
XVBC9B | Main | range of product | Harmony XVB Universal
XVBC9B | Main | product or component type | Indicator bank
XVBC9B | Main | beacon or indicator bank unit type | Audible unit
XVBC9B | Main | mounting diameter | 70 mm
XVBC9B | Main | component name | XVBC
XVBC9B | Main | noise level | 70…90 dB at 1 m
XVBC9B | Main | [Us] rated supply voltage | 12...48 V AC/DC
XVBC9B | Complementary | signalling type | Continuous or intermittent buzzer
XVBC9B | Complementary | assembly style | Customer assembly, up to 5 units
XVBC9B | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC9B | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC9B | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC9B | Complementary | current consumption | < 15 mA
XVBC9B | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC9B | Complementary | fundamental frequency | 2.8 kHz
XVBC9B | Complementary | CAD overall width | 70 mm
XVBC9B | Complementary | CAD overall height | 63 mm
XVBC9B | Complementary | CAD overall depth | 70 mm
XVBC9B | Complementary | net weight | 0.17 kg
XVBC9B | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBC9B | Environment | standards | EN/IEC 60947-5-1
XVBC9B | Environment | protective treatment | TC
XVBC9B | Environment | ambient air temperature for storage | -40…70 °C
XVBC9B | Environment | ambient air temperature for operation | -25…50 °C
XVBC9B | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC9B | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC9B | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC9B | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC9B | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC9B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC9B | Offer Sustainability | Mercury free | Yes
XVBC9B | Offer Sustainability | RoHS exemption information | Yes
XVBC9B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC9B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC9B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC9B | Contractual warranty | Warranty | 18 months
XVBC9M | Main | range of product | Harmony XVB Universal
XVBC9M | Main | product or component type | Indicator bank
XVBC9M | Main | beacon or indicator bank unit type | Audible unit
XVBC9M | Main | mounting diameter | 70 mm
XVBC9M | Main | component name | XVBC
XVBC9M | Main | noise level | 70…90 dB at 1 m
XVBC9M | Main | [Us] rated supply voltage | 120...230 V AC
XVBC9M | Complementary | signalling type | Continuous or intermittent buzzer
XVBC9M | Complementary | assembly style | Customer assembly, up to 5 units
XVBC9M | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC9M | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC9M | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC9M | Complementary | current consumption | < 25 mA
XVBC9M | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC9M | Complementary | fundamental frequency | 2.8 kHz
XVBC9M | Complementary | CAD overall width | 70 mm
XVBC9M | Complementary | CAD overall height | 63 mm
XVBC9M | Complementary | CAD overall depth | 70 mm
XVBC9M | Complementary | net weight | 0.18 kg
XVBC9M | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBC9M | Environment | standards | EN/IEC 60947-5-1
XVBC9M | Environment | protective treatment | TC
XVBC9M | Environment | ambient air temperature for storage | -40…70 °C
XVBC9M | Environment | ambient air temperature for operation | -25…50 °C
XVBC9M | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC9M | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC9M | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC9M | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC9M | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC9M | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC9M | Offer Sustainability | Mercury free | Yes
XVBC9M | Offer Sustainability | RoHS exemption information | Yes
XVBC9M | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC9M | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC9M | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC9M | Contractual warranty | Warranty | 18 months
XVBC07 | Main | range of product | Harmony XVB Universal
XVBC07 | Main | product or component type | Base unit
XVBC07 | Main | component name | XVBC
XVBC07 | Main | material | Glass reinforced polyamide: base unit
XVBC07 | Complementary | fixing mode | Direct or tube fixing
XVBC07 | Complementary | mounting diameter | 70 mm
XVBC07 | Complementary | product destination | Banks without flash discharge tube unit
XVBC07 | Complementary | electrical connection | 1 connector for standard input
XVBC07 | Complementary | cable entry | Bottom or side entry
XVBC07 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC07 | Complementary | terminals description ISO n°1 | (COM-2)PW ¦ (COM-3)PW ¦ (COM-1)PW ¦ (GND)GROUND ¦ (COM-4)PW ¦ (COM-5)PW
XVBC07 | Complementary | net weight | 0.16 kg
XVBC07 | Environment | product certifications | CCC ¦ UL 508 ¦ CSA C22-2 No 14 ¦ GOST
XVBC07 | Environment | standards | EN/IEC 60947-5-1
XVBC07 | Environment | protective treatment | TC
XVBC07 | Environment | ambient air temperature for storage | -40…70 °C
XVBC07 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC07 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC07 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC07 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC07 | Offer Sustainability | Mercury free | Yes
XVBC07 | Offer Sustainability | RoHS exemption information | Yes
XVBC07 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC07 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC07 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC07 | Contractual warranty | Warranty | 18 months
XVBC21 | Main | range of product | Harmony XVB Universal
XVBC21 | Main | product or component type | Base unit with cover
XVBC21 | Main | component name | XVBC
XVBC21 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover unit
XVBC21 | Complementary | fixing mode | Direct or tube fixing
XVBC21 | Complementary | mounting diameter | 70 mm
XVBC21 | Complementary | product destination | Banks without flash discharge tube unit
XVBC21 | Complementary | electrical connection | 1 connector for standard input
XVBC21 | Complementary | cable entry | Bottom or side entry
XVBC21 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC21 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW ¦ (COM-4)PW ¦ (COM-3)PW ¦ (COM-5)PW ¦ (COM-2)PW
XVBC21 | Complementary | net weight | 0.19 kg
XVBC21 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBC21 | Environment | standards | EN/IEC 60947-5-1
XVBC21 | Environment | protective treatment | TC
XVBC21 | Environment | ambient air temperature for storage | -40…70 °C
XVBC21 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC21 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC21 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC21 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC21 | Offer Sustainability | Mercury free | Yes
XVBC21 | Offer Sustainability | RoHS exemption information | Yes
XVBC21 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC21 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC21 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC21 | Contractual warranty | Warranty | 18 months
XVBC21A | Main | range of product | Harmony XVB Universal
XVBC21A | Main | product or component type | Base unit with cover
XVBC21A | Main | component name | XVBC
XVBC21A | Complementary | range compatibility | AS-Interface cabling system
XVBC21A | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover unit
XVBC21A | Complementary | mounting diameter | 70 mm
XVBC21A | Complementary | [Us] rated supply voltage | External: 19.2...30 V ¦ AS-Interface line: 24...31.6 V
XVBC21A | Complementary | current consumption | 250 mA under load via AS-Interface line ¦ 30 mA under load external ¦ 30 mA no load
XVBC21A | Complementary | actuator sensor interface profile [AS-i] | S.7.F
XVBC21A | Complementary | electrical connection | 1 connector M12 for AS-Interface line
XVBC21A | Complementary | cable entry | Side entry
XVBC21A | Complementary | assembly style | Customer assembly, up to 5 units
XVBC21A | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC21A | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC21A | Complementary | terminals description ISO n°1 | (COM-5)PW ¦ (COM-1)PW ¦ (COM-4)PW ¦ (COM-3)PW ¦ (GND)GROUND ¦ (COM-2)PW
XVBC21A | Complementary | net weight | 0.19 kg
XVBC21A | Environment | product certifications | AS-Interface No 25701 ¦ CSA
XVBC21A | Environment | standards | EN/IEC 60947-5-1
XVBC21A | Environment | protective treatment | TC
XVBC21A | Environment | ambient air temperature for storage | -20…70 °C
XVBC21A | Environment | ambient air temperature for operation | -10…50 °C
XVBC21A | Environment | shock resistance | 25 gn conforming to IEC 60068-2-27
XVBC21A | Environment | vibration resistance | 5 gn conforming to IEC 60068-2-6
XVBC21A | Environment | overvoltage category | Class I conforming to IEC 60536
XVBC21A | Environment | IP degree of protection | IP65 conforming to IEC 60529 ¦ IP65 conforming to NF C 20-010
XVBC21A | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC21A | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC21A | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC21A | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC21A | Offer Sustainability | Mercury free | Yes
XVBC21A | Offer Sustainability | RoHS exemption information | Yes
XVBC21A | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC21A | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC21A | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC21A | Contractual warranty | Warranty | 18 months
XVBC21B | Main | range of product | Harmony XVB Universal
XVBC21B | Main | product or component type | Base unit with cover
XVBC21B | Main | component name | XVBC
XVBC21B | Complementary | range compatibility | AS-Interface cabling system
XVBC21B | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover unit
XVBC21B | Complementary | mounting diameter | 70 mm
XVBC21B | Complementary | [Us] rated supply voltage | External: 19.2...30 V ¦ AS-Interface line: 24...31.6 V
XVBC21B | Complementary | current consumption | 250 mA under load via AS-Interface line ¦ 30 mA under load external ¦ 30 mA no load
XVBC21B | Complementary | actuator sensor interface profile [AS-i] | S.7.F
XVBC21B | Complementary | electrical connection | 1 remote connector M12, cable length: 1 m for AS-Interface line
XVBC21B | Complementary | cable entry | Side entry
XVBC21B | Complementary | assembly style | Customer assembly, up to 5 units
XVBC21B | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC21B | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC21B | Complementary | terminals description ISO n°1 | (COM-4)PW ¦ (COM-2)PW ¦ (COM-3)PW ¦ (COM-1)PW ¦ (GND)GROUND ¦ (COM-5)PW
XVBC21B | Complementary | net weight | 0.3 kg
XVBC21B | Environment | product certifications | CSA ¦ AS-Interface No 25701
XVBC21B | Environment | standards | EN/IEC 60947-5-1
XVBC21B | Environment | protective treatment | TC
XVBC21B | Environment | ambient air temperature for storage | -20…70 °C
XVBC21B | Environment | ambient air temperature for operation | -10…50 °C
XVBC21B | Environment | shock resistance | 25 gn conforming to IEC 60068-2-27
XVBC21B | Environment | vibration resistance | 5 gn conforming to IEC 60068-2-6
XVBC21B | Environment | overvoltage category | Class I conforming to IEC 60536
XVBC21B | Environment | IP degree of protection | IP65 conforming to IEC 60529 ¦ IP65 conforming to NF C 20-010
XVBC21B | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC21B | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC21B | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC21B | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC21B | Offer Sustainability | Mercury free | Yes
XVBC21B | Offer Sustainability | RoHS exemption information | Yes
XVBC21B | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC21B | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC21B | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC21B | Contractual warranty | Warranty | 18 months
XVDLS33 | Main | range of product | Harmony XVD Optimum
XVDLS33 | Main | product or component type | Complete miniature beacon
XVDLS33 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS33 | Main | signalling type | Steady
XVDLS33 | Main | mounting diameter | 45 mm
XVDLS33 | Main | component name | XVDLS
XVDLS33 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS33 | Main | light source | Bulb not included, green
XVDLS33 | Main | bulb type | Incandescent with BA 15d base
XVDLS33 | Main | [Us] rated supply voltage | <= 230 V
XVDLS33 | Main | maximum power dissipation in W | 5 W
XVDLS33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS33 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS33 | Complementary | CAD overall width | 45 mm
XVDLS33 | Complementary | CAD overall height | 104 mm
XVDLS33 | Complementary | CAD overall depth | 45 mm
XVDLS33 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS33 | Complementary | net weight | 0.08 kg
XVDLS33 | Environment | product certifications | CSA ¦ UL
XVDLS33 | Environment | standards | EN/IEC 60947-5-1
XVDLS33 | Environment | protective treatment | TC
XVDLS33 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS33 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS33 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS33 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS33 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS33 | Offer Sustainability | Mercury free | Yes
XVDLS33 | Offer Sustainability | RoHS exemption information | Yes
XVDLS33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS33 | Contractual warranty | Warranty | 18 months
XVDLS34 | Main | range of product | Harmony XVD Optimum
XVDLS34 | Main | product or component type | Complete miniature beacon
XVDLS34 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS34 | Main | signalling type | Steady
XVDLS34 | Main | mounting diameter | 45 mm
XVDLS34 | Main | component name | XVDLS
XVDLS34 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS34 | Main | light source | Bulb not included, red
XVDLS34 | Main | bulb type | Incandescent with BA 15d base
XVDLS34 | Main | [Us] rated supply voltage | <= 230 V
XVDLS34 | Main | maximum power dissipation in W | 5 W
XVDLS34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS34 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS34 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS34 | Complementary | CAD overall width | 45 mm
XVDLS34 | Complementary | CAD overall height | 104 mm
XVDLS34 | Complementary | CAD overall depth | 45 mm
XVDLS34 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS34 | Complementary | net weight | 0.08 kg
XVDLS34 | Environment | product certifications | UL ¦ CSA
XVDLS34 | Environment | standards | EN/IEC 60947-5-1
XVDLS34 | Environment | protective treatment | TC
XVDLS34 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS34 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS34 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS34 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS34 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS34 | Offer Sustainability | Mercury free | Yes
XVDLS34 | Offer Sustainability | RoHS exemption information | Yes
XVDLS34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS34 | Contractual warranty | Warranty | 18 months
XVDLS35 | Main | range of product | Harmony XVD Optimum
XVDLS35 | Main | product or component type | Complete miniature beacon
XVDLS35 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS35 | Main | signalling type | Steady
XVDLS35 | Main | mounting diameter | 45 mm
XVDLS35 | Main | component name | XVDLS
XVDLS35 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS35 | Main | light source | Bulb not included, orange
XVDLS35 | Main | bulb type | Incandescent with BA 15d base
XVDLS35 | Main | [Us] rated supply voltage | <= 230 V
XVDLS35 | Main | maximum power dissipation in W | 5 W
XVDLS35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS35 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS35 | Complementary | CAD overall width | 45 mm
XVDLS35 | Complementary | CAD overall height | 104 mm
XVDLS35 | Complementary | CAD overall depth | 45 mm
XVDLS35 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS35 | Complementary | net weight | 0.08 kg
XVDLS35 | Environment | product certifications | CSA ¦ UL
XVDLS35 | Environment | standards | EN/IEC 60947-5-1
XVDLS35 | Environment | protective treatment | TC
XVDLS35 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS35 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS35 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS35 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS35 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS35 | Offer Sustainability | Mercury free | Yes
XVDLS35 | Offer Sustainability | RoHS exemption information | Yes
XVDLS35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS35 | Contractual warranty | Warranty | 18 months
XVDLS36 | Main | range of product | Harmony XVD Optimum
XVDLS36 | Main | product or component type | Complete miniature beacon
XVDLS36 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS36 | Main | signalling type | Steady
XVDLS36 | Main | mounting diameter | 45 mm
XVDLS36 | Main | component name | XVDLS
XVDLS36 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS36 | Main | light source | Bulb not included, blue
XVDLS36 | Main | bulb type | Incandescent with BA 15d base
XVDLS36 | Main | [Us] rated supply voltage | <= 230 V
XVDLS36 | Main | maximum power dissipation in W | 5 W
XVDLS36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS36 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS36 | Complementary | CAD overall width | 45 mm
XVDLS36 | Complementary | CAD overall height | 104 mm
XVDLS36 | Complementary | CAD overall depth | 45 mm
XVDLS36 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS36 | Complementary | net weight | 0.08 kg
XVDLS36 | Environment | product certifications | UL ¦ CSA
XVDLS36 | Environment | standards | EN/IEC 60947-5-1
XVDLS36 | Environment | protective treatment | TC
XVDLS36 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS36 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS36 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS36 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS36 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS36 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS36 | Offer Sustainability | Mercury free | Yes
XVDLS36 | Offer Sustainability | RoHS exemption information | Yes
XVDLS36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS36 | Contractual warranty | Warranty | 18 months
XVDLS37 | Main | range of product | Harmony XVD Optimum
XVDLS37 | Main | product or component type | Complete miniature beacon
XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS37 | Main | signalling type | Steady
XVDLS37 | Main | mounting diameter | 45 mm
XVDLS37 | Main | component name | XVDLS
XVDLS37 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS37 | Main | light source | Bulb not included, clear
XVDLS37 | Main | bulb type | Incandescent with BA 15d base
XVDLS37 | Main | [Us] rated supply voltage | <= 230 V
XVDLS37 | Main | maximum power dissipation in W | 5 W
XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS37 | Complementary | CAD overall width | 45 mm
XVDLS37 | Complementary | CAD overall height | 104 mm
XVDLS37 | Complementary | CAD overall depth | 45 mm
XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS37 | Complementary | net weight | 0.08 kg
XVDLS37 | Environment | product certifications | CSA ¦ UL
XVDLS37 | Environment | standards | EN/IEC 60947-5-1
XVDLS37 | Environment | protective treatment | TC
XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS37 | Offer Sustainability | Mercury free | Yes
XVDLS37 | Offer Sustainability | RoHS exemption information | Yes
XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS37 | Contractual warranty | Warranty | 18 months
XVDLS38 | Main | range of product | Harmony XVD Optimum
XVDLS38 | Main | product or component type | Complete miniature beacon
XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS38 | Main | signalling type | Steady
XVDLS38 | Main | mounting diameter | 45 mm
XVDLS38 | Main | component name | XVDLS
XVDLS38 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS38 | Main | light source | Bulb not included, yellow
XVDLS38 | Main | bulb type | Incandescent with BA 15d base
XVDLS38 | Main | [Us] rated supply voltage | <= 230 V
XVDLS38 | Main | maximum power dissipation in W | 5 W
XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS38 | Complementary | CAD overall width | 45 mm
XVDLS38 | Complementary | CAD overall height | 104 mm
XVDLS38 | Complementary | CAD overall depth | 45 mm
XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS38 | Complementary | net weight | 0.08 kg
XVDLS38 | Environment | product certifications | CSA ¦ UL
XVDLS38 | Environment | standards | EN/IEC 60947-5-1
XVDLS38 | Environment | protective treatment | TC
XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C
XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS38 | Offer Sustainability | Mercury free | Yes
XVDLS38 | Offer Sustainability | RoHS exemption information | Yes
XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS38 | Contractual warranty | Warranty | 18 months
XVDLS6B3 | Main | range of product | Harmony XVD Optimum
XVDLS6B3 | Main | product or component type | Complete miniature beacon
XVDLS6B3 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B3 | Main | signalling type | Flashing
XVDLS6B3 | Main | mounting diameter | 45 mm
XVDLS6B3 | Main | component name | XVDLS
XVDLS6B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B3 | Main | light source | Integral flash discharge tube, green
XVDLS6B3 | Main | bulb type | Flash discharge tube
XVDLS6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B3 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B3 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B3 | Complementary | flash energy | 1 J
XVDLS6B3 | Complementary | CAD overall width | 45 mm
XVDLS6B3 | Complementary | CAD overall height | 104 mm
XVDLS6B3 | Complementary | CAD overall depth | 45 mm
XVDLS6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6B3 | Complementary | net weight | 0.085 kg
XVDLS6B3 | Environment | product certifications | CSA ¦ UL
XVDLS6B3 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B3 | Environment | protective treatment | TC
XVDLS6B3 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B3 | Offer Sustainability | Mercury free | Yes
XVDLS6B3 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B3 | Contractual warranty | Warranty | 18 months
XVDLS6B4 | Main | range of product | Harmony XVD Optimum
XVDLS6B4 | Main | product or component type | Complete miniature beacon
XVDLS6B4 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B4 | Main | signalling type | Flashing
XVDLS6B4 | Main | mounting diameter | 45 mm
XVDLS6B4 | Main | component name | XVDLS
XVDLS6B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B4 | Main | light source | Integral flash discharge tube, red
XVDLS6B4 | Main | bulb type | Flash discharge tube
XVDLS6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B4 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B4 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B4 | Complementary | flash energy | 1 J
XVDLS6B4 | Complementary | CAD overall width | 45 mm
XVDLS6B4 | Complementary | CAD overall height | 104 mm
XVDLS6B4 | Complementary | CAD overall depth | 45 mm
XVDLS6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B4 | Complementary | net weight | 0.085 kg
XVDLS6B4 | Environment | product certifications | UL ¦ CSA
XVDLS6B4 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B4 | Environment | protective treatment | TC
XVDLS6B4 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B4 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B4 | Offer Sustainability | Mercury free | Yes
XVDLS6B4 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B4 | Contractual warranty | Warranty | 18 months
XVDLS6B5 | Main | range of product | Harmony XVD Optimum
XVDLS6B5 | Main | product or component type | Complete miniature beacon
XVDLS6B5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B5 | Main | signalling type | Flashing
XVDLS6B5 | Main | mounting diameter | 45 mm
XVDLS6B5 | Main | component name | XVDLS
XVDLS6B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B5 | Main | light source | Integral flash discharge tube, orange
XVDLS6B5 | Main | bulb type | Flash discharge tube
XVDLS6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B5 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6B5 | Complementary | flash energy | 1 J
XVDLS6B5 | Complementary | CAD overall width | 45 mm
XVDLS6B5 | Complementary | CAD overall height | 104 mm
XVDLS6B5 | Complementary | CAD overall depth | 45 mm
XVDLS6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6B5 | Complementary | net weight | 0.085 kg
XVDLS6B5 | Environment | product certifications | CSA ¦ UL
XVDLS6B5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B5 | Environment | protective treatment | TC
XVDLS6B5 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B5 | Offer Sustainability | Mercury free | Yes
XVDLS6B5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B5 | Contractual warranty | Warranty | 18 months
XVDLS6B6 | Main | range of product | Harmony XVD Optimum
XVDLS6B6 | Main | product or component type | Complete miniature beacon
XVDLS6B6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B6 | Main | signalling type | Flashing
XVDLS6B6 | Main | mounting diameter | 45 mm
XVDLS6B6 | Main | component name | XVDLS
XVDLS6B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B6 | Main | light source | Integral flash discharge tube, blue
XVDLS6B6 | Main | bulb type | Flash discharge tube
XVDLS6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B6 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B6 | Complementary | flash energy | 1 J
XVDLS6B6 | Complementary | CAD overall width | 45 mm
XVDLS6B6 | Complementary | CAD overall height | 104 mm
XVDLS6B6 | Complementary | CAD overall depth | 45 mm
XVDLS6B6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B6 | Complementary | net weight | 0.085 kg
XVDLS6B6 | Environment | product certifications | CSA ¦ UL
XVDLS6B6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B6 | Environment | protective treatment | TC
XVDLS6B6 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B6 | Offer Sustainability | Mercury free | Yes
XVDLS6B6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B6 | Contractual warranty | Warranty | 18 months
XVDLS6B7 | Main | range of product | Harmony XVD Optimum
XVDLS6B7 | Main | product or component type | Complete miniature beacon
XVDLS6B7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B7 | Main | signalling type | Flashing
XVDLS6B7 | Main | mounting diameter | 45 mm
XVDLS6B7 | Main | component name | XVDLS
XVDLS6B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B7 | Main | light source | Integral flash discharge tube, clear
XVDLS6B7 | Main | bulb type | Flash discharge tube
XVDLS6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B7 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6B7 | Complementary | flash energy | 1 J
XVDLS6B7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6B7 | Complementary | CAD overall width | 45 mm
XVDLS6B7 | Complementary | CAD overall height | 104 mm
XVDLS6B7 | Complementary | CAD overall depth | 45 mm
XVDLS6B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B7 | Complementary | net weight | 0.085 kg
XVDLS6B7 | Environment | product certifications | UL ¦ CSA
XVDLS6B7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B7 | Environment | protective treatment | TC
XVDLS6B7 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B7 | Offer Sustainability | Mercury free | Yes
XVDLS6B7 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B7 | Contractual warranty | Warranty | 18 months
XVDLS6B8 | Main | range of product | Harmony XVD Optimum
XVDLS6B8 | Main | product or component type | Complete miniature beacon
XVDLS6B8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6B8 | Main | signalling type | Flashing
XVDLS6B8 | Main | mounting diameter | 45 mm
XVDLS6B8 | Main | component name | XVDLS
XVDLS6B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6B8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6B8 | Main | bulb type | Flash discharge tube
XVDLS6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDLS6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6B8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6B8 | Complementary | current consumption | < 145 mA DC ¦ < 90 mA AC
XVDLS6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6B8 | Complementary | flash energy | 1 J
XVDLS6B8 | Complementary | CAD overall width | 45 mm
XVDLS6B8 | Complementary | CAD overall height | 104 mm
XVDLS6B8 | Complementary | CAD overall depth | 45 mm
XVDLS6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6B8 | Complementary | net weight | 0.085 kg
XVDLS6B8 | Environment | product certifications | CSA ¦ UL
XVDLS6B8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6B8 | Environment | protective treatment | TC
XVDLS6B8 | Environment | ambient air temperature for operation | -10…50 °C
XVDLS6B8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6B8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6B8 | Offer Sustainability | Mercury free | Yes
XVDLS6B8 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6B8 | Contractual warranty | Warranty | 18 months
XVDLS6G4 | Main | range of product | Harmony XVD Optimum
XVDLS6G4 | Main | product or component type | Complete miniature beacon
XVDLS6G4 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G4 | Main | signalling type | Flashing
XVDLS6G4 | Main | mounting diameter | 45 mm
XVDLS6G4 | Main | component name | XVDLS
XVDLS6G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G4 | Main | light source | Integral flash discharge tube, red
XVDLS6G4 | Main | bulb type | Flash discharge tube
XVDLS6G4 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G4 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G4 | Complementary | current consumption | < 35 mA AC
XVDLS6G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G4 | Complementary | flash energy | 1 J
XVDLS6G4 | Complementary | CAD overall width | 45 mm
XVDLS6G4 | Complementary | CAD overall height | 104 mm
XVDLS6G4 | Complementary | CAD overall depth | 45 mm
XVDLS6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G4 | Complementary | net weight | 0.085 kg
XVDLS6G4 | Environment | product certifications | CSA ¦ UL
XVDLS6G4 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G4 | Environment | protective treatment | TC
XVDLS6G4 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G4 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G4 | Offer Sustainability | Mercury free | Yes
XVDLS6G4 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G4 | Contractual warranty | Warranty | 18 months
XVDLS6G5 | Main | range of product | Harmony XVD Optimum
XVDLS6G5 | Main | product or component type | Complete miniature beacon
XVDLS6G5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G5 | Main | signalling type | Flashing
XVDLS6G5 | Main | mounting diameter | 45 mm
XVDLS6G5 | Main | component name | XVDLS
XVDLS6G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G5 | Main | light source | Integral flash discharge tube, orange
XVDLS6G5 | Main | bulb type | Flash discharge tube
XVDLS6G5 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G5 | Complementary | current consumption | < 35 mA AC
XVDLS6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6G5 | Complementary | flash energy | 1 J
XVDLS6G5 | Complementary | CAD overall width | 45 mm
XVDLS6G5 | Complementary | CAD overall height | 104 mm
XVDLS6G5 | Complementary | CAD overall depth | 45 mm
XVDLS6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6G5 | Complementary | net weight | 0.085 kg
XVDLS6G5 | Environment | product certifications | CSA ¦ UL
XVDLS6G5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G5 | Environment | protective treatment | TC
XVDLS6G5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G5 | Offer Sustainability | Mercury free | Yes
XVDLS6G5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G5 | Contractual warranty | Warranty | 18 months
XVDLS6G6 | Main | range of product | Harmony XVD Optimum
XVDLS6G6 | Main | product or component type | Complete miniature beacon
XVDLS6G6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G6 | Main | signalling type | Flashing
XVDLS6G6 | Main | mounting diameter | 45 mm
XVDLS6G6 | Main | component name | XVDLS
XVDLS6G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G6 | Main | light source | Integral flash discharge tube, blue
XVDLS6G6 | Main | bulb type | Flash discharge tube
XVDLS6G6 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G6 | Complementary | current consumption | < 35 mA AC
XVDLS6G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G6 | Complementary | flash energy | 1 J
XVDLS6G6 | Complementary | CAD overall width | 45 mm
XVDLS6G6 | Complementary | CAD overall height | 104 mm
XVDLS6G6 | Complementary | CAD overall depth | 45 mm
XVDLS6G6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G6 | Complementary | net weight | 0.085 kg
XVDLS6G6 | Environment | product certifications | CSA ¦ UL
XVDLS6G6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G6 | Environment | protective treatment | TC
XVDLS6G6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6G6 | Offer Sustainability | Mercury free | Yes
XVDLS6G6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6G6 | Contractual warranty | Warranty | 18 months
XVDLS6G7 | Main | range of product | Harmony XVD Optimum
XVDLS6G7 | Main | product or component type | Complete miniature beacon
XVDLS6G7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G7 | Main | signalling type | Flashing
XVDLS6G7 | Main | mounting diameter | 45 mm
XVDLS6G7 | Main | component name | XVDLS
XVDLS6G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G7 | Main | light source | Integral flash discharge tube, clear
XVDLS6G7 | Main | bulb type | Flash discharge tube
XVDLS6G7 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G7 | Complementary | current consumption | < 35 mA AC
XVDLS6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G7 | Complementary | flash energy | 1 J
XVDLS6G7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6G7 | Complementary | CAD overall width | 45 mm
XVDLS6G7 | Complementary | CAD overall height | 104 mm
XVDLS6G7 | Complementary | CAD overall depth | 45 mm
XVDLS6G7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6G7 | Complementary | net weight | 0.085 kg
XVDLS6G7 | Environment | product certifications | CSA ¦ UL
XVDLS6G7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G7 | Environment | protective treatment | TC
XVDLS6G7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G7 | Contractual warranty | Warranty | 18 months
XVDLS6G8 | Main | range of product | Harmony XVD Optimum
XVDLS6G8 | Main | product or component type | Complete miniature beacon
XVDLS6G8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6G8 | Main | signalling type | Flashing
XVDLS6G8 | Main | mounting diameter | 45 mm
XVDLS6G8 | Main | component name | XVDLS
XVDLS6G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6G8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6G8 | Main | bulb type | Flash discharge tube
XVDLS6G8 | Main | [Us] rated supply voltage | 120 V AC
XVDLS6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6G8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6G8 | Complementary | current consumption | < 35 mA AC
XVDLS6G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6G8 | Complementary | flash energy | 1 J
XVDLS6G8 | Complementary | CAD overall width | 45 mm
XVDLS6G8 | Complementary | CAD overall height | 104 mm
XVDLS6G8 | Complementary | CAD overall depth | 45 mm
XVDLS6G8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6G8 | Complementary | net weight | 0.085 kg
XVDLS6G8 | Environment | product certifications | UL ¦ CSA
XVDLS6G8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6G8 | Environment | protective treatment | TC
XVDLS6G8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6G8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6G8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6G8 | Contractual warranty | Warranty | 18 months
XVDLS6M3 | Main | range of product | Harmony XVD Optimum
XVDLS6M3 | Main | product or component type | Complete miniature beacon
XVDLS6M3 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M3 | Main | signalling type | Flashing
XVDLS6M3 | Main | mounting diameter | 45 mm
XVDLS6M3 | Main | component name | XVDLS
XVDLS6M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M3 | Main | light source | Integral flash discharge tube, green
XVDLS6M3 | Main | bulb type | Flash discharge tube
XVDLS6M3 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M3 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M3 | Complementary | current consumption | < 25 mA AC
XVDLS6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M3 | Complementary | flash energy | 1 J
XVDLS6M3 | Complementary | CAD overall width | 45 mm
XVDLS6M3 | Complementary | CAD overall height | 104 mm
XVDLS6M3 | Complementary | CAD overall depth | 45 mm
XVDLS6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M3 | Complementary | net weight | 0.085 kg
XVDLS6M3 | Environment | product certifications | CSA ¦ UL
XVDLS6M3 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M3 | Environment | protective treatment | TC
XVDLS6M3 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M3 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M3 | Offer Sustainability | Mercury free | Yes
XVDLS6M3 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M3 | Contractual warranty | Warranty | 18 months
XVDLS6M5 | Main | range of product | Harmony XVD Optimum
XVDLS6M5 | Main | product or component type | Complete miniature beacon
XVDLS6M5 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M5 | Main | signalling type | Flashing
XVDLS6M5 | Main | mounting diameter | 45 mm
XVDLS6M5 | Main | component name | XVDLS
XVDLS6M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M5 | Main | light source | Integral flash discharge tube, orange
XVDLS6M5 | Main | bulb type | Flash discharge tube
XVDLS6M5 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M5 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M5 | Complementary | current consumption | < 25 mA AC
XVDLS6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDLS6M5 | Complementary | flash energy | 1 J
XVDLS6M5 | Complementary | CAD overall width | 45 mm
XVDLS6M5 | Complementary | CAD overall height | 104 mm
XVDLS6M5 | Complementary | CAD overall depth | 45 mm
XVDLS6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M5 | Complementary | net weight | 0.085 kg
XVDLS6M5 | Environment | product certifications | CSA ¦ UL
XVDLS6M5 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M5 | Environment | protective treatment | TC
XVDLS6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M5 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M5 | Offer Sustainability | Mercury free | Yes
XVDLS6M5 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M5 | Contractual warranty | Warranty | 18 months
XVDLS6M6 | Main | range of product | Harmony XVD Optimum
XVDLS6M6 | Main | product or component type | Complete miniature beacon
XVDLS6M6 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M6 | Main | signalling type | Flashing
XVDLS6M6 | Main | mounting diameter | 45 mm
XVDLS6M6 | Main | component name | XVDLS
XVDLS6M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M6 | Main | light source | Integral flash discharge tube, blue
XVDLS6M6 | Main | bulb type | Flash discharge tube
XVDLS6M6 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M6 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M6 | Complementary | current consumption | < 25 mA AC
XVDLS6M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M6 | Complementary | flash energy | 1 J
XVDLS6M6 | Complementary | CAD overall width | 45 mm
XVDLS6M6 | Complementary | CAD overall height | 104 mm
XVDLS6M6 | Complementary | CAD overall depth | 45 mm
XVDLS6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDLS6M6 | Complementary | net weight | 0.085 kg
XVDLS6M6 | Environment | product certifications | CSA ¦ UL
XVDLS6M6 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M6 | Environment | protective treatment | TC
XVDLS6M6 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M6 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M6 | Offer Sustainability | Mercury free | Yes
XVDLS6M6 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M6 | Contractual warranty | Warranty | 18 months
XVDLS6M7 | Main | range of product | Harmony XVD Optimum
XVDLS6M7 | Main | product or component type | Complete miniature beacon
XVDLS6M7 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M7 | Main | signalling type | Flashing
XVDLS6M7 | Main | mounting diameter | 45 mm
XVDLS6M7 | Main | component name | XVDLS
XVDLS6M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M7 | Main | light source | Integral flash discharge tube, clear
XVDLS6M7 | Main | bulb type | Flash discharge tube
XVDLS6M7 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M7 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M7 | Complementary | current consumption | < 25 mA AC
XVDLS6M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M7 | Complementary | flash energy | 1 J
XVDLS6M7 | Complementary | illuminating intensity | 1.4 cd
XVDLS6M7 | Complementary | CAD overall width | 45 mm
XVDLS6M7 | Complementary | CAD overall height | 104 mm
XVDLS6M7 | Complementary | CAD overall depth | 45 mm
XVDLS6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M7 | Complementary | net weight | 0.085 kg
XVDLS6M7 | Environment | product certifications | UL ¦ CSA
XVDLS6M7 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M7 | Environment | protective treatment | TC
XVDLS6M7 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M7 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M7 | Offer Sustainability | Mercury free | Yes
XVDLS6M7 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M7 | Contractual warranty | Warranty | 18 months
XVDLS6M8 | Main | range of product | Harmony XVD Optimum
XVDLS6M8 | Main | product or component type | Complete miniature beacon
XVDLS6M8 | Main | beacon or indicator bank unit type | Base unit direct fixing ¦ Illuminated unit
XVDLS6M8 | Main | signalling type | Flashing
XVDLS6M8 | Main | mounting diameter | 45 mm
XVDLS6M8 | Main | component name | XVDLS
XVDLS6M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDLS6M8 | Main | light source | Integral flash discharge tube, yellow
XVDLS6M8 | Main | bulb type | Flash discharge tube
XVDLS6M8 | Main | [Us] rated supply voltage | 230 V AC
XVDLS6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDLS6M8 | Complementary | cable entry | 1 entry tapped for Pg 7
XVDLS6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDLS6M8 | Complementary | current consumption | < 25 mA AC
XVDLS6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDLS6M8 | Complementary | flash energy | 1 J
XVDLS6M8 | Complementary | CAD overall width | 45 mm
XVDLS6M8 | Complementary | CAD overall height | 104 mm
XVDLS6M8 | Complementary | CAD overall depth | 45 mm
XVDLS6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDLS6M8 | Complementary | net weight | 0.085 kg
XVDLS6M8 | Environment | product certifications | CSA ¦ UL
XVDLS6M8 | Environment | standards | EN/IEC 60947-5-1
XVDLS6M8 | Environment | protective treatment | TC
XVDLS6M8 | Environment | ambient air temperature for storage | -40…70 °C
XVDLS6M8 | Environment | electrical shock protection class | Class II conforming to IEC 60536
XVDLS6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDLS6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVDLS6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVDLS6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVDLS6M8 | Offer Sustainability | Mercury free | Yes
XVDLS6M8 | Offer Sustainability | RoHS exemption information | Yes
XVDLS6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVDLS6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVDLS6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVDLS6M8 | Contractual warranty | Warranty | 18 months
XVDMR6 | Main | range of product | Harmony XVD Application
XVDMR6 | Main | product or component type | Complete pre-cabled beacon
XVDMR6 | Main | beacon or indicator bank unit type | 1 illuminated unit
XVDMR6 | Main | signalling type | Flashing
XVDMR6 | Main | component name | XVD
XVDMR6 | Main | light source | Flash discharge tube, red
XVDMR6 | Main | [Us] rated supply voltage | 230 V AC
XVDMR6 | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDMR6 | Complementary | mounting diameter | 70 mm
XVDMR6 | Complementary | flash energy | 5 J
XVDMR6 | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
XVDMR6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDMR6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDMR6 | Complementary | current consumption | < 105 mA AC
XVDMR6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDMR6 | Complementary | flashing frequency | 1 Hz
XVDMR6 | Complementary | net weight | 0.6 kg
XVDMR6 | Environment | standards | EN/IEC 60947-5-1
XVDMR6 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDMR6 | Environment | protective treatment | TC
XVDMR6 | Environment | ambient air temperature for operation | -25…50 °C
XVDMR6 | Environment | ambient air temperature for storage | -40…70 °C
XVDMR6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDMR6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDMR6 | Contractual warranty | Warranty | 18 months
XVDB2GR | Main | range of product | Harmony XVD Application
XVDB2GR | Main | product or component type | Complete pre-cabled indicator bank
XVDB2GR | Main | beacon or indicator bank unit type | 2 illuminated units
XVDB2GR | Main | component name | XVD
XVDB2GR | Main | light source | Green LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVDB2GR | Main | light block color | Green/red
XVDB2GR | Main | [Us] rated supply voltage | 24 V AC/DC
XVDB2GR | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover ¦ Polycarbonate: illuminated unit
XVDB2GR | Complementary | mounting diameter | 70 mm
XVDB2GR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
XVDB2GR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDB2GR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDB2GR | Complementary | current consumption | < 47 mA on LED unit
XVDB2GR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDB2GR | Complementary | net weight | 0.553 kg
XVDB2GR | Environment | standards | EN/IEC 60947-5-1
XVDB2GR | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDB2GR | Environment | protective treatment | TC
XVDB2GR | Environment | ambient air temperature for storage | -40…70 °C
XVDB2GR | Environment | ambient air temperature for operation | -25…50 °C
XVDB2GR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDB2GR | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDB2GR | Contractual warranty | Warranty | 18 months
XVDB2GAR | Main | range of product | Harmony XVD Application
XVDB2GAR | Main | product or component type | Complete pre-cabled indicator bank
XVDB2GAR | Main | beacon or indicator bank unit type | 3 illuminated units
XVDB2GAR | Main | component name | XVD
XVDB2GAR | Main | light source | Green LED with BA 15d base steady signalling ¦ Orange LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVDB2GAR | Main | light block color | Green/orange/red
XVDB2GAR | Main | [Us] rated supply voltage | 24 V AC/DC
XVDB2GAR | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover ¦ Polycarbonate: illuminated unit
XVDB2GAR | Complementary | mounting diameter | 70 mm
XVDB2GAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
XVDB2GAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDB2GAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDB2GAR | Complementary | current consumption | < 47 mA on LED unit
XVDB2GAR | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDB2GAR | Complementary | net weight | 0.698 kg
XVDB2GAR | Environment | standards | EN/IEC 60947-5-1
XVDB2GAR | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDB2GAR | Environment | protective treatment | TC
XVDB2GAR | Environment | ambient air temperature for storage | -40…70 °C
XVDB2GAR | Environment | ambient air temperature for operation | -25…50 °C
XVDB2GAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDB2GAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDB2GAR | Contractual warranty | Warranty | 18 months
XVDB1SGAR | Main | range of product | Harmony XVD Application
XVDB1SGAR | Main | product or component type | Complete pre-cabled indicator bank
XVDB1SGAR | Main | beacon or indicator bank unit type | 3 illuminated units + 1 audible buzzer unit
XVDB1SGAR | Main | component name | XVD
XVDB1SGAR | Main | light source | Green incandescent bulb with BA 15d base steady signalling <10 W ¦ Orange incandescent bulb with BA 15d base steady signalling <10 W ¦ Red incandescent bulb with BA 15d base steady signalling <10 W
XVDB1SGAR | Main | light block color | Green/orange/red
XVDB1SGAR | Main | [Us] rated supply voltage | 24 V AC/DC
XVDB1SGAR | Complementary | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: cover ¦ Polycarbonate: illuminated unit
XVDB1SGAR | Complementary | mounting diameter | 70 mm
XVDB1SGAR | Complementary | connections - terminals | Screw clamp terminals, 1 x 0.82 mm² with bared wire ends
XVDB1SGAR | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDB1SGAR | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDB1SGAR | Complementary | current consumption | < 20 mA on audible unit
XVDB1SGAR | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDB1SGAR | Complementary | fundamental frequency | 2.8 kHz
XVDB1SGAR | Complementary | net weight | 1.088 kg
XVDB1SGAR | Environment | standards | EN/IEC 60947-5-1
XVDB1SGAR | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDB1SGAR | Environment | protective treatment | TC
XVDB1SGAR | Environment | ambient air temperature for storage | -40…70 °C
XVDB1SGAR | Environment | ambient air temperature for operation | -25…70 °C
XVDB1SGAR | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDB1SGAR | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDB1SGAR | Environment | noise level | 70…90 dB at 1 m
XVDB1SGAR | Contractual warranty | Warranty | 18 months
XVDL33 | Main | range of product | Harmony XVD Application
XVDL33 | Main | product or component type | Beacon
XVDL33 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL33 | Main | signalling type | Steady
XVDL33 | Main | mounting diameter | 70 mm
XVDL33 | Main | component name | XVD
XVDL33 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL33 | Main | light source | Bulb not included, green
XVDL33 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL33 | Main | [Us] rated supply voltage | <= 250 V
XVDL33 | Main | maximum power dissipation in W | 10 W
XVDL33 | Complementary | assembly style | Customer assembly
XVDL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL33 | Complementary | CAD overall width | 70 mm
XVDL33 | Complementary | CAD overall height | 133 mm
XVDL33 | Complementary | CAD overall depth | 70 mm
XVDL33 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL33 | Complementary | net weight | 0.255 kg
XVDL33 | Environment | pollution degree | 2
XVDL33 | Environment | product certifications | CSA ¦ GOST ¦ UL
XVDL33 | Environment | standards | EN/IEC 60947-5-1
XVDL33 | Environment | protective treatment | TC
XVDL33 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL33 | Environment | ambient air temperature for storage | -40…70 °C
XVDL33 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL33 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL33 | Contractual warranty | Warranty | 18 months
XVDL34 | Main | range of product | Harmony XVD Application
XVDL34 | Main | product or component type | Beacon
XVDL34 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL34 | Main | signalling type | Steady
XVDL34 | Main | mounting diameter | 70 mm
XVDL34 | Main | component name | XVD
XVDL34 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL34 | Main | light source | Bulb not included, red
XVDL34 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL34 | Main | [Us] rated supply voltage | <= 250 V
XVDL34 | Main | maximum power dissipation in W | 10 W
XVDL34 | Complementary | assembly style | Customer assembly
XVDL34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL34 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL34 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL34 | Complementary | CAD overall width | 70 mm
XVDL34 | Complementary | CAD overall height | 133 mm
XVDL34 | Complementary | CAD overall depth | 70 mm
XVDL34 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL34 | Complementary | net weight | 0.255 kg
XVDL34 | Environment | pollution degree | 2
XVDL34 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL34 | Environment | standards | EN/IEC 60947-5-1
XVDL34 | Environment | protective treatment | TC
XVDL34 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL34 | Environment | ambient air temperature for storage | -40…70 °C
XVDL34 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL34 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL34 | Contractual warranty | Warranty | 18 months
XVDL35 | Main | range of product | Harmony XVD Application
XVDL35 | Main | product or component type | Beacon
XVDL35 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL35 | Main | signalling type | Steady
XVDL35 | Main | mounting diameter | 70 mm
XVDL35 | Main | component name | XVD
XVDL35 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL35 | Main | light source | Bulb not included, orange
XVDL35 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL35 | Main | [Us] rated supply voltage | <= 250 V
XVDL35 | Main | maximum power dissipation in W | 10 W
XVDL35 | Complementary | assembly style | Customer assembly
XVDL35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL35 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL35 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL35 | Complementary | CAD overall width | 70 mm
XVDL35 | Complementary | CAD overall height | 133 mm
XVDL35 | Complementary | CAD overall depth | 70 mm
XVDL35 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL35 | Complementary | net weight | 0.255 kg
XVDL35 | Environment | pollution degree | 2
XVDL35 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL35 | Environment | standards | EN/IEC 60947-5-1
XVDL35 | Environment | protective treatment | TC
XVDL35 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL35 | Environment | ambient air temperature for storage | -40…70 °C
XVDL35 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL35 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL35 | Contractual warranty | Warranty | 18 months
XVDL36 | Main | range of product | Harmony XVD Application
XVDL36 | Main | product or component type | Beacon
XVDL36 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL36 | Main | signalling type | Steady
XVDL36 | Main | mounting diameter | 70 mm
XVDL36 | Main | component name | XVD
XVDL36 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL36 | Main | light source | Bulb not included, blue
XVDL36 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL36 | Main | [Us] rated supply voltage | <= 250 V
XVDL36 | Main | maximum power dissipation in W | 10 W
XVDL36 | Complementary | assembly style | Customer assembly
XVDL36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL36 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL36 | Complementary | CAD overall width | 70 mm
XVDL36 | Complementary | CAD overall height | 133 mm
XVDL36 | Complementary | CAD overall depth | 70 mm
XVDL36 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL36 | Complementary | net weight | 0.255 kg
XVDL36 | Environment | pollution degree | 2
XVDL36 | Environment | product certifications | GOST ¦ UL ¦ CSA
XVDL36 | Environment | standards | EN/IEC 60947-5-1
XVDL36 | Environment | protective treatment | TC
XVDL36 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL36 | Environment | ambient air temperature for storage | -40…70 °C
XVDL36 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL36 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL36 | Contractual warranty | Warranty | 18 months
XVDL37 | Main | range of product | Harmony XVD Application
XVDL37 | Main | product or component type | Beacon
XVDL37 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL37 | Main | signalling type | Steady
XVDL37 | Main | mounting diameter | 70 mm
XVDL37 | Main | component name | XVD
XVDL37 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL37 | Main | light source | Bulb not included, clear
XVDL37 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL37 | Main | [Us] rated supply voltage | <= 250 V
XVDL37 | Main | maximum power dissipation in W | 10 W
XVDL37 | Complementary | assembly style | Customer assembly
XVDL37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL37 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL37 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL37 | Complementary | CAD overall width | 70 mm
XVDL37 | Complementary | CAD overall height | 133 mm
XVDL37 | Complementary | CAD overall depth | 70 mm
XVDL37 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL37 | Complementary | net weight | 0.255 kg
XVDL37 | Environment | pollution degree | 2
XVDL37 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL37 | Environment | standards | EN/IEC 60947-5-1
XVDL37 | Environment | protective treatment | TC
XVDL37 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL37 | Environment | ambient air temperature for storage | -40…70 °C
XVDL37 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL37 | Contractual warranty | Warranty | 18 months
XVDL38 | Main | range of product | Harmony XVD Application
XVDL38 | Main | product or component type | Beacon
XVDL38 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL38 | Main | signalling type | Steady
XVDL38 | Main | mounting diameter | 70 mm
XVDL38 | Main | component name | XVD
XVDL38 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL38 | Main | light source | Bulb not included, yellow
XVDL38 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL38 | Main | [Us] rated supply voltage | <= 250 V
XVDL38 | Main | maximum power dissipation in W | 10 W
XVDL38 | Complementary | assembly style | Customer assembly
XVDL38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL38 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL38 | Complementary | CAD overall width | 70 mm
XVDL38 | Complementary | CAD overall height | 133 mm
XVDL38 | Complementary | CAD overall depth | 70 mm
XVDL38 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL38 | Complementary | net weight | 0.255 kg
XVDL38 | Environment | pollution degree | 2
XVDL38 | Environment | product certifications | GOST ¦ UL ¦ CSA
XVDL38 | Environment | standards | EN/IEC 60947-5-1
XVDL38 | Environment | protective treatment | TC
XVDL38 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVDL38 | Environment | ambient air temperature for storage | -40…70 °C
XVDL38 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL38 | Contractual warranty | Warranty | 18 months
XVDL4B3 | Main | range of product | Harmony XVD Application
XVDL4B3 | Main | product or component type | Beacon
XVDL4B3 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B3 | Main | signalling type | Flashing
XVDL4B3 | Main | mounting diameter | 70 mm
XVDL4B3 | Main | component name | XVD
XVDL4B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B3 | Main | light source | Bulb not included, green
XVDL4B3 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B3 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B3 | Main | maximum power dissipation in W | 10 W
XVDL4B3 | Complementary | assembly style | Customer assembly
XVDL4B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B3 | Complementary | flashing frequency | 1 Hz
XVDL4B3 | Complementary | CAD overall width | 70 mm
XVDL4B3 | Complementary | CAD overall height | 133 mm
XVDL4B3 | Complementary | CAD overall depth | 70 mm
XVDL4B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL4B3 | Complementary | net weight | 0.275 kg
XVDL4B3 | Environment | pollution degree | 2
XVDL4B3 | Environment | product certifications | GOST ¦ UL ¦ CSA
XVDL4B3 | Environment | standards | EN/IEC 60947-5-1
XVDL4B3 | Environment | protective treatment | TC
XVDL4B3 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B3 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B3 | Contractual warranty | Warranty | 18 months
XVDL4B4 | Main | range of product | Harmony XVD Application
XVDL4B4 | Main | product or component type | Beacon
XVDL4B4 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B4 | Main | signalling type | Flashing
XVDL4B4 | Main | mounting diameter | 70 mm
XVDL4B4 | Main | component name | XVD
XVDL4B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B4 | Main | light source | Bulb not included, red
XVDL4B4 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B4 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B4 | Main | maximum power dissipation in W | 10 W
XVDL4B4 | Complementary | assembly style | Customer assembly
XVDL4B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B4 | Complementary | flashing frequency | 1 Hz
XVDL4B4 | Complementary | CAD overall width | 70 mm
XVDL4B4 | Complementary | CAD overall height | 133 mm
XVDL4B4 | Complementary | CAD overall depth | 70 mm
XVDL4B4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL4B4 | Complementary | net weight | 0.275 kg
XVDL4B4 | Environment | pollution degree | 2
XVDL4B4 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL4B4 | Environment | standards | EN/IEC 60947-5-1
XVDL4B4 | Environment | protective treatment | TC
XVDL4B4 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B4 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B4 | Contractual warranty | Warranty | 18 months
XVDL4B5 | Main | range of product | Harmony XVD Application
XVDL4B5 | Main | product or component type | Beacon
XVDL4B5 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B5 | Main | signalling type | Flashing
XVDL4B5 | Main | mounting diameter | 70 mm
XVDL4B5 | Main | component name | XVD
XVDL4B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B5 | Main | light source | Bulb not included, orange
XVDL4B5 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B5 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B5 | Main | maximum power dissipation in W | 10 W
XVDL4B5 | Complementary | assembly style | Customer assembly
XVDL4B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B5 | Complementary | flashing frequency | 1 Hz
XVDL4B5 | Complementary | CAD overall width | 70 mm
XVDL4B5 | Complementary | CAD overall height | 133 mm
XVDL4B5 | Complementary | CAD overall depth | 70 mm
XVDL4B5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4B5 | Complementary | net weight | 0.275 kg
XVDL4B5 | Environment | pollution degree | 2
XVDL4B5 | Environment | product certifications | UL ¦ GOST ¦ CSA
XVDL4B5 | Environment | standards | EN/IEC 60947-5-1
XVDL4B5 | Environment | protective treatment | TC
XVDL4B5 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B5 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B5 | Contractual warranty | Warranty | 18 months
XVDL4B6 | Main | range of product | Harmony XVD Application
XVDL4B6 | Main | product or component type | Beacon
XVDL4B6 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B6 | Main | signalling type | Flashing
XVDL4B6 | Main | mounting diameter | 70 mm
XVDL4B6 | Main | component name | XVD
XVDL4B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B6 | Main | light source | Bulb not included, blue
XVDL4B6 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B6 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B6 | Main | maximum power dissipation in W | 10 W
XVDL4B6 | Complementary | assembly style | Customer assembly
XVDL4B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B6 | Complementary | flashing frequency | 1 Hz
XVDL4B6 | Complementary | CAD overall width | 70 mm
XVDL4B6 | Complementary | CAD overall height | 133 mm
XVDL4B6 | Complementary | CAD overall depth | 70 mm
XVDL4B6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4B6 | Complementary | net weight | 0.275 kg
XVDL4B6 | Environment | pollution degree | 2
XVDL4B6 | Environment | product certifications | CSA ¦ GOST ¦ UL
XVDL4B6 | Environment | standards | EN/IEC 60947-5-1
XVDL4B6 | Environment | protective treatment | TC
XVDL4B6 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B6 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B6 | Contractual warranty | Warranty | 18 months
XVDL4B7 | Main | range of product | Harmony XVD Application
XVDL4B7 | Main | product or component type | Beacon
XVDL4B7 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B7 | Main | signalling type | Flashing
XVDL4B7 | Main | mounting diameter | 70 mm
XVDL4B7 | Main | component name | XVD
XVDL4B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B7 | Main | light source | Bulb not included, clear
XVDL4B7 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B7 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B7 | Main | maximum power dissipation in W | 10 W
XVDL4B7 | Complementary | assembly style | Customer assembly
XVDL4B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B7 | Complementary | flashing frequency | 1 Hz
XVDL4B7 | Complementary | CAD overall width | 70 mm
XVDL4B7 | Complementary | CAD overall height | 133 mm
XVDL4B7 | Complementary | CAD overall depth | 70 mm
XVDL4B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4B7 | Complementary | net weight | 0.275 kg
XVDL4B7 | Environment | pollution degree | 2
XVDL4B7 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDL4B7 | Environment | standards | EN/IEC 60947-5-1
XVDL4B7 | Environment | protective treatment | TC
XVDL4B7 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B7 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B7 | Contractual warranty | Warranty | 18 months
XVDL4B8 | Main | range of product | Harmony XVD Application
XVDL4B8 | Main | product or component type | Beacon
XVDL4B8 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4B8 | Main | signalling type | Flashing
XVDL4B8 | Main | mounting diameter | 70 mm
XVDL4B8 | Main | component name | XVD
XVDL4B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4B8 | Main | light source | Bulb not included, yellow
XVDL4B8 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVDL4B8 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVDL4B8 | Main | maximum power dissipation in W | 10 W
XVDL4B8 | Complementary | assembly style | Customer assembly
XVDL4B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4B8 | Complementary | flashing frequency | 1 Hz
XVDL4B8 | Complementary | CAD overall width | 70 mm
XVDL4B8 | Complementary | CAD overall height | 133 mm
XVDL4B8 | Complementary | CAD overall depth | 70 mm
XVDL4B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4B8 | Complementary | net weight | 0.275 kg
XVDL4B8 | Environment | pollution degree | 2
XVDL4B8 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL4B8 | Environment | standards | EN/IEC 60947-5-1
XVDL4B8 | Environment | protective treatment | TC
XVDL4B8 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4B8 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4B8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4B8 | Contractual warranty | Warranty | 18 months
XVDL4M3 | Main | range of product | Harmony XVD Application
XVDL4M3 | Main | product or component type | Beacon
XVDL4M3 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M3 | Main | signalling type | Flashing
XVDL4M3 | Main | mounting diameter | 70 mm
XVDL4M3 | Main | component name | XVD
XVDL4M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M3 | Main | light source | Bulb not included, green
XVDL4M3 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M3 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M3 | Main | maximum power dissipation in W | 10 W
XVDL4M3 | Complementary | assembly style | Customer assembly
XVDL4M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4M3 | Complementary | flashing frequency | 1 Hz
XVDL4M3 | Complementary | CAD overall width | 70 mm
XVDL4M3 | Complementary | CAD overall height | 133 mm
XVDL4M3 | Complementary | CAD overall depth | 70 mm
XVDL4M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL4M3 | Complementary | net weight | 0.275 kg
XVDL4M3 | Environment | pollution degree | 2
XVDL4M3 | Environment | product certifications | UL ¦ GOST ¦ CSA
XVDL4M3 | Environment | standards | EN/IEC 60947-5-1
XVDL4M3 | Environment | protective treatment | TC
XVDL4M3 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M3 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M3 | Contractual warranty | Warranty | 18 months
XVDL4M4 | Main | range of product | Harmony XVD Application
XVDL4M4 | Main | product or component type | Beacon
XVDL4M4 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M4 | Main | signalling type | Flashing
XVDL4M4 | Main | mounting diameter | 70 mm
XVDL4M4 | Main | component name | XVD
XVDL4M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M4 | Main | light source | Bulb not included, red
XVDL4M4 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M4 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M4 | Main | maximum power dissipation in W | 10 W
XVDL4M4 | Complementary | assembly style | Customer assembly
XVDL4M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4M4 | Complementary | flashing frequency | 1 Hz
XVDL4M4 | Complementary | CAD overall width | 70 mm
XVDL4M4 | Complementary | CAD overall height | 133 mm
XVDL4M4 | Complementary | CAD overall depth | 70 mm
XVDL4M4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL4M4 | Complementary | net weight | 0.275 kg
XVDL4M4 | Environment | pollution degree | 2
XVDL4M4 | Environment | product certifications | UL ¦ GOST ¦ CSA
XVDL4M4 | Environment | standards | EN/IEC 60947-5-1
XVDL4M4 | Environment | protective treatment | TC
XVDL4M4 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M4 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M4 | Contractual warranty | Warranty | 18 months
XVDL4M5 | Main | range of product | Harmony XVD Application
XVDL4M5 | Main | product or component type | Beacon
XVDL4M5 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M5 | Main | signalling type | Flashing
XVDL4M5 | Main | mounting diameter | 70 mm
XVDL4M5 | Main | component name | XVD
XVDL4M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M5 | Main | light source | Bulb not included, orange
XVDL4M5 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M5 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M5 | Main | maximum power dissipation in W | 10 W
XVDL4M5 | Complementary | assembly style | Customer assembly
XVDL4M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4M5 | Complementary | flashing frequency | 1 Hz
XVDL4M5 | Complementary | CAD overall width | 70 mm
XVDL4M5 | Complementary | CAD overall height | 133 mm
XVDL4M5 | Complementary | CAD overall depth | 70 mm
XVDL4M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL4M5 | Complementary | net weight | 0.275 kg
XVDL4M5 | Environment | pollution degree | 2
XVDL4M5 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDL4M5 | Environment | standards | EN/IEC 60947-5-1
XVDL4M5 | Environment | protective treatment | TC
XVDL4M5 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M5 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M5 | Contractual warranty | Warranty | 18 months
XVDL4M6 | Main | range of product | Harmony XVD Application
XVDL4M6 | Main | product or component type | Beacon
XVDL4M6 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M6 | Main | signalling type | Flashing
XVDL4M6 | Main | mounting diameter | 70 mm
XVDL4M6 | Main | component name | XVD
XVDL4M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M6 | Main | light source | Bulb not included, blue
XVDL4M6 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M6 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M6 | Main | maximum power dissipation in W | 10 W
XVDL4M6 | Complementary | assembly style | Customer assembly
XVDL4M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4M6 | Complementary | flashing frequency | 1 Hz
XVDL4M6 | Complementary | CAD overall width | 70 mm
XVDL4M6 | Complementary | CAD overall height | 133 mm
XVDL4M6 | Complementary | CAD overall depth | 70 mm
XVDL4M6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4M6 | Complementary | net weight | 0.275 kg
XVDL4M6 | Environment | pollution degree | 2
XVDL4M6 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDL4M6 | Environment | standards | EN/IEC 60947-5-1
XVDL4M6 | Environment | protective treatment | TC
XVDL4M6 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M6 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M6 | Contractual warranty | Warranty | 18 months
XVDL4M7 | Main | range of product | Harmony XVD Application
XVDL4M7 | Main | product or component type | Beacon
XVDL4M7 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M7 | Main | signalling type | Flashing
XVDL4M7 | Main | mounting diameter | 70 mm
XVDL4M7 | Main | component name | XVD
XVDL4M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M7 | Main | light source | Bulb not included, clear
XVDL4M7 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M7 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M7 | Main | maximum power dissipation in W | 10 W
XVDL4M7 | Complementary | assembly style | Customer assembly
XVDL4M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL4M7 | Complementary | flashing frequency | 1 Hz
XVDL4M7 | Complementary | CAD overall width | 70 mm
XVDL4M7 | Complementary | CAD overall height | 133 mm
XVDL4M7 | Complementary | CAD overall depth | 70 mm
XVDL4M7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4M7 | Complementary | net weight | 0.275 kg
XVDL4M7 | Environment | pollution degree | 2
XVDL4M7 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL4M7 | Environment | standards | EN/IEC 60947-5-1
XVDL4M7 | Environment | protective treatment | TC
XVDL4M7 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M7 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M7 | Contractual warranty | Warranty | 18 months
XVDL4M8 | Main | range of product | Harmony XVD Application
XVDL4M8 | Main | product or component type | Beacon
XVDL4M8 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL4M8 | Main | signalling type | Flashing
XVDL4M8 | Main | mounting diameter | 70 mm
XVDL4M8 | Main | component name | XVD
XVDL4M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL4M8 | Main | light source | Bulb not included, yellow
XVDL4M8 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVDL4M8 | Main | [Us] rated supply voltage | 48...230 V AC
XVDL4M8 | Main | maximum power dissipation in W | 10 W
XVDL4M8 | Complementary | assembly style | Customer assembly
XVDL4M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL4M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL4M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL4M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL4M8 | Complementary | flashing frequency | 1 Hz
XVDL4M8 | Complementary | CAD overall width | 70 mm
XVDL4M8 | Complementary | CAD overall height | 133 mm
XVDL4M8 | Complementary | CAD overall depth | 70 mm
XVDL4M8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL4M8 | Complementary | net weight | 0.275 kg
XVDL4M8 | Environment | pollution degree | 2
XVDL4M8 | Environment | product certifications | UL ¦ GOST ¦ CSA
XVDL4M8 | Environment | standards | EN/IEC 60947-5-1
XVDL4M8 | Environment | protective treatment | TC
XVDL4M8 | Environment | ambient air temperature for operation | -25…40 °C: incandescent ¦ -25…50 °C: LED
XVDL4M8 | Environment | ambient air temperature for storage | -40…70 °C
XVDL4M8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL4M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL4M8 | Contractual warranty | Warranty | 18 months
XVDL6B3 | Main | range of product | Harmony XVD Application
XVDL6B3 | Main | product or component type | Beacon
XVDL6B3 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B3 | Main | signalling type | Flashing
XVDL6B3 | Main | mounting diameter | 70 mm
XVDL6B3 | Main | component name | XVD
XVDL6B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B3 | Main | light source | Integral flash discharge tube, green
XVDL6B3 | Main | bulb type | Flash discharge tube
XVDL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B3 | Complementary | assembly style | Customer assembly
XVDL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B3 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL6B3 | Complementary | flash energy | 5 J
XVDL6B3 | Complementary | flashing frequency | 1 Hz
XVDL6B3 | Complementary | CAD overall width | 70 mm
XVDL6B3 | Complementary | CAD overall height | 245 mm
XVDL6B3 | Complementary | CAD overall depth | 70 mm
XVDL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6B3 | Complementary | net weight | 0.48 kg
XVDL6B3 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL6B3 | Environment | standards | EN/IEC 60947-5-1
XVDL6B3 | Environment | protective treatment | TC
XVDL6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B3 | Contractual warranty | Warranty | 18 months
XVDL6B4 | Main | range of product | Harmony XVD Application
XVDL6B4 | Main | product or component type | Beacon
XVDL6B4 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B4 | Main | signalling type | Flashing
XVDL6B4 | Main | mounting diameter | 70 mm
XVDL6B4 | Main | component name | XVD
XVDL6B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B4 | Main | light source | Integral flash discharge tube, red
XVDL6B4 | Main | bulb type | Flash discharge tube
XVDL6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B4 | Complementary | assembly style | Customer assembly
XVDL6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B4 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6B4 | Complementary | flash energy | 5 J
XVDL6B4 | Complementary | flashing frequency | 1 Hz
XVDL6B4 | Complementary | CAD overall width | 70 mm
XVDL6B4 | Complementary | CAD overall height | 245 mm
XVDL6B4 | Complementary | CAD overall depth | 70 mm
XVDL6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6B4 | Complementary | net weight | 0.48 kg
XVDL6B4 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL6B4 | Environment | standards | EN/IEC 60947-5-1
XVDL6B4 | Environment | protective treatment | TC
XVDL6B4 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B4 | Contractual warranty | Warranty | 18 months
XVDL6B5 | Main | range of product | Harmony XVD Application
XVDL6B5 | Main | product or component type | Beacon
XVDL6B5 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B5 | Main | signalling type | Flashing
XVDL6B5 | Main | mounting diameter | 70 mm
XVDL6B5 | Main | component name | XVD
XVDL6B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B5 | Main | light source | Integral flash discharge tube, orange
XVDL6B5 | Main | bulb type | Flash discharge tube
XVDL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B5 | Complementary | assembly style | Customer assembly
XVDL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B5 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6B5 | Complementary | flash energy | 5 J
XVDL6B5 | Complementary | flashing frequency | 1 Hz
XVDL6B5 | Complementary | CAD overall width | 70 mm
XVDL6B5 | Complementary | CAD overall height | 245 mm
XVDL6B5 | Complementary | CAD overall depth | 70 mm
XVDL6B5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6B5 | Complementary | net weight | 0.48 kg
XVDL6B5 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL6B5 | Environment | standards | EN/IEC 60947-5-1
XVDL6B5 | Environment | protective treatment | TC
XVDL6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B5 | Contractual warranty | Warranty | 18 months
XVDL6B6 | Main | range of product | Harmony XVD Application
XVDL6B6 | Main | product or component type | Beacon
XVDL6B6 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B6 | Main | signalling type | Flashing
XVDL6B6 | Main | mounting diameter | 70 mm
XVDL6B6 | Main | component name | XVD
XVDL6B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B6 | Main | light source | Integral flash discharge tube, blue
XVDL6B6 | Main | bulb type | Flash discharge tube
XVDL6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B6 | Complementary | assembly style | Customer assembly
XVDL6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B6 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6B6 | Complementary | flash energy | 5 J
XVDL6B6 | Complementary | flashing frequency | 1 Hz
XVDL6B6 | Complementary | CAD overall width | 70 mm
XVDL6B6 | Complementary | CAD overall height | 245 mm
XVDL6B6 | Complementary | CAD overall depth | 70 mm
XVDL6B6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6B6 | Complementary | net weight | 0.48 kg
XVDL6B6 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDL6B6 | Environment | standards | EN/IEC 60947-5-1
XVDL6B6 | Environment | protective treatment | TC
XVDL6B6 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B6 | Contractual warranty | Warranty | 18 months
XVDL6B7 | Main | range of product | Harmony XVD Application
XVDL6B7 | Main | product or component type | Beacon
XVDL6B7 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B7 | Main | signalling type | Flashing
XVDL6B7 | Main | mounting diameter | 70 mm
XVDL6B7 | Main | component name | XVD
XVDL6B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B7 | Main | light source | Integral flash discharge tube, clear
XVDL6B7 | Main | bulb type | Flash discharge tube
XVDL6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B7 | Complementary | assembly style | Customer assembly
XVDL6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B7 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL6B7 | Complementary | flash energy | 5 J
XVDL6B7 | Complementary | flashing frequency | 1 Hz
XVDL6B7 | Complementary | illuminating intensity | 13 cd
XVDL6B7 | Complementary | CAD overall width | 70 mm
XVDL6B7 | Complementary | CAD overall height | 245 mm
XVDL6B7 | Complementary | CAD overall depth | 70 mm
XVDL6B7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6B7 | Complementary | net weight | 0.48 kg
XVDL6B7 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL6B7 | Environment | standards | EN/IEC 60947-5-1
XVDL6B7 | Environment | protective treatment | TC
XVDL6B7 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B7 | Contractual warranty | Warranty | 18 months
XVDL6B8 | Main | range of product | Harmony XVD Application
XVDL6B8 | Main | product or component type | Beacon
XVDL6B8 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6B8 | Main | signalling type | Flashing
XVDL6B8 | Main | mounting diameter | 70 mm
XVDL6B8 | Main | component name | XVD
XVDL6B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6B8 | Main | light source | Integral flash discharge tube, yellow
XVDL6B8 | Main | bulb type | Flash discharge tube
XVDL6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVDL6B8 | Complementary | assembly style | Customer assembly
XVDL6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6B8 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVDL6B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6B8 | Complementary | flash energy | 5 J
XVDL6B8 | Complementary | flashing frequency | 1 Hz
XVDL6B8 | Complementary | CAD overall width | 70 mm
XVDL6B8 | Complementary | CAD overall height | 245 mm
XVDL6B8 | Complementary | CAD overall depth | 70 mm
XVDL6B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6B8 | Complementary | net weight | 0.48 kg
XVDL6B8 | Environment | product certifications | GOST ¦ UL ¦ CSA
XVDL6B8 | Environment | standards | EN/IEC 60947-5-1
XVDL6B8 | Environment | protective treatment | TC
XVDL6B8 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6B8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6B8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6B8 | Contractual warranty | Warranty | 18 months
XVDL6M3 | Main | range of product | Harmony XVD Application
XVDL6M3 | Main | product or component type | Beacon
XVDL6M3 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M3 | Main | signalling type | Flashing
XVDL6M3 | Main | mounting diameter | 70 mm
XVDL6M3 | Main | component name | XVD
XVDL6M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M3 | Main | light source | Integral flash discharge tube, green
XVDL6M3 | Main | bulb type | Flash discharge tube
XVDL6M3 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M3 | Complementary | assembly style | Customer assembly
XVDL6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M3 | Complementary | current consumption | < 105 mA AC
XVDL6M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL6M3 | Complementary | flash energy | 5 J
XVDL6M3 | Complementary | flashing frequency | 1 Hz
XVDL6M3 | Complementary | CAD overall width | 70 mm
XVDL6M3 | Complementary | CAD overall height | 245 mm
XVDL6M3 | Complementary | CAD overall depth | 70 mm
XVDL6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6M3 | Complementary | net weight | 0.475 kg
XVDL6M3 | Environment | product certifications | GOST ¦ UL ¦ CSA
XVDL6M3 | Environment | standards | EN/IEC 60947-5-1
XVDL6M3 | Environment | protective treatment | TC
XVDL6M3 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M3 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M3 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M3 | Contractual warranty | Warranty | 18 months
XVDL6M4 | Main | range of product | Harmony XVD Application
XVDL6M4 | Main | product or component type | Beacon
XVDL6M4 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M4 | Main | signalling type | Flashing
XVDL6M4 | Main | mounting diameter | 70 mm
XVDL6M4 | Main | component name | XVD
XVDL6M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M4 | Main | light source | Integral flash discharge tube, red
XVDL6M4 | Main | bulb type | Flash discharge tube
XVDL6M4 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M4 | Complementary | assembly style | Customer assembly
XVDL6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M4 | Complementary | current consumption | < 105 mA AC
XVDL6M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6M4 | Complementary | flash energy | 5 J
XVDL6M4 | Complementary | flashing frequency | 1 Hz
XVDL6M4 | Complementary | CAD overall width | 70 mm
XVDL6M4 | Complementary | CAD overall height | 245 mm
XVDL6M4 | Complementary | CAD overall depth | 70 mm
XVDL6M4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6M4 | Complementary | net weight | 0.475 kg
XVDL6M4 | Environment | product certifications | UL ¦ CSA ¦ GOST
XVDL6M4 | Environment | standards | EN/IEC 60947-5-1
XVDL6M4 | Environment | protective treatment | TC
XVDL6M4 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M4 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M4 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M4 | Contractual warranty | Warranty | 18 months
XVDL6M5 | Main | range of product | Harmony XVD Application
XVDL6M5 | Main | product or component type | Beacon
XVDL6M5 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M5 | Main | signalling type | Flashing
XVDL6M5 | Main | mounting diameter | 70 mm
XVDL6M5 | Main | component name | XVD
XVDL6M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M5 | Main | light source | Integral flash discharge tube, orange
XVDL6M5 | Main | bulb type | Flash discharge tube
XVDL6M5 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M5 | Complementary | assembly style | Customer assembly
XVDL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M5 | Complementary | current consumption | < 105 mA AC
XVDL6M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVDL6M5 | Complementary | flash energy | 5 J
XVDL6M5 | Complementary | flashing frequency | 1 Hz
XVDL6M5 | Complementary | CAD overall width | 70 mm
XVDL6M5 | Complementary | CAD overall height | 245 mm
XVDL6M5 | Complementary | CAD overall depth | 70 mm
XVDL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVDL6M5 | Complementary | net weight | 0.475 kg
XVDL6M5 | Environment | product certifications | UL ¦ GOST ¦ CSA
XVDL6M5 | Environment | standards | EN/IEC 60947-5-1
XVDL6M5 | Environment | protective treatment | TC
XVDL6M5 | Environment | ambient air temperature for operation | -25…50 °C
XVDL6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M5 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M5 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M5 | Contractual warranty | Warranty | 18 months
XVDL6M6 | Main | range of product | Harmony XVD Application
XVDL6M6 | Main | product or component type | Beacon
XVDL6M6 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M6 | Main | signalling type | Flashing
XVDL6M6 | Main | mounting diameter | 70 mm
XVDL6M6 | Main | component name | XVD
XVDL6M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M6 | Main | light source | Integral flash discharge tube, blue
XVDL6M6 | Main | bulb type | Flash discharge tube
XVDL6M6 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M6 | Complementary | assembly style | Customer assembly
XVDL6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M6 | Complementary | current consumption | < 105 mA AC
XVDL6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6M6 | Complementary | flash energy | 5 J
XVDL6M6 | Complementary | flashing frequency | 1 Hz
XVDL6M6 | Complementary | CAD overall width | 70 mm
XVDL6M6 | Complementary | CAD overall height | 245 mm
XVDL6M6 | Complementary | CAD overall depth | 70 mm
XVDL6M6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6M6 | Complementary | net weight | 0.475 kg
XVDL6M6 | Environment | product certifications | CSA ¦ UL ¦ GOST
XVDL6M6 | Environment | standards | EN/IEC 60947-5-1
XVDL6M6 | Environment | protective treatment | TC
XVDL6M6 | Environment | ambient air temperature for operation | -25…50 °C
XVDL6M6 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M6 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M6 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M6 | Contractual warranty | Warranty | 18 months
XVDL6M7 | Main | range of product | Harmony XVD Application
XVDL6M7 | Main | product or component type | Beacon
XVDL6M7 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M7 | Main | signalling type | Flashing
XVDL6M7 | Main | mounting diameter | 70 mm
XVDL6M7 | Main | component name | XVD
XVDL6M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M7 | Main | light source | Integral flash discharge tube, clear
XVDL6M7 | Main | bulb type | Flash discharge tube
XVDL6M7 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M7 | Complementary | assembly style | Customer assembly
XVDL6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M7 | Complementary | current consumption | < 105 mA AC
XVDL6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6M7 | Complementary | flash energy | 5 J
XVDL6M7 | Complementary | flashing frequency | 1 Hz
XVDL6M7 | Complementary | illuminating intensity | 13 cd
XVDL6M7 | Complementary | CAD overall width | 70 mm
XVDL6M7 | Complementary | CAD overall height | 245 mm
XVDL6M7 | Complementary | CAD overall depth | 70 mm
XVDL6M7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6M7 | Complementary | net weight | 0.475 kg
XVDL6M7 | Environment | product certifications | CSA ¦ GOST ¦ UL
XVDL6M7 | Environment | standards | EN/IEC 60947-5-1
XVDL6M7 | Environment | protective treatment | TC
XVDL6M7 | Environment | ambient air temperature for operation | -25…50 °C
XVDL6M7 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M7 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M7 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M7 | Contractual warranty | Warranty | 18 months
XVDL6M8 | Main | range of product | Harmony XVD Application
XVDL6M8 | Main | product or component type | Beacon
XVDL6M8 | Main | beacon or indicator bank unit type | Base unit ¦ Illuminated unit
XVDL6M8 | Main | signalling type | Flashing
XVDL6M8 | Main | mounting diameter | 70 mm
XVDL6M8 | Main | component name | XVD
XVDL6M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVDL6M8 | Main | light source | Integral flash discharge tube, yellow
XVDL6M8 | Main | bulb type | Flash discharge tube
XVDL6M8 | Main | [Us] rated supply voltage | 230 V AC
XVDL6M8 | Complementary | assembly style | Customer assembly
XVDL6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVDL6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVDL6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVDL6M8 | Complementary | current consumption | < 105 mA AC
XVDL6M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVDL6M8 | Complementary | flash energy | 5 J
XVDL6M8 | Complementary | flashing frequency | 1 Hz
XVDL6M8 | Complementary | CAD overall width | 70 mm
XVDL6M8 | Complementary | CAD overall height | 245 mm
XVDL6M8 | Complementary | CAD overall depth | 70 mm
XVDL6M8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVDL6M8 | Complementary | net weight | 0.475 kg
XVDL6M8 | Environment | product certifications | GOST ¦ CSA ¦ UL
XVDL6M8 | Environment | standards | EN/IEC 60947-5-1
XVDL6M8 | Environment | protective treatment | TC
XVDL6M8 | Environment | ambient air temperature for operation | -25…50 °C
XVDL6M8 | Environment | ambient air temperature for storage | -40…70 °C
XVDL6M8 | Environment | electrical shock protection class | Class I on support tube, with metal fixing plate conforming to IEC 60536 ¦ Class II on base unit conforming to IEC 60536 ¦ Class II on support tube, with plastic fixing plate conforming to IEC 60536
XVDL6M8 | Environment | IP degree of protection | IP40 conforming to IEC 60529
XVDL6M8 | Contractual warranty | Warranty | 18 months
XVMB1RA | Main | range of product | Harmony XVM
XVMB1RA | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RA | Main | beacon or indicator bank unit type | 2 illuminated units
XVMB1RA | Main | component name | XVM
XVMB1RA | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RA | Main | light block color | Red/orange
XVMB1RA | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RA | Main | indicator bank base type | Base without buzzer
XVMB1RA | Main | mounting mode | Vertical
XVMB1RA | Complementary | kit composition | Plastic fixing plate ¦ Aluminium support tube ¦ Cover ¦ Base unit
XVMB1RA | Complementary | mounting diameter | 45 mm
XVMB1RA | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RA | Complementary | marking | CE
XVMB1RA | Complementary | mounting support | Aluminium tube
XVMB1RA | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RA | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RA | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RA | Complementary | net weight | 0.392 kg
XVMB1RA | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RA | Environment | product certifications | CCC
XVMB1RA | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1RA | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RA | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RA | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RA | Environment | protective treatment | TC
XVMB1RA | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RA | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RA | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RA | Offer Sustainability | Mercury free | Yes
XVMB1RA | Offer Sustainability | RoHS exemption information | Yes
XVMB1RA | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RA | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RA | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RA | Contractual warranty | Warranty | 18 months
XVMB1RG | Main | range of product | Harmony XVM
XVMB1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RG | Main | beacon or indicator bank unit type | 2 illuminated units
XVMB1RG | Main | component name | XVM
XVMB1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RG | Main | light block color | Red/green
XVMB1RG | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RG | Main | indicator bank base type | Base without buzzer
XVMB1RG | Main | mounting mode | Vertical
XVMB1RG | Complementary | kit composition | Base unit ¦ Aluminium support tube ¦ Cover ¦ Plastic fixing plate
XVMB1RG | Complementary | mounting diameter | 45 mm
XVMB1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RG | Complementary | marking | CE
XVMB1RG | Complementary | mounting support | Aluminium tube
XVMB1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RG | Complementary | net weight | 0.392 kg
XVMB1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RG | Environment | product certifications | CCC
XVMB1RG | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1RG | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RG | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RG | Environment | protective treatment | TC
XVMB1RG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RG | Offer Sustainability | Mercury free | Yes
XVMB1RG | Offer Sustainability | RoHS exemption information | Yes
XVMB1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RG | Contractual warranty | Warranty | 18 months
XVMG1RG | Main | range of product | Harmony XVM
XVMG1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1RG | Main | beacon or indicator bank unit type | 2 illuminated units
XVMG1RG | Main | component name | XVM
XVMG1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMG1RG | Main | light block color | Red/green
XVMG1RG | Main | [Us] rated supply voltage | 120 V AC/DC
XVMG1RG | Main | indicator bank base type | Base without buzzer
XVMG1RG | Main | mounting mode | Vertical
XVMG1RG | Complementary | kit composition | Cover ¦ Aluminium support tube ¦ Base unit ¦ Plastic fixing plate
XVMG1RG | Complementary | mounting diameter | 45 mm
XVMG1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1RG | Complementary | marking | CE
XVMG1RG | Complementary | mounting support | Aluminium tube
XVMG1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1RG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1RG | Complementary | net weight | 0.392 kg
XVMG1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1RG | Environment | product certifications | CCC
XVMG1RG | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMG1RG | Environment | ambient air temperature for storage | -25…70 °C
XVMG1RG | Environment | ambient air temperature for operation | -10…50 °C
XVMG1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1RG | Environment | protective treatment | TC
XVMG1RG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMG1RG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMG1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMG1RG | Offer Sustainability | Mercury free | Yes
XVMG1RG | Offer Sustainability | RoHS exemption information | Yes
XVMG1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMG1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMG1RG | Contractual warranty | Warranty | 18 months
XVMM1RG | Main | range of product | Harmony XVM
XVMM1RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RG | Main | beacon or indicator bank unit type | 2 illuminated units
XVMM1RG | Main | component name | XVM
XVMM1RG | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RG | Main | light block color | Red/green
XVMM1RG | Main | [Us] rated supply voltage | 230 V AC/DC
XVMM1RG | Main | indicator bank base type | Base without buzzer
XVMM1RG | Main | mounting mode | Vertical
XVMM1RG | Complementary | kit composition | Plastic fixing plate ¦ Cover ¦ Base unit ¦ Aluminium support tube
XVMM1RG | Complementary | mounting diameter | 45 mm
XVMM1RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RG | Complementary | marking | CE
XVMM1RG | Complementary | mounting support | Aluminium tube
XVMM1RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMM1RG | Complementary | net weight | 0.392 kg
XVMM1RG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RG | Environment | product certifications | CCC
XVMM1RG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM1RG | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RG | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RG | Environment | protective treatment | TC
XVMM1RG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM1RG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM1RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM1RG | Offer Sustainability | Mercury free | Yes
XVMM1RG | Offer Sustainability | RoHS exemption information | Yes
XVMM1RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM1RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM1RG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM1RG | Contractual warranty | Warranty | 18 months
XVMB2RG | Main | range of product | Harmony XVM
XVMB2RG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2RG | Main | beacon or indicator bank unit type | 2 illuminated units
XVMB2RG | Main | component name | XVM
XVMB2RG | Main | light source | Green LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVMB2RG | Main | light block color | Red/green
XVMB2RG | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2RG | Main | indicator bank base type | Base without buzzer
XVMB2RG | Main | mounting mode | Vertical
XVMB2RG | Complementary | kit composition | Aluminium support tube ¦ Base unit ¦ Cover ¦ Plastic fixing plate
XVMB2RG | Complementary | mounting diameter | 45 mm
XVMB2RG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2RG | Complementary | marking | CE
XVMB2RG | Complementary | mounting support | Aluminium tube
XVMB2RG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2RG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2RG | Complementary | current consumption | 43 mA on steady LED unit
XVMB2RG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMB2RG | Complementary | net weight | 0.395 kg
XVMB2RG | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2RG | Environment | product certifications | CCC
XVMB2RG | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB2RG | Environment | ambient air temperature for storage | -25…70 °C
XVMB2RG | Environment | ambient air temperature for operation | -10…50 °C
XVMB2RG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2RG | Environment | protective treatment | TC
XVMB2RG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2RG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2RG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2RG | Offer Sustainability | Mercury free | Yes
XVMB2RG | Offer Sustainability | RoHS exemption information | Yes
XVMB2RG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2RG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2RG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2RG | Contractual warranty | Warranty | 18 months
XVMB1RGS | Main | range of product | Harmony XVM
XVMB1RGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RGS | Main | beacon or indicator bank unit type | 2 illuminated units
XVMB1RGS | Main | component name | XVM
XVMB1RGS | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RGS | Main | light block color | Red/green
XVMB1RGS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RGS | Main | indicator bank base type | Base with integrated buzzer
XVMB1RGS | Main | mounting mode | Vertical
XVMB1RGS | Complementary | kit composition | Plastic fixing plate ¦ Aluminium support tube ¦ Cover ¦ Base unit
XVMB1RGS | Complementary | mounting diameter | 45 mm
XVMB1RGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RGS | Complementary | marking | CE
XVMB1RGS | Complementary | mounting support | Aluminium tube
XVMB1RGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RGS | Complementary | current consumption | 15 mA on base unit
XVMB1RGS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RGS | Complementary | fundamental frequency | 4 kHz
XVMB1RGS | Complementary | net weight | 0.402 kg
XVMB1RGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RGS | Environment | product certifications | CCC
XVMB1RGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1RGS | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RGS | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RGS | Environment | protective treatment | TC
XVMB1RGS | Environment | noise level | 0…80 dB at 1 m
XVMB1RGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RGS | Offer Sustainability | Mercury free | Yes
XVMB1RGS | Offer Sustainability | RoHS exemption information | Yes
XVMB1RGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RGS | Contractual warranty | Warranty | 18 months
XVMM1RGS | Main | range of product | Harmony XVM
XVMM1RGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RGS | Main | beacon or indicator bank unit type | 2 illuminated units
XVMM1RGS | Main | component name | XVM
XVMM1RGS | Main | light source | Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RGS | Main | light block color | Red/green
XVMM1RGS | Main | [Us] rated supply voltage | 230 V AC
XVMM1RGS | Main | indicator bank base type | Base with integrated buzzer
XVMM1RGS | Main | mounting mode | Vertical
XVMM1RGS | Complementary | kit composition | Cover ¦ Aluminium support tube ¦ Plastic fixing plate ¦ Base unit
XVMM1RGS | Complementary | mounting diameter | 45 mm
XVMM1RGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RGS | Complementary | marking | CE
XVMM1RGS | Complementary | mounting support | Aluminium tube
XVMM1RGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RGS | Complementary | current consumption | 18 mA on base unit
XVMM1RGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMM1RGS | Complementary | fundamental frequency | 4 kHz
XVMM1RGS | Complementary | net weight | 0.402 kg
XVMM1RGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RGS | Environment | product certifications | CCC
XVMM1RGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMM1RGS | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RGS | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RGS | Environment | protective treatment | TC
XVMM1RGS | Environment | noise level | 0…80 dB at 1 m
XVMM1RGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM1RGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM1RGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM1RGS | Offer Sustainability | Mercury free | Yes
XVMM1RGS | Offer Sustainability | RoHS exemption information | Yes
XVMM1RGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM1RGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM1RGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM1RGS | Contractual warranty | Warranty | 18 months
XVMB2RGS | Main | range of product | Harmony XVM
XVMB2RGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2RGS | Main | beacon or indicator bank unit type | 2 illuminated units
XVMB2RGS | Main | component name | XVM
XVMB2RGS | Main | light source | Green LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVMB2RGS | Main | light block color | Red/green
XVMB2RGS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2RGS | Main | indicator bank base type | Base with integrated buzzer
XVMB2RGS | Main | mounting mode | Vertical
XVMB2RGS | Complementary | kit composition | Aluminium support tube ¦ Base unit ¦ Plastic fixing plate ¦ Cover
XVMB2RGS | Complementary | mounting diameter | 45 mm
XVMB2RGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2RGS | Complementary | marking | CE
XVMB2RGS | Complementary | mounting support | Aluminium tube
XVMB2RGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2RGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2RGS | Complementary | current consumption | 15 mA on base unit ¦ 43 mA on steady LED unit
XVMB2RGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMB2RGS | Complementary | fundamental frequency | 4 kHz
XVMB2RGS | Complementary | net weight | 0.404 kg
XVMB2RGS | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2RGS | Environment | product certifications | CCC
XVMB2RGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB2RGS | Environment | ambient air temperature for storage | -25…70 °C
XVMB2RGS | Environment | ambient air temperature for operation | -10…50 °C
XVMB2RGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2RGS | Environment | protective treatment | TC
XVMB2RGS | Environment | noise level | 0…80 dB at 1 m
XVMB2RGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2RGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2RGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2RGS | Offer Sustainability | Mercury free | Yes
XVMB2RGS | Offer Sustainability | RoHS exemption information | Yes
XVMB2RGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2RGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2RGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2RGS | Contractual warranty | Warranty | 18 months
XVMB1RAG | Main | range of product | Harmony XVM
XVMB1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB1RAG | Main | component name | XVM
XVMB1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RAG | Main | light block color | Red/orange/green
XVMB1RAG | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RAG | Main | indicator bank base type | Base without buzzer
XVMB1RAG | Main | mounting mode | Vertical
XVMB1RAG | Complementary | kit composition | Plastic fixing plate ¦ Base unit ¦ Aluminium support tube ¦ Cover
XVMB1RAG | Complementary | mounting diameter | 45 mm
XVMB1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RAG | Complementary | marking | CE
XVMB1RAG | Complementary | mounting support | Aluminium tube
XVMB1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RAG | Complementary | net weight | 0.493 kg
XVMB1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RAG | Environment | product certifications | CCC
XVMB1RAG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMB1RAG | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RAG | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RAG | Environment | protective treatment | TC
XVMB1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RAG | Offer Sustainability | Mercury free | Yes
XVMB1RAG | Offer Sustainability | RoHS exemption information | Yes
XVMB1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RAG | Contractual warranty | Warranty | 18 months
XVMB1R6AG | Main | range of product | Harmony XVM
XVMB1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB1R6AG | Main | component name | XVM
XVMB1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red flash discharge tubeflashing signalling ¦ Green incandescent bulb with BA 15d base steady signalling <5 W
XVMB1R6AG | Main | light block color | Orange/green/red (flashing)
XVMB1R6AG | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1R6AG | Main | indicator bank base type | Base without buzzer
XVMB1R6AG | Main | mounting mode | Vertical
XVMB1R6AG | Complementary | kit composition | Cover ¦ Plastic fixing plate ¦ Aluminium support tube ¦ Base unit
XVMB1R6AG | Complementary | mounting diameter | 45 mm
XVMB1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1R6AG | Complementary | marking | CE
XVMB1R6AG | Complementary | mounting support | Aluminium tube
XVMB1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1R6AG | Complementary | current consumption | 140 mA on flash discharge tube unit AC ¦ 98 mA on flash discharge tube unit DC
XVMB1R6AG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
XVMB1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMB1R6AG | Complementary | net weight | 0.454 kg
XVMB1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1R6AG | Environment | product certifications | CCC
XVMB1R6AG | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1R6AG | Environment | ambient air temperature for storage | -25…70 °C
XVMB1R6AG | Environment | ambient air temperature for operation | -10…50 °C
XVMB1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1R6AG | Environment | protective treatment | TC
XVMB1R6AG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1R6AG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1R6AG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1R6AG | Offer Sustainability | Mercury free | Yes
XVMB1R6AG | Offer Sustainability | RoHS exemption information | Yes
XVMB1R6AG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1R6AG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1R6AG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1R6AG | Contractual warranty | Warranty | 18 months
XVMG1RAG | Main | range of product | Harmony XVM
XVMG1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMG1RAG | Main | component name | XVM
XVMG1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMG1RAG | Main | light block color | Red/orange/green
XVMG1RAG | Main | [Us] rated supply voltage | 120 V AC/DC
XVMG1RAG | Main | indicator bank base type | Base without buzzer
XVMG1RAG | Main | mounting mode | Vertical
XVMG1RAG | Complementary | kit composition | Cover ¦ Base unit ¦ Plastic fixing plate ¦ Aluminium support tube
XVMG1RAG | Complementary | mounting diameter | 45 mm
XVMG1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1RAG | Complementary | marking | CE
XVMG1RAG | Complementary | mounting support | Aluminium tube
XVMG1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMG1RAG | Complementary | net weight | 0.493 kg
XVMG1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1RAG | Environment | product certifications | CCC
XVMG1RAG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMG1RAG | Environment | ambient air temperature for storage | -25…70 °C
XVMG1RAG | Environment | ambient air temperature for operation | -10…50 °C
XVMG1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1RAG | Environment | protective treatment | TC
XVMG1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMG1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMG1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMG1RAG | Offer Sustainability | Mercury free | Yes
XVMG1RAG | Offer Sustainability | RoHS exemption information | Yes
XVMG1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMG1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMG1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMG1RAG | Contractual warranty | Warranty | 18 months
XVMG1R6AG | Main | range of product | Harmony XVM
XVMG1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMG1R6AG | Main | component name | XVM
XVMG1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red flash discharge tubeflashing signalling ¦ Green incandescent bulb with BA 15d base steady signalling <5 W
XVMG1R6AG | Main | light block color | Orange/green/red (flashing)
XVMG1R6AG | Main | [Us] rated supply voltage | 120 V AC/DC
XVMG1R6AG | Main | indicator bank base type | Base without buzzer
XVMG1R6AG | Main | mounting mode | Vertical
XVMG1R6AG | Complementary | kit composition | Aluminium support tube ¦ Cover ¦ Plastic fixing plate ¦ Base unit
XVMG1R6AG | Complementary | mounting diameter | 45 mm
XVMG1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1R6AG | Complementary | marking | CE
XVMG1R6AG | Complementary | mounting support | Aluminium tube
XVMG1R6AG | Complementary | short-circuit protection | 0.2 A
XVMG1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1R6AG | Complementary | current consumption | 33 mA on flash discharge tube unit
XVMG1R6AG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
XVMG1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMG1R6AG | Complementary | net weight | 0.454 kg
XVMG1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1R6AG | Environment | product certifications | CCC
XVMG1R6AG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMG1R6AG | Environment | ambient air temperature for storage | -25…70 °C
XVMG1R6AG | Environment | ambient air temperature for operation | -10…50 °C
XVMG1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1R6AG | Environment | protective treatment | TC
XVMG1R6AG | Contractual warranty | Warranty | 18 months
XVMM1RAG | Main | range of product | Harmony XVM
XVMM1RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RAG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMM1RAG | Main | component name | XVM
XVMM1RAG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RAG | Main | light block color | Red/orange/green
XVMM1RAG | Main | [Us] rated supply voltage | 230 V AC/DC
XVMM1RAG | Main | indicator bank base type | Base without buzzer
XVMM1RAG | Main | mounting mode | Vertical
XVMM1RAG | Complementary | kit composition | Base unit ¦ Aluminium support tube ¦ Cover ¦ Plastic fixing plate
XVMM1RAG | Complementary | mounting diameter | 45 mm
XVMM1RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RAG | Complementary | marking | CE
XVMM1RAG | Complementary | mounting support | Aluminium tube
XVMM1RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RAG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMM1RAG | Complementary | net weight | 0.493 kg
XVMM1RAG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RAG | Environment | product certifications | CCC
XVMM1RAG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM1RAG | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RAG | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RAG | Environment | protective treatment | TC
XVMM1RAG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM1RAG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM1RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM1RAG | Offer Sustainability | Mercury free | Yes
XVMM1RAG | Offer Sustainability | RoHS exemption information | Yes
XVMM1RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM1RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM1RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM1RAG | Contractual warranty | Warranty | 18 months
XVMM1R6AG | Main | range of product | Harmony XVM
XVMM1R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMM1R6AG | Main | component name | XVM
XVMM1R6AG | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red flash discharge tubeflashing signalling ¦ Green incandescent bulb with BA 15d base steady signalling <5 W
XVMM1R6AG | Main | light block color | Orange/green/red (flashing)
XVMM1R6AG | Main | [Us] rated supply voltage | 230 V AC/DC
XVMM1R6AG | Main | indicator bank base type | Base without buzzer
XVMM1R6AG | Main | mounting mode | Vertical
XVMM1R6AG | Complementary | kit composition | Base unit ¦ Plastic fixing plate ¦ Cover ¦ Aluminium support tube
XVMM1R6AG | Complementary | mounting diameter | 45 mm
XVMM1R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1R6AG | Complementary | marking | CE
XVMM1R6AG | Complementary | mounting support | Aluminium tube
XVMM1R6AG | Complementary | short-circuit protection | 0.2 A
XVMM1R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1R6AG | Complementary | current consumption | 20 mA on flash discharge tube unit
XVMM1R6AG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMM1R6AG | Complementary | luminance | 650 cd/m² for incandescent bulb unit
XVMM1R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMM1R6AG | Complementary | net weight | 0.454 kg
XVMM1R6AG | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1R6AG | Environment | product certifications | CCC
XVMM1R6AG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM1R6AG | Environment | ambient air temperature for storage | -25…70 °C
XVMM1R6AG | Environment | ambient air temperature for operation | -10…50 °C
XVMM1R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1R6AG | Environment | protective treatment | TC
XVMM1R6AG | Contractual warranty | Warranty | 18 months
XVMB2R6AG | Main | range of product | Harmony XVM
XVMB2R6AG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2R6AG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB2R6AG | Main | component name | XVM
XVMB2R6AG | Main | light source | Red flash discharge tubeflashing signalling ¦ Green LED with BA 15d base steady signalling ¦ Orange LED with BA 15d base steady signalling
XVMB2R6AG | Main | light block color | Orange/green/red (flashing)
XVMB2R6AG | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2R6AG | Main | indicator bank base type | Base without buzzer
XVMB2R6AG | Main | mounting mode | Vertical
XVMB2R6AG | Complementary | kit composition | Base unit ¦ Aluminium support tube ¦ Cover ¦ Plastic fixing plate
XVMB2R6AG | Complementary | mounting diameter | 45 mm
XVMB2R6AG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2R6AG | Complementary | marking | CE
XVMB2R6AG | Complementary | mounting support | Aluminium tube
XVMB2R6AG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2R6AG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2R6AG | Complementary | current consumption | 140 mA on flash discharge tube unit AC ¦ 98 mA on flash discharge tube unit DC ¦ 43 mA on steady LED unit
XVMB2R6AG | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB2R6AG | Complementary | luminance | 900 cd/m² for LED unit
XVMB2R6AG | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMB2R6AG | Complementary | net weight | 0.456 kg
XVMB2R6AG | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2R6AG | Environment | product certifications | CCC
XVMB2R6AG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMB2R6AG | Environment | ambient air temperature for storage | -25…70 °C
XVMB2R6AG | Environment | ambient air temperature for operation | -10…50 °C
XVMB2R6AG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2R6AG | Environment | protective treatment | TC
XVMB2R6AG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2R6AG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2R6AG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2R6AG | Offer Sustainability | Mercury free | Yes
XVMB2R6AG | Offer Sustainability | RoHS exemption information | Yes
XVMB2R6AG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2R6AG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2R6AG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2R6AG | Contractual warranty | Warranty | 18 months
XVMM2RAG | Main | range of product | Harmony XVM
XVMM2RAG | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM2RAG | Main | beacon or indicator bank unit type | 3 illuminated units
XVMM2RAG | Main | component name | XVM
XVMM2RAG | Main | light source | Green LED with BA 15d base steady signalling ¦ Orange LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVMM2RAG | Main | light block color | Red/orange/green
XVMM2RAG | Main | [Us] rated supply voltage | 230 V AC
XVMM2RAG | Main | indicator bank base type | Base without buzzer
XVMM2RAG | Main | mounting mode | Vertical
XVMM2RAG | Complementary | kit composition | Base unit ¦ Cover ¦ Plastic fixing plate ¦ Aluminium support tube
XVMM2RAG | Complementary | mounting diameter | 45 mm
XVMM2RAG | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM2RAG | Complementary | marking | CE
XVMM2RAG | Complementary | mounting support | Aluminium tube
XVMM2RAG | Complementary | short-circuit protection | 0.2 A
XVMM2RAG | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM2RAG | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM2RAG | Complementary | current consumption | 15 mA on steady LED unit
XVMM2RAG | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMM2RAG | Complementary | net weight | 0.443 kg
XVMM2RAG | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMM2RAG | Environment | product certifications | CCC
XVMM2RAG | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM2RAG | Environment | ambient air temperature for storage | -25…70 °C
XVMM2RAG | Environment | ambient air temperature for operation | -10…50 °C
XVMM2RAG | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM2RAG | Environment | protective treatment | TC
XVMM2RAG | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM2RAG | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM2RAG | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM2RAG | Offer Sustainability | Mercury free | Yes
XVMM2RAG | Offer Sustainability | RoHS exemption information | Yes
XVMM2RAG | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM2RAG | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM2RAG | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM2RAG | Contractual warranty | Warranty | 18 months
XVMB1RAGS | Main | range of product | Harmony XVM
XVMB1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB1RAGS | Main | component name | XVM
XVMB1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RAGS | Main | light block color | Red/orange/green
XVMB1RAGS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RAGS | Main | indicator bank base type | Base with integrated buzzer
XVMB1RAGS | Main | mounting mode | Vertical
XVMB1RAGS | Complementary | kit composition | Cover ¦ Plastic fixing plate ¦ Aluminium support tube ¦ Base unit
XVMB1RAGS | Complementary | mounting diameter | 45 mm
XVMB1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RAGS | Complementary | marking | CE
XVMB1RAGS | Complementary | mounting support | Aluminium tube
XVMB1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RAGS | Complementary | current consumption | 15 mA on base unit
XVMB1RAGS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RAGS | Complementary | fundamental frequency | 4 kHz
XVMB1RAGS | Complementary | net weight | 0.449 kg
XVMB1RAGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RAGS | Environment | product certifications | CCC
XVMB1RAGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1RAGS | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RAGS | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RAGS | Environment | protective treatment | TC
XVMB1RAGS | Environment | noise level | 0…80 dB at 1 m
XVMB1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RAGS | Offer Sustainability | Mercury free | Yes
XVMB1RAGS | Offer Sustainability | RoHS exemption information | Yes
XVMB1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RAGS | Contractual warranty | Warranty | 18 months
XVMB1R6AGS | Main | range of product | Harmony XVM
XVMB1R6AGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1R6AGS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB1R6AGS | Main | component name | XVM
XVMB1R6AGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red flash discharge tubeflashing signalling ¦ Green incandescent bulb with BA 15d base steady signalling <5 W
XVMB1R6AGS | Main | light block color | Orange/green/red (flashing)
XVMB1R6AGS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1R6AGS | Main | indicator bank base type | Base with integrated buzzer
XVMB1R6AGS | Main | mounting mode | Vertical
XVMB1R6AGS | Complementary | kit composition | Aluminium support tube ¦ Cover ¦ Plastic fixing plate ¦ Base unit
XVMB1R6AGS | Complementary | mounting diameter | 45 mm
XVMB1R6AGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1R6AGS | Complementary | marking | CE
XVMB1R6AGS | Complementary | mounting support | Aluminium tube
XVMB1R6AGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1R6AGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1R6AGS | Complementary | current consumption | 140 mA on flash discharge tube unit AC ¦ 98 mA on flash discharge tube unit DC ¦ 15 mA on base unit
XVMB1R6AGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMB1R6AGS | Complementary | luminance | 650 cd/m² for incandescent bulb unit
XVMB1R6AGS | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMB1R6AGS | Complementary | fundamental frequency | 4 kHz
XVMB1R6AGS | Complementary | net weight | 0.463 kg
XVMB1R6AGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1R6AGS | Environment | product certifications | CCC
XVMB1R6AGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1R6AGS | Environment | ambient air temperature for storage | -25…70 °C
XVMB1R6AGS | Environment | ambient air temperature for operation | -10…50 °C
XVMB1R6AGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1R6AGS | Environment | protective treatment | TC
XVMB1R6AGS | Environment | noise level | 0…80 dB at 1 m
XVMB1R6AGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1R6AGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1R6AGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1R6AGS | Offer Sustainability | Mercury free | Yes
XVMB1R6AGS | Offer Sustainability | RoHS exemption information | Yes
XVMB1R6AGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1R6AGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1R6AGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1R6AGS | Contractual warranty | Warranty | 18 months
XVMG1RAGS | Main | range of product | Harmony XVM
XVMG1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMG1RAGS | Main | component name | XVM
XVMG1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMG1RAGS | Main | light block color | Red/orange/green
XVMG1RAGS | Main | [Us] rated supply voltage | 120 V AC
XVMG1RAGS | Main | indicator bank base type | Base with integrated buzzer
XVMG1RAGS | Main | mounting mode | Vertical
XVMG1RAGS | Complementary | kit composition | Aluminium support tube ¦ Base unit ¦ Cover ¦ Plastic fixing plate
XVMG1RAGS | Complementary | mounting diameter | 45 mm
XVMG1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1RAGS | Complementary | marking | CE
XVMG1RAGS | Complementary | mounting support | Aluminium tube
XVMG1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1RAGS | Complementary | current consumption | 18 mA on base unit
XVMG1RAGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1RAGS | Complementary | fundamental frequency | 4 kHz
XVMG1RAGS | Complementary | net weight | 0.449 kg
XVMG1RAGS | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMG1RAGS | Environment | product certifications | CCC
XVMG1RAGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMG1RAGS | Environment | ambient air temperature for storage | -25…70 °C
XVMG1RAGS | Environment | ambient air temperature for operation | -10…50 °C
XVMG1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1RAGS | Environment | protective treatment | TC
XVMG1RAGS | Environment | noise level | 0…80 dB at 1 m
XVMG1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMG1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMG1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMG1RAGS | Offer Sustainability | Mercury free | Yes
XVMG1RAGS | Offer Sustainability | RoHS exemption information | Yes
XVMG1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMG1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMG1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMG1RAGS | Contractual warranty | Warranty | 18 months
XVMG1R6AGS | Main | range of product | Harmony XVM
XVMG1R6AGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1R6AGS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMG1R6AGS | Main | component name | XVM
XVMG1R6AGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Red flash discharge tubeflashing signalling ¦ Green incandescent bulb with BA 15d base steady signalling <5 W
XVMG1R6AGS | Main | light block color | Orange/green/red (flashing)
XVMG1R6AGS | Main | [Us] rated supply voltage | 120 V AC
XVMG1R6AGS | Main | indicator bank base type | Base with integrated buzzer
XVMG1R6AGS | Main | mounting mode | Vertical
XVMG1R6AGS | Complementary | kit composition | Plastic fixing plate ¦ Aluminium support tube ¦ Cover ¦ Base unit
XVMG1R6AGS | Complementary | mounting diameter | 45 mm
XVMG1R6AGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1R6AGS | Complementary | marking | CE
XVMG1R6AGS | Complementary | mounting support | Aluminium tube
XVMG1R6AGS | Complementary | short-circuit protection | 0.2 A
XVMG1R6AGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1R6AGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1R6AGS | Complementary | current consumption | 18 mA on base unit ¦ 33 mA on flash discharge tube unit
XVMG1R6AGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1R6AGS | Complementary | luminance | 650 cd/m² for incandescent bulb unit
XVMG1R6AGS | Complementary | flashing frequency | 0.8 Hz with flash discharge tube unit
XVMG1R6AGS | Complementary | fundamental frequency | 4 kHz
XVMG1R6AGS | Complementary | net weight | 0.463 kg
XVMG1R6AGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1R6AGS | Environment | product certifications | CCC
XVMG1R6AGS | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMG1R6AGS | Environment | ambient air temperature for storage | -25…70 °C
XVMG1R6AGS | Environment | ambient air temperature for operation | -10…50 °C
XVMG1R6AGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1R6AGS | Environment | protective treatment | TC
XVMG1R6AGS | Environment | noise level | 0…80 dB at 1 m
XVMG1R6AGS | Contractual warranty | Warranty | 18 months
XVMM1RAGS | Main | range of product | Harmony XVM
XVMM1RAGS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RAGS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMM1RAGS | Main | component name | XVM
XVMM1RAGS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RAGS | Main | light block color | Red/orange/green
XVMM1RAGS | Main | [Us] rated supply voltage | 230 V AC
XVMM1RAGS | Main | indicator bank base type | Base with integrated buzzer
XVMM1RAGS | Main | mounting mode | Vertical
XVMM1RAGS | Complementary | kit composition | Base unit ¦ Cover ¦ Aluminium support tube ¦ Plastic fixing plate
XVMM1RAGS | Complementary | mounting diameter | 45 mm
XVMM1RAGS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RAGS | Complementary | marking | CE
XVMM1RAGS | Complementary | mounting support | Aluminium tube
XVMM1RAGS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RAGS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RAGS | Complementary | current consumption | 18 mA on base unit
XVMM1RAGS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMM1RAGS | Complementary | fundamental frequency | 4 kHz
XVMM1RAGS | Complementary | net weight | 0.449 kg
XVMM1RAGS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RAGS | Environment | product certifications | CCC
XVMM1RAGS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMM1RAGS | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RAGS | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RAGS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RAGS | Environment | protective treatment | TC
XVMM1RAGS | Environment | noise level | 0…80 dB at 1 m
XVMM1RAGS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM1RAGS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM1RAGS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM1RAGS | Offer Sustainability | Mercury free | Yes
XVMM1RAGS | Offer Sustainability | RoHS exemption information | Yes
XVMM1RAGS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM1RAGS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM1RAGS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM1RAGS | Contractual warranty | Warranty | 18 months
XVMB2RA5GS | Main | range of product | Harmony XVM
XVMB2RA5GS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2RA5GS | Main | beacon or indicator bank unit type | 3 illuminated units
XVMB2RA5GS | Main | component name | XVM
XVMB2RA5GS | Main | light source | Orange LED with BA 15d base flashing signalling ¦ Green LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling
XVMB2RA5GS | Main | light block color | Red/green/orange (flashing)
XVMB2RA5GS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2RA5GS | Main | indicator bank base type | Base with integrated buzzer
XVMB2RA5GS | Main | mounting mode | Vertical
XVMB2RA5GS | Complementary | kit composition | Base unit ¦ Plastic fixing plate ¦ Aluminium support tube ¦ Cover
XVMB2RA5GS | Complementary | mounting diameter | 45 mm
XVMB2RA5GS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2RA5GS | Complementary | marking | CE
XVMB2RA5GS | Complementary | mounting support | Aluminium tube
XVMB2RA5GS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2RA5GS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2RA5GS | Complementary | current consumption | 15 mA on base unit ¦ 45 mA on flashing LED unit ¦ 43 mA on steady LED unit
XVMB2RA5GS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB2RA5GS | Complementary | flashing frequency | 1 Hz with flashing LED unit
XVMB2RA5GS | Complementary | fundamental frequency | 4 kHz
XVMB2RA5GS | Complementary | net weight | 0.453 kg
XVMB2RA5GS | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2RA5GS | Environment | product certifications | CCC
XVMB2RA5GS | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMB2RA5GS | Environment | ambient air temperature for storage | -25…70 °C
XVMB2RA5GS | Environment | ambient air temperature for operation | -10…50 °C
XVMB2RA5GS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2RA5GS | Environment | protective treatment | TC
XVMB2RA5GS | Environment | noise level | 0…80 dB at 1 m
XVMB2RA5GS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2RA5GS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2RA5GS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2RA5GS | Offer Sustainability | Mercury free | Yes
XVMB2RA5GS | Offer Sustainability | RoHS exemption information | Yes
XVMB2RA5GS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2RA5GS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2RA5GS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2RA5GS | Contractual warranty | Warranty | 18 months
XVMB1RAGB | Main | range of product | Harmony XVM
XVMB1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
XVMB1RAGB | Main | component name | XVM
XVMB1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RAGB | Main | light block color | Red/orange/green/blue
XVMB1RAGB | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RAGB | Main | indicator bank base type | Base without buzzer
XVMB1RAGB | Main | mounting mode | Vertical
XVMB1RAGB | Complementary | kit composition | Plastic fixing plate ¦ Aluminium support tube ¦ Cover ¦ Base unit
XVMB1RAGB | Complementary | mounting diameter | 45 mm
XVMB1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RAGB | Complementary | marking | CE
XVMB1RAGB | Complementary | mounting support | Aluminium tube
XVMB1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RAGB | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB1RAGB | Complementary | net weight | 0.486 kg
XVMB1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RAGB | Environment | product certifications | CCC
XVMB1RAGB | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB1RAGB | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RAGB | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RAGB | Environment | protective treatment | TC
XVMB1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RAGB | Offer Sustainability | Mercury free | Yes
XVMB1RAGB | Offer Sustainability | RoHS exemption information | Yes
XVMB1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RAGB | Contractual warranty | Warranty | 18 months
XVMG1RAGB | Main | range of product | Harmony XVM
XVMG1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
XVMG1RAGB | Main | component name | XVM
XVMG1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMG1RAGB | Main | light block color | Red/orange/green/blue
XVMG1RAGB | Main | [Us] rated supply voltage | 120 V AC/DC
XVMG1RAGB | Main | indicator bank base type | Base without buzzer
XVMG1RAGB | Main | mounting mode | Vertical
XVMG1RAGB | Complementary | kit composition | Aluminium support tube ¦ Base unit ¦ Plastic fixing plate ¦ Cover
XVMG1RAGB | Complementary | mounting diameter | 45 mm
XVMG1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1RAGB | Complementary | marking | CE
XVMG1RAGB | Complementary | mounting support | Aluminium tube
XVMG1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1RAGB | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1RAGB | Complementary | net weight | 0.486 kg
XVMG1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1RAGB | Environment | product certifications | CCC
XVMG1RAGB | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMG1RAGB | Environment | ambient air temperature for storage | -25…70 °C
XVMG1RAGB | Environment | ambient air temperature for operation | -10…50 °C
XVMG1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1RAGB | Environment | protective treatment | TC
XVMG1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
XVMG1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
XVMG1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMG1RAGB | Offer Sustainability | Mercury free | Yes
XVMG1RAGB | Offer Sustainability | RoHS exemption information | Yes
XVMG1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMG1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMG1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMG1RAGB | Contractual warranty | Warranty | 18 months
XVMM1RAGB | Main | range of product | Harmony XVM
XVMM1RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
XVMM1RAGB | Main | component name | XVM
XVMM1RAGB | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RAGB | Main | light block color | Red/orange/green/blue
XVMM1RAGB | Main | [Us] rated supply voltage | 230 V AC/DC
XVMM1RAGB | Main | indicator bank base type | Base without buzzer
XVMM1RAGB | Main | mounting mode | Vertical
XVMM1RAGB | Complementary | kit composition | Cover ¦ Base unit ¦ Plastic fixing plate ¦ Aluminium support tube
XVMM1RAGB | Complementary | mounting diameter | 45 mm
XVMM1RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RAGB | Complementary | marking | CE
XVMM1RAGB | Complementary | mounting support | Aluminium tube
XVMM1RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RAGB | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMM1RAGB | Complementary | net weight | 0.486 kg
XVMM1RAGB | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RAGB | Environment | product certifications | CCC
XVMM1RAGB | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM1RAGB | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RAGB | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RAGB | Environment | protective treatment | TC
XVMM1RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
XVMM1RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
XVMM1RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMM1RAGB | Offer Sustainability | Mercury free | Yes
XVMM1RAGB | Offer Sustainability | RoHS exemption information | Yes
XVMM1RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMM1RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMM1RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMM1RAGB | Contractual warranty | Warranty | 18 months
XVMB2RAGB | Main | range of product | Harmony XVM
XVMB2RAGB | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2RAGB | Main | beacon or indicator bank unit type | 4 illuminated units
XVMB2RAGB | Main | component name | XVM
XVMB2RAGB | Main | light source | Green LED with BA 15d base steady signalling ¦ Orange LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling ¦ Blue LED with BA 15d base steady signalling
XVMB2RAGB | Main | light block color | Red/orange/green/blue
XVMB2RAGB | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2RAGB | Main | indicator bank base type | Base without buzzer
XVMB2RAGB | Main | mounting mode | Vertical
XVMB2RAGB | Complementary | kit composition | Cover ¦ Plastic fixing plate ¦ Base unit ¦ Aluminium support tube
XVMB2RAGB | Complementary | mounting diameter | 45 mm
XVMB2RAGB | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2RAGB | Complementary | marking | CE
XVMB2RAGB | Complementary | mounting support | Aluminium tube
XVMB2RAGB | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2RAGB | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2RAGB | Complementary | current consumption | 43 mA on steady LED unit
XVMB2RAGB | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB2RAGB | Complementary | net weight | 0.491 kg
XVMB2RAGB | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2RAGB | Environment | product certifications | CCC
XVMB2RAGB | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMB2RAGB | Environment | ambient air temperature for storage | -25…70 °C
XVMB2RAGB | Environment | ambient air temperature for operation | -10…50 °C
XVMB2RAGB | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2RAGB | Environment | protective treatment | TC
XVMB2RAGB | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2RAGB | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2RAGB | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2RAGB | Offer Sustainability | Mercury free | Yes
XVMB2RAGB | Offer Sustainability | RoHS exemption information | Yes
XVMB2RAGB | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2RAGB | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2RAGB | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2RAGB | Contractual warranty | Warranty | 18 months
XVMB1RAGBS | Main | range of product | Harmony XVM
XVMB1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
XVMB1RAGBS | Main | component name | XVM
XVMB1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMB1RAGBS | Main | light block color | Red/orange/green/blue
XVMB1RAGBS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB1RAGBS | Main | indicator bank base type | Base with integrated buzzer
XVMB1RAGBS | Main | mounting mode | Vertical
XVMB1RAGBS | Complementary | kit composition | Plastic fixing plate ¦ Cover ¦ Aluminium support tube ¦ Base unit
XVMB1RAGBS | Complementary | mounting diameter | 45 mm
XVMB1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB1RAGBS | Complementary | marking | CE
XVMB1RAGBS | Complementary | mounting support | Aluminium tube
XVMB1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB1RAGBS | Complementary | current consumption | 15 mA on base unit
XVMB1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMB1RAGBS | Complementary | fundamental frequency | 4 kHz
XVMB1RAGBS | Complementary | net weight | 0.496 kg
XVMB1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMB1RAGBS | Environment | product certifications | CCC
XVMB1RAGBS | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMB1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
XVMB1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
XVMB1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB1RAGBS | Environment | protective treatment | TC
XVMB1RAGBS | Environment | noise level | 0…80 dB at 1 m
XVMB1RAGBS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB1RAGBS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB1RAGBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB1RAGBS | Offer Sustainability | Mercury free | Yes
XVMB1RAGBS | Offer Sustainability | RoHS exemption information | Yes
XVMB1RAGBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB1RAGBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB1RAGBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB1RAGBS | Contractual warranty | Warranty | 18 months
XVMG1RAGBS | Main | range of product | Harmony XVM
XVMG1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMG1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
XVMG1RAGBS | Main | component name | XVM
XVMG1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMG1RAGBS | Main | light block color | Red/orange/green/blue
XVMG1RAGBS | Main | [Us] rated supply voltage | 120 V AC
XVMG1RAGBS | Main | indicator bank base type | Base with integrated buzzer
XVMG1RAGBS | Main | mounting mode | Vertical
XVMG1RAGBS | Complementary | kit composition | Aluminium support tube ¦ Base unit ¦ Plastic fixing plate ¦ Cover
XVMG1RAGBS | Complementary | mounting diameter | 45 mm
XVMG1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMG1RAGBS | Complementary | marking | CE
XVMG1RAGBS | Complementary | mounting support | Aluminium tube
XVMG1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMG1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMG1RAGBS | Complementary | current consumption | 18 mA on base unit
XVMG1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVMG1RAGBS | Complementary | fundamental frequency | 4 kHz
XVMG1RAGBS | Complementary | net weight | 0.496 kg
XVMG1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMG1RAGBS | Environment | product certifications | CCC
XVMG1RAGBS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMG1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
XVMG1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
XVMG1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMG1RAGBS | Environment | protective treatment | TC
XVMG1RAGBS | Environment | noise level | 0…80 dB at 1 m
XVMG1RAGBS | Contractual warranty | Warranty | 18 months
XVMM1RAGBS | Main | range of product | Harmony XVM
XVMM1RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMM1RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
XVMM1RAGBS | Main | component name | XVM
XVMM1RAGBS | Main | light source | Orange incandescent bulb with BA 15d base steady signalling <5 W ¦ Green incandescent bulb with BA 15d base steady signalling <5 W ¦ Red incandescent bulb with BA 15d base steady signalling <5 W ¦ Blue incandescent bulb with BA 15d base steady signalling <5 W
XVMM1RAGBS | Main | light block color | Red/orange/green/blue
XVMM1RAGBS | Main | [Us] rated supply voltage | 230 V AC
XVMM1RAGBS | Main | indicator bank base type | Base with integrated buzzer
XVMM1RAGBS | Main | mounting mode | Vertical
XVMM1RAGBS | Complementary | kit composition | Cover ¦ Aluminium support tube ¦ Plastic fixing plate ¦ Base unit
XVMM1RAGBS | Complementary | mounting diameter | 45 mm
XVMM1RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMM1RAGBS | Complementary | marking | CE
XVMM1RAGBS | Complementary | mounting support | Aluminium tube
XVMM1RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMM1RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMM1RAGBS | Complementary | current consumption | 18 mA on base unit
XVMM1RAGBS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMM1RAGBS | Complementary | fundamental frequency | 4 kHz
XVMM1RAGBS | Complementary | net weight | 0.496 kg
XVMM1RAGBS | Environment | IP degree of protection | IP42 vertical position conforming to IEC 60529
XVMM1RAGBS | Environment | product certifications | CCC
XVMM1RAGBS | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVMM1RAGBS | Environment | ambient air temperature for storage | -25…70 °C
XVMM1RAGBS | Environment | ambient air temperature for operation | -10…50 °C
XVMM1RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMM1RAGBS | Environment | protective treatment | TC
XVMM1RAGBS | Environment | noise level | 0…80 dB at 1 m
XVMM1RAGBS | Contractual warranty | Warranty | 18 months
XVMB2RAGBS | Main | range of product | Harmony XVM
XVMB2RAGBS | Main | product or component type | Pre-assembled and pre-cabled indicator bank
XVMB2RAGBS | Main | beacon or indicator bank unit type | 4 illuminated units
XVMB2RAGBS | Main | component name | XVM
XVMB2RAGBS | Main | light source | Green LED with BA 15d base steady signalling ¦ Orange LED with BA 15d base steady signalling ¦ Red LED with BA 15d base steady signalling ¦ Blue LED with BA 15d base steady signalling
XVMB2RAGBS | Main | light block color | Red/orange/green/blue
XVMB2RAGBS | Main | [Us] rated supply voltage | 24 V AC/DC
XVMB2RAGBS | Main | indicator bank base type | Base with integrated buzzer
XVMB2RAGBS | Main | mounting mode | Vertical
XVMB2RAGBS | Complementary | kit composition | Cover ¦ Plastic fixing plate ¦ Base unit ¦ Aluminium support tube
XVMB2RAGBS | Complementary | mounting diameter | 45 mm
XVMB2RAGBS | Complementary | connections - terminals | Flying leads,clamping capacity: 1 x 0.325 mm² (AWG 22)
XVMB2RAGBS | Complementary | marking | CE
XVMB2RAGBS | Complementary | mounting support | Aluminium tube
XVMB2RAGBS | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVMB2RAGBS | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVMB2RAGBS | Complementary | current consumption | 15 mA on base unit ¦ 43 mA on steady LED unit
XVMB2RAGBS | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVMB2RAGBS | Complementary | fundamental frequency | 4 kHz
XVMB2RAGBS | Complementary | net weight | 0.501 kg
XVMB2RAGBS | Environment | IP degree of protection | IP54 vertical position conforming to IEC 60529
XVMB2RAGBS | Environment | product certifications | CCC
XVMB2RAGBS | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVMB2RAGBS | Environment | ambient air temperature for storage | -25…70 °C
XVMB2RAGBS | Environment | ambient air temperature for operation | -10…50 °C
XVMB2RAGBS | Environment | overvoltage category | Class I conforming to IEC 60947-1 ¦ Class I conforming to IEC 60947-5-1 ¦ Class I conforming to IEC 61140
XVMB2RAGBS | Environment | protective treatment | TC
XVMB2RAGBS | Environment | noise level | 0…80 dB at 1 m
XVMB2RAGBS | Offer Sustainability | Sustainable offer status | Green Premium product
XVMB2RAGBS | Offer Sustainability | REACh Regulation | REACh Declaration
XVMB2RAGBS | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVMB2RAGBS | Offer Sustainability | Mercury free | Yes
XVMB2RAGBS | Offer Sustainability | RoHS exemption information | Yes
XVMB2RAGBS | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVMB2RAGBS | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVMB2RAGBS | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVMB2RAGBS | Contractual warranty | Warranty | 18 months
XVEL33 | Main | range of product | Harmony XVE Optimum
XVEL33 | Main | product or component type | Complete illuminated beacon
XVEL33 | Main | beacon or indicator bank unit type | 1 base unit ¦ 1 illuminated unit ¦ 1 screw fixing cover ¦ 1 short fixing base
XVEL33 | Main | signalling type | Steady
XVEL33 | Main | component name | XVE
XVEL33 | Main | light source | Bulb not included, green
XVEL33 | Main | bulb type | Incandescent with BA 15d base
XVEL33 | Main | [Us] rated supply voltage | <= 240 V AC/DC
XVEL33 | Complementary | mounting diameter | 70 mm
XVEL33 | Complementary | maximum power dissipation in W | 5 W
XVEL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVEL33 | Complementary | marking | CE
XVEL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVEL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVEL33 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVEL33 | Complementary | luminance | 640 cd/m²
XVEL33 | Complementary | CAD overall width | 70 mm
XVEL33 | Complementary | CAD overall height | 129 mm
XVEL33 | Complementary | CAD overall depth | 70 mm
XVEL33 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVEL33 | Complementary | net weight | 0.245 kg
XVEL33 | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVEL33 | Environment | product certifications | CSA ¦ UL ¦ CCC
XVEL33 | Environment | ambient air temperature for storage | -40…70 °C
XVEL33 | Environment | ambient air temperature for operation | -25…55 °C
XVEL33 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 ¦ Class I plastic tube mounting conforming to IEC 61140
XVEL33 | Environment | protective treatment | TC
XVEL33 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVEL33 | Contractual warranty | Warranty | 18 months
XVEL6B3 | Main | range of product | Harmony XVE Optimum
XVEL6B3 | Main | product or component type | Complete illuminated beacon
XVEL6B3 | Main | beacon or indicator bank unit type | 1 base unit ¦ 1 illuminated unit ¦ 1 screw fixing cover ¦ 1 short fixing base
XVEL6B3 | Main | signalling type | Flashing
XVEL6B3 | Main | component name | XVE
XVEL6B3 | Main | light source | Integral flash discharge tube, green
XVEL6B3 | Main | bulb type | Flash discharge tube
XVEL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVEL6B3 | Complementary | mounting diameter | 70 mm
XVEL6B3 | Complementary | flash energy | 1 J
XVEL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVEL6B3 | Complementary | marking | CE
XVEL6B3 | Complementary | short-circuit protection | 0.63 A
XVEL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVEL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVEL6B3 | Complementary | current consumption | < 145 mA AC ¦ < 85 mA DC
XVEL6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVEL6B3 | Complementary | flashing frequency | 1 Hz
XVEL6B3 | Complementary | CAD overall width | 70 mm
XVEL6B3 | Complementary | CAD overall height | 129 mm
XVEL6B3 | Complementary | CAD overall depth | 70 mm
XVEL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVEL6B3 | Complementary | net weight | 0.27 kg
XVEL6B3 | Environment | standards | EN/IEC 60947-1 ¦ EN/IEC 60947-5-1
XVEL6B3 | Environment | product certifications | CSA ¦ CCC ¦ UL
XVEL6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVEL6B3 | Environment | ambient air temperature for operation | -25…55 °C
XVEL6B3 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 ¦ Class I plastic tube mounting conforming to IEC 61140
XVEL6B3 | Environment | protective treatment | TC
XVEL6B3 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVEL6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVEL6B3 | Offer Sustainability | Mercury free | Yes
XVEL6B3 | Offer Sustainability | RoHS exemption information | Yes
XVEL6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVEL6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVEL6B3 | Contractual warranty | Warranty | 18 months
XVEL6B5 | Main | range of product | Harmony XVE Optimum
XVEL6B5 | Main | product or component type | Complete illuminated beacon
XVEL6B5 | Main | beacon or indicator bank unit type | 1 base unit ¦ 1 illuminated unit ¦ 1 screw fixing cover ¦ 1 short fixing base
XVEL6B5 | Main | signalling type | Flashing
XVEL6B5 | Main | component name | XVE
XVEL6B5 | Main | light source | Integral flash discharge tube, orange
XVEL6B5 | Main | bulb type | Flash discharge tube
XVEL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVEL6B5 | Complementary | mounting diameter | 70 mm
XVEL6B5 | Complementary | flash energy | 1 J
XVEL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVEL6B5 | Complementary | marking | CE
XVEL6B5 | Complementary | short-circuit protection | 0.63 A
XVEL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVEL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVEL6B5 | Complementary | current consumption | < 145 mA AC ¦ < 85 mA DC
XVEL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVEL6B5 | Complementary | flashing frequency | 1 Hz
XVEL6B5 | Complementary | CAD overall width | 70 mm
XVEL6B5 | Complementary | CAD overall height | 129 mm
XVEL6B5 | Complementary | CAD overall depth | 70 mm
XVEL6B5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVEL6B5 | Complementary | net weight | 0.27 kg
XVEL6B5 | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVEL6B5 | Environment | product certifications | UL ¦ CSA ¦ CCC
XVEL6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVEL6B5 | Environment | ambient air temperature for operation | -25…55 °C
XVEL6B5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 ¦ Class I plastic tube mounting conforming to IEC 61140
XVEL6B5 | Environment | protective treatment | TC
XVEL6B5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVEL6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVEL6B5 | Offer Sustainability | Mercury free | Yes
XVEL6B5 | Offer Sustainability | RoHS exemption information | Yes
XVEL6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVEL6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVEL6B5 | Contractual warranty | Warranty | 18 months
XVEL6M5 | Main | range of product | Harmony XVE Optimum
XVEL6M5 | Main | product or component type | Complete illuminated beacon
XVEL6M5 | Main | beacon or indicator bank unit type | 1 base unit ¦ 1 illuminated unit ¦ 1 screw fixing cover ¦ 1 short fixing base
XVEL6M5 | Main | signalling type | Flashing
XVEL6M5 | Main | component name | XVE
XVEL6M5 | Main | light source | Integral flash discharge tube, orange
XVEL6M5 | Main | bulb type | Flash discharge tube
XVEL6M5 | Main | [Us] rated supply voltage | 230...240 V AC
XVEL6M5 | Complementary | mounting diameter | 70 mm
XVEL6M5 | Complementary | flash energy | 1 J
XVEL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVEL6M5 | Complementary | marking | CE
XVEL6M5 | Complementary | short-circuit protection | 0.16 A
XVEL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVEL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVEL6M5 | Complementary | current consumption | < 25 mA
XVEL6M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVEL6M5 | Complementary | flashing frequency | 1 Hz
XVEL6M5 | Complementary | CAD overall width | 70 mm
XVEL6M5 | Complementary | CAD overall height | 129 mm
XVEL6M5 | Complementary | CAD overall depth | 70 mm
XVEL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVEL6M5 | Complementary | net weight | 0.27 kg
XVEL6M5 | Environment | standards | EN/IEC 60947-5-1 ¦ EN/IEC 60947-1
XVEL6M5 | Environment | product certifications | CCC ¦ UL ¦ CSA
XVEL6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVEL6M5 | Environment | ambient air temperature for operation | -25…55 °C
XVEL6M5 | Environment | electrical shock protection class | Class I aluminium tube mounting conforming to IEC 61140 ¦ Class I plastic tube mounting conforming to IEC 61140
XVEL6M5 | Environment | protective treatment | TC
XVEL6M5 | Environment | IP degree of protection | IP40 any position except vertical position conforming to IEC 60529 ¦ IP42 vertical position conforming to IEC 60529
XVEL6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVEL6M5 | Offer Sustainability | Mercury free | Yes
XVEL6M5 | Offer Sustainability | RoHS exemption information | Yes
XVEL6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVEL6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVEL6M5 | Contractual warranty | Warranty | 18 months
XVBL33 | Main | range of product | Harmony XVB Universal
XVBL33 | Main | product or component type | Complete beacon
XVBL33 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL33 | Main | signalling type | Steady
XVBL33 | Main | mounting diameter | 70 mm
XVBL33 | Main | component name | XVBL
XVBL33 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL33 | Main | light source | Bulb not included, green
XVBL33 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL33 | Main | [Us] rated supply voltage | <= 250 V
XVBL33 | Main | maximum power dissipation in W | 7 W
XVBL33 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL33 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL33 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL33 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL33 | Complementary | CAD overall width | 70 mm
XVBL33 | Complementary | CAD overall height | 139 mm
XVBL33 | Complementary | CAD overall depth | 70 mm
XVBL33 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL33 | Complementary | net weight | 0.26 kg
XVBL33 | Environment | pollution degree | 2
XVBL33 | Environment | product certifications | GOST ¦ CCC ¦ UL 508 ¦ CSA C22-2 No 14
XVBL33 | Environment | standards | EN/IEC 60947-5-1
XVBL33 | Environment | protective treatment | TC
XVBL33 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL33 | Environment | ambient air temperature for storage | -40…70 °C
XVBL33 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL33 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL33 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL33 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL33 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL33 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL33 | Offer Sustainability | Mercury free | Yes
XVBL33 | Offer Sustainability | RoHS exemption information | Yes
XVBL33 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL33 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL33 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL33 | Contractual warranty | Warranty | 18 months
XVBL34 | Main | range of product | Harmony XVB Universal
XVBL34 | Main | product or component type | Complete beacon
XVBL34 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL34 | Main | signalling type | Steady
XVBL34 | Main | mounting diameter | 70 mm
XVBL34 | Main | component name | XVBL
XVBL34 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL34 | Main | light source | Bulb not included, red
XVBL34 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL34 | Main | [Us] rated supply voltage | <= 250 V
XVBL34 | Main | maximum power dissipation in W | 7 W
XVBL34 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL34 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL34 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL34 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL34 | Complementary | CAD overall width | 70 mm
XVBL34 | Complementary | CAD overall height | 139 mm
XVBL34 | Complementary | CAD overall depth | 70 mm
XVBL34 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL34 | Complementary | net weight | 0.26 kg
XVBL34 | Environment | pollution degree | 2
XVBL34 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBL34 | Environment | standards | EN/IEC 60947-5-1
XVBL34 | Environment | protective treatment | TC
XVBL34 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL34 | Environment | ambient air temperature for storage | -40…70 °C
XVBL34 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL34 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL34 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL34 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL34 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL34 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL34 | Offer Sustainability | Mercury free | Yes
XVBL34 | Offer Sustainability | RoHS exemption information | Yes
XVBL34 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL34 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL34 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL34 | Contractual warranty | Warranty | 18 months
XVBL35 | Main | range of product | Harmony XVB Universal
XVBL35 | Main | product or component type | Complete beacon
XVBL35 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL35 | Main | signalling type | Steady
XVBL35 | Main | mounting diameter | 70 mm
XVBL35 | Main | component name | XVBL
XVBL35 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL35 | Main | light source | Bulb not included, orange
XVBL35 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL35 | Main | [Us] rated supply voltage | <= 250 V
XVBL35 | Main | maximum power dissipation in W | 7 W
XVBL35 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL35 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL35 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL35 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL35 | Complementary | CAD overall width | 70 mm
XVBL35 | Complementary | CAD overall height | 139 mm
XVBL35 | Complementary | CAD overall depth | 70 mm
XVBL35 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL35 | Complementary | net weight | 0.26 kg
XVBL35 | Environment | pollution degree | 2
XVBL35 | Environment | product certifications | CCC ¦ GOST ¦ UL 508 ¦ CSA C22-2 No 14
XVBL35 | Environment | standards | EN/IEC 60947-5-1
XVBL35 | Environment | protective treatment | TC
XVBL35 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL35 | Environment | ambient air temperature for storage | -40…70 °C
XVBL35 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL35 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL35 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL35 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL35 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL35 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL35 | Offer Sustainability | Mercury free | Yes
XVBL35 | Offer Sustainability | RoHS exemption information | Yes
XVBL35 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL35 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL35 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL35 | Contractual warranty | Warranty | 18 months
XVBL36 | Main | range of product | Harmony XVB Universal
XVBL36 | Main | product or component type | Complete beacon
XVBL36 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL36 | Main | signalling type | Steady
XVBL36 | Main | mounting diameter | 70 mm
XVBL36 | Main | component name | XVBL
XVBL36 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL36 | Main | light source | Bulb not included, blue
XVBL36 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL36 | Main | [Us] rated supply voltage | <= 250 V
XVBL36 | Main | maximum power dissipation in W | 7 W
XVBL36 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL36 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL36 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL36 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL36 | Complementary | CAD overall width | 70 mm
XVBL36 | Complementary | CAD overall height | 139 mm
XVBL36 | Complementary | CAD overall depth | 70 mm
XVBL36 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL36 | Complementary | net weight | 0.26 kg
XVBL36 | Environment | pollution degree | 2
XVBL36 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ CCC ¦ UL 508
XVBL36 | Environment | standards | EN/IEC 60947-5-1
XVBL36 | Environment | protective treatment | TC
XVBL36 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL36 | Environment | ambient air temperature for storage | -40…70 °C
XVBL36 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL36 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL36 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL36 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL36 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL36 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL36 | Offer Sustainability | Mercury free | Yes
XVBL36 | Offer Sustainability | RoHS exemption information | Yes
XVBL36 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL36 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL36 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL36 | Contractual warranty | Warranty | 18 months
XVBL37 | Main | range of product | Harmony XVB Universal
XVBL37 | Main | product or component type | Complete beacon
XVBL37 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL37 | Main | signalling type | Steady
XVBL37 | Main | mounting diameter | 70 mm
XVBL37 | Main | component name | XVBL
XVBL37 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL37 | Main | light source | Bulb not included, clear
XVBL37 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL37 | Main | [Us] rated supply voltage | <= 250 V
XVBL37 | Main | maximum power dissipation in W | 7 W
XVBL37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL37 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL37 | Complementary | CAD overall width | 70 mm
XVBL37 | Complementary | CAD overall height | 139 mm
XVBL37 | Complementary | CAD overall depth | 70 mm
XVBL37 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL37 | Complementary | net weight | 0.26 kg
XVBL37 | Environment | pollution degree | 2
XVBL37 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBL37 | Environment | standards | EN/IEC 60947-5-1
XVBL37 | Environment | protective treatment | TC
XVBL37 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL37 | Environment | ambient air temperature for storage | -40…70 °C
XVBL37 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL37 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL37 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL37 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL37 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL37 | Offer Sustainability | Mercury free | Yes
XVBL37 | Offer Sustainability | RoHS exemption information | Yes
XVBL37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL37 | Contractual warranty | Warranty | 18 months
XVBL38 | Main | range of product | Harmony XVB Universal
XVBL38 | Main | product or component type | Complete beacon
XVBL38 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL38 | Main | signalling type | Steady
XVBL38 | Main | mounting diameter | 70 mm
XVBL38 | Main | component name | XVBL
XVBL38 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL38 | Main | light source | Bulb not included, yellow
XVBL38 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL38 | Main | [Us] rated supply voltage | <= 250 V
XVBL38 | Main | maximum power dissipation in W | 7 W
XVBL38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL38 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL38 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL38 | Complementary | CAD overall width | 70 mm
XVBL38 | Complementary | CAD overall height | 139 mm
XVBL38 | Complementary | CAD overall depth | 70 mm
XVBL38 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL38 | Complementary | net weight | 0.26 kg
XVBL38 | Environment | pollution degree | 2
XVBL38 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBL38 | Environment | standards | EN/IEC 60947-5-1
XVBL38 | Environment | protective treatment | TC
XVBL38 | Environment | ambient air temperature for operation | -25…50 °C: LED ¦ -25…70 °C: incandescent
XVBL38 | Environment | ambient air temperature for storage | -40…70 °C
XVBL38 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL38 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL38 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL38 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL38 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL38 | Offer Sustainability | Mercury free | Yes
XVBL38 | Offer Sustainability | RoHS exemption information | Yes
XVBL38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL38 | Contractual warranty | Warranty | 18 months
XVBL4B3 | Main | range of product | Harmony XVB Universal
XVBL4B3 | Main | product or component type | Complete beacon
XVBL4B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B3 | Main | signalling type | Flashing
XVBL4B3 | Main | mounting diameter | 70 mm
XVBL4B3 | Main | component name | XVBL
XVBL4B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B3 | Main | light source | Bulb not included, green
XVBL4B3 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B3 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B3 | Main | maximum power dissipation in W | 7 W
XVBL4B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4B3 | Complementary | flashing frequency | 1 Hz
XVBL4B3 | Complementary | CAD overall width | 70 mm
XVBL4B3 | Complementary | CAD overall height | 139 mm
XVBL4B3 | Complementary | CAD overall depth | 70 mm
XVBL4B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4B3 | Complementary | net weight | 0.28 kg
XVBL4B3 | Environment | pollution degree | 2
XVBL4B3 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBL4B3 | Environment | standards | EN/IEC 60947-5-1
XVBL4B3 | Environment | protective treatment | TC
XVBL4B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B3 | Offer Sustainability | Mercury free | Yes
XVBL4B3 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B3 | Contractual warranty | Warranty | 18 months
XVBL4B4 | Main | range of product | Harmony XVB Universal
XVBL4B4 | Main | product or component type | Complete beacon
XVBL4B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B4 | Main | signalling type | Flashing
XVBL4B4 | Main | mounting diameter | 70 mm
XVBL4B4 | Main | component name | XVBL
XVBL4B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B4 | Main | light source | Bulb not included, red
XVBL4B4 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B4 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B4 | Main | maximum power dissipation in W | 7 W
XVBL4B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL4B4 | Complementary | flashing frequency | 1 Hz
XVBL4B4 | Complementary | CAD overall width | 70 mm
XVBL4B4 | Complementary | CAD overall height | 139 mm
XVBL4B4 | Complementary | CAD overall depth | 70 mm
XVBL4B4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4B4 | Complementary | net weight | 0.28 kg
XVBL4B4 | Environment | pollution degree | 2
XVBL4B4 | Environment | product certifications | UL 508 ¦ CSA C22-2 No 14 ¦ GOST ¦ CCC
XVBL4B4 | Environment | standards | EN/IEC 60947-5-1
XVBL4B4 | Environment | protective treatment | TC
XVBL4B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B4 | Offer Sustainability | Mercury free | Yes
XVBL4B4 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B4 | Contractual warranty | Warranty | 18 months
XVBL4B5 | Main | range of product | Harmony XVB Universal
XVBL4B5 | Main | product or component type | Complete beacon
XVBL4B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B5 | Main | signalling type | Flashing
XVBL4B5 | Main | mounting diameter | 70 mm
XVBL4B5 | Main | component name | XVBL
XVBL4B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B5 | Main | light source | Bulb not included, orange
XVBL4B5 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B5 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B5 | Main | maximum power dissipation in W | 7 W
XVBL4B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4B5 | Complementary | flashing frequency | 1 Hz
XVBL4B5 | Complementary | CAD overall width | 70 mm
XVBL4B5 | Complementary | CAD overall height | 139 mm
XVBL4B5 | Complementary | CAD overall depth | 70 mm
XVBL4B5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL4B5 | Complementary | net weight | 0.28 kg
XVBL4B5 | Environment | pollution degree | 2
XVBL4B5 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ CCC ¦ UL 508
XVBL4B5 | Environment | standards | EN/IEC 60947-5-1
XVBL4B5 | Environment | protective treatment | TC
XVBL4B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B5 | Offer Sustainability | Mercury free | Yes
XVBL4B5 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B5 | Contractual warranty | Warranty | 18 months
XVBL4B6 | Main | range of product | Harmony XVB Universal
XVBL4B6 | Main | product or component type | Complete beacon
XVBL4B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B6 | Main | signalling type | Flashing
XVBL4B6 | Main | mounting diameter | 70 mm
XVBL4B6 | Main | component name | XVBL
XVBL4B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B6 | Main | light source | Bulb not included, blue
XVBL4B6 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B6 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B6 | Main | maximum power dissipation in W | 7 W
XVBL4B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4B6 | Complementary | flashing frequency | 1 Hz
XVBL4B6 | Complementary | CAD overall width | 70 mm
XVBL4B6 | Complementary | CAD overall height | 139 mm
XVBL4B6 | Complementary | CAD overall depth | 70 mm
XVBL4B6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4B6 | Complementary | net weight | 0.28 kg
XVBL4B6 | Environment | pollution degree | 2
XVBL4B6 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL4B6 | Environment | standards | EN/IEC 60947-5-1
XVBL4B6 | Environment | protective treatment | TC
XVBL4B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B6 | Offer Sustainability | Mercury free | Yes
XVBL4B6 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B6 | Contractual warranty | Warranty | 18 months
XVBL4B7 | Main | range of product | Harmony XVB Universal
XVBL4B7 | Main | product or component type | Complete beacon
XVBL4B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B7 | Main | signalling type | Flashing
XVBL4B7 | Main | mounting diameter | 70 mm
XVBL4B7 | Main | component name | XVBL
XVBL4B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B7 | Main | light source | Bulb not included, clear
XVBL4B7 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B7 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B7 | Main | maximum power dissipation in W | 7 W
XVBL4B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4B7 | Complementary | flashing frequency | 1 Hz
XVBL4B7 | Complementary | CAD overall width | 70 mm
XVBL4B7 | Complementary | CAD overall height | 139 mm
XVBL4B7 | Complementary | CAD overall depth | 70 mm
XVBL4B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL4B7 | Complementary | net weight | 0.28 kg
XVBL4B7 | Environment | pollution degree | 2
XVBL4B7 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL4B7 | Environment | standards | EN/IEC 60947-5-1
XVBL4B7 | Environment | protective treatment | TC
XVBL4B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B7 | Offer Sustainability | Mercury free | Yes
XVBL4B7 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B7 | Contractual warranty | Warranty | 18 months
XVBL4B8 | Main | range of product | Harmony XVB Universal
XVBL4B8 | Main | product or component type | Complete beacon
XVBL4B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4B8 | Main | signalling type | Flashing
XVBL4B8 | Main | mounting diameter | 70 mm
XVBL4B8 | Main | component name | XVBL
XVBL4B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4B8 | Main | light source | Bulb not included, yellow
XVBL4B8 | Main | bulb type | Incandescent ¦ Incandescent with BA 15d base ¦ Protected LED
XVBL4B8 | Main | [Us] rated supply voltage | 24 V AC ¦ 24...48 V DC
XVBL4B8 | Main | maximum power dissipation in W | 7 W
XVBL4B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL4B8 | Complementary | flashing frequency | 1 Hz
XVBL4B8 | Complementary | CAD overall width | 70 mm
XVBL4B8 | Complementary | CAD overall height | 139 mm
XVBL4B8 | Complementary | CAD overall depth | 70 mm
XVBL4B8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4B8 | Complementary | net weight | 0.28 kg
XVBL4B8 | Environment | pollution degree | 2
XVBL4B8 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL4B8 | Environment | standards | EN/IEC 60947-5-1
XVBL4B8 | Environment | protective treatment | TC
XVBL4B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4B8 | Offer Sustainability | Mercury free | Yes
XVBL4B8 | Offer Sustainability | RoHS exemption information | Yes
XVBL4B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4B8 | Contractual warranty | Warranty | 18 months
XVBL4M3 | Main | range of product | Harmony XVB Universal
XVBL4M3 | Main | product or component type | Complete beacon
XVBL4M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4M3 | Main | signalling type | Flashing
XVBL4M3 | Main | mounting diameter | 70 mm
XVBL4M3 | Main | component name | XVBL
XVBL4M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4M3 | Main | light source | Bulb not included, green
XVBL4M3 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL4M3 | Main | [Us] rated supply voltage | 48...230 V AC
XVBL4M3 | Main | maximum power dissipation in W | 7 W
XVBL4M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL4M3 | Complementary | flashing frequency | 1 Hz
XVBL4M3 | Complementary | CAD overall width | 70 mm
XVBL4M3 | Complementary | CAD overall height | 139 mm
XVBL4M3 | Complementary | CAD overall depth | 70 mm
XVBL4M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4M3 | Complementary | net weight | 0.28 kg
XVBL4M3 | Environment | pollution degree | 2
XVBL4M3 | Environment | product certifications | CCC ¦ UL 508 ¦ CSA C22-2 No 14 ¦ GOST
XVBL4M3 | Environment | standards | EN/IEC 60947-5-1
XVBL4M3 | Environment | protective treatment | TC
XVBL4M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4M3 | Offer Sustainability | Mercury free | Yes
XVBL4M3 | Offer Sustainability | RoHS exemption information | Yes
XVBL4M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4M3 | Contractual warranty | Warranty | 18 months
XVBL4M4 | Main | range of product | Harmony XVB Universal
XVBL4M4 | Main | product or component type | Complete beacon
XVBL4M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4M4 | Main | signalling type | Flashing
XVBL4M4 | Main | mounting diameter | 70 mm
XVBL4M4 | Main | component name | XVBL
XVBL4M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4M4 | Main | light source | Bulb not included, red
XVBL4M4 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL4M4 | Main | [Us] rated supply voltage | 48...230 V AC
XVBL4M4 | Main | maximum power dissipation in W | 7 W
XVBL4M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4M4 | Complementary | flashing frequency | 1 Hz
XVBL4M4 | Complementary | CAD overall width | 70 mm
XVBL4M4 | Complementary | CAD overall height | 139 mm
XVBL4M4 | Complementary | CAD overall depth | 70 mm
XVBL4M4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL4M4 | Complementary | net weight | 0.28 kg
XVBL4M4 | Environment | pollution degree | 2
XVBL4M4 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBL4M4 | Environment | standards | EN/IEC 60947-5-1
XVBL4M4 | Environment | protective treatment | TC
XVBL4M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4M4 | Offer Sustainability | Mercury free | Yes
XVBL4M4 | Offer Sustainability | RoHS exemption information | Yes
XVBL4M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4M4 | Contractual warranty | Warranty | 18 months
XVBL4M5 | Main | range of product | Harmony XVB Universal
XVBL4M5 | Main | product or component type | Complete beacon
XVBL4M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4M5 | Main | signalling type | Flashing
XVBL4M5 | Main | mounting diameter | 70 mm
XVBL4M5 | Main | component name | XVBL
XVBL4M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4M5 | Main | light source | Bulb not included, orange
XVBL4M5 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL4M5 | Main | [Us] rated supply voltage | 48...230 V AC
XVBL4M5 | Main | maximum power dissipation in W | 7 W
XVBL4M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL4M5 | Complementary | flashing frequency | 1 Hz
XVBL4M5 | Complementary | CAD overall width | 70 mm
XVBL4M5 | Complementary | CAD overall height | 139 mm
XVBL4M5 | Complementary | CAD overall depth | 70 mm
XVBL4M5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL4M5 | Complementary | net weight | 0.28 kg
XVBL4M5 | Environment | pollution degree | 2
XVBL4M5 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ CCC ¦ GOST
XVBL4M5 | Environment | standards | EN/IEC 60947-5-1
XVBL4M5 | Environment | protective treatment | TC
XVBL4M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4M5 | Offer Sustainability | Mercury free | Yes
XVBL4M5 | Offer Sustainability | RoHS exemption information | Yes
XVBL4M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4M5 | Contractual warranty | Warranty | 18 months
XVBL4M6 | Main | range of product | Harmony XVB Universal
XVBL4M6 | Main | product or component type | Complete beacon
XVBL4M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4M6 | Main | signalling type | Flashing
XVBL4M6 | Main | mounting diameter | 70 mm
XVBL4M6 | Main | component name | XVBL
XVBL4M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4M6 | Main | light source | Bulb not included, blue
XVBL4M6 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL4M6 | Main | [Us] rated supply voltage | 48...230 V AC
XVBL4M6 | Main | maximum power dissipation in W | 7 W
XVBL4M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL4M6 | Complementary | flashing frequency | 1 Hz
XVBL4M6 | Complementary | CAD overall width | 70 mm
XVBL4M6 | Complementary | CAD overall height | 139 mm
XVBL4M6 | Complementary | CAD overall depth | 70 mm
XVBL4M6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4M6 | Complementary | net weight | 0.28 kg
XVBL4M6 | Environment | pollution degree | 2
XVBL4M6 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBL4M6 | Environment | standards | EN/IEC 60947-5-1
XVBL4M6 | Environment | protective treatment | TC
XVBL4M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4M6 | Offer Sustainability | Mercury free | Yes
XVBL4M6 | Offer Sustainability | RoHS exemption information | Yes
XVBL4M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4M6 | Contractual warranty | Warranty | 18 months
XVBL4M7 | Main | range of product | Harmony XVB Universal
XVBL4M7 | Main | product or component type | Complete beacon
XVBL4M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL4M7 | Main | signalling type | Flashing
XVBL4M7 | Main | mounting diameter | 70 mm
XVBL4M7 | Main | component name | XVBL
XVBL4M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL4M7 | Main | light source | Bulb not included, clear
XVBL4M7 | Main | bulb type | Incandescent with BA 15d base ¦ Protected LED
XVBL4M7 | Main | [Us] rated supply voltage | 48...230 V AC
XVBL4M7 | Main | maximum power dissipation in W | 7 W
XVBL4M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL4M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL4M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL4M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL4M7 | Complementary | flashing frequency | 1 Hz
XVBL4M7 | Complementary | CAD overall width | 70 mm
XVBL4M7 | Complementary | CAD overall height | 139 mm
XVBL4M7 | Complementary | CAD overall depth | 70 mm
XVBL4M7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL4M7 | Complementary | net weight | 0.28 kg
XVBL4M7 | Environment | pollution degree | 2
XVBL4M7 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL4M7 | Environment | standards | EN/IEC 60947-5-1
XVBL4M7 | Environment | protective treatment | TC
XVBL4M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL4M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL4M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL4M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL4M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL4M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL4M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL4M7 | Offer Sustainability | Mercury free | Yes
XVBL4M7 | Offer Sustainability | RoHS exemption information | Yes
XVBL4M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL4M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL4M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL4M7 | Contractual warranty | Warranty | 18 months
XVBL0B3 | Main | range of product | Harmony XVB Universal
XVBL0B3 | Main | product or component type | Complete beacon
XVBL0B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B3 | Main | signalling type | Steady
XVBL0B3 | Main | mounting diameter | 70 mm
XVBL0B3 | Main | component name | XVBL
XVBL0B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B3 | Main | light source | Integral LED, green
XVBL0B3 | Main | bulb type | Protected LED
XVBL0B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B3 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0B3 | Complementary | CAD overall width | 70 mm
XVBL0B3 | Complementary | CAD overall height | 139 mm
XVBL0B3 | Complementary | CAD overall depth | 70 mm
XVBL0B3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0B3 | Complementary | net weight | 0.27 kg
XVBL0B3 | Environment | pollution degree | 2
XVBL0B3 | Environment | product certifications | GOST ¦ UL 508 ¦ CCC ¦ CSA C22-2 No 14
XVBL0B3 | Environment | standards | EN/IEC 60947-5-1
XVBL0B3 | Environment | protective treatment | TC
XVBL0B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B3 | Offer Sustainability | Mercury free | Yes
XVBL0B3 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B3 | Contractual warranty | Warranty | 18 months
XVBL0B4 | Main | range of product | Harmony XVB Universal
XVBL0B4 | Main | product or component type | Complete beacon
XVBL0B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B4 | Main | signalling type | Steady
XVBL0B4 | Main | mounting diameter | 70 mm
XVBL0B4 | Main | component name | XVBL
XVBL0B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B4 | Main | light source | Integral LED, red
XVBL0B4 | Main | bulb type | Protected LED
XVBL0B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B4 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0B4 | Complementary | CAD overall width | 70 mm
XVBL0B4 | Complementary | CAD overall height | 139 mm
XVBL0B4 | Complementary | CAD overall depth | 70 mm
XVBL0B4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0B4 | Complementary | net weight | 0.27 kg
XVBL0B4 | Environment | pollution degree | 2
XVBL0B4 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ GOST ¦ CCC
XVBL0B4 | Environment | standards | EN/IEC 60947-5-1
XVBL0B4 | Environment | protective treatment | TC
XVBL0B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B4 | Offer Sustainability | Mercury free | Yes
XVBL0B4 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B4 | Contractual warranty | Warranty | 18 months
XVBL0B5 | Main | range of product | Harmony XVB Universal
XVBL0B5 | Main | product or component type | Complete beacon
XVBL0B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B5 | Main | signalling type | Steady
XVBL0B5 | Main | mounting diameter | 70 mm
XVBL0B5 | Main | component name | XVBL
XVBL0B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B5 | Main | light source | Integral LED, orange
XVBL0B5 | Main | bulb type | Protected LED
XVBL0B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B5 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0B5 | Complementary | CAD overall width | 70 mm
XVBL0B5 | Complementary | CAD overall height | 139 mm
XVBL0B5 | Complementary | CAD overall depth | 70 mm
XVBL0B5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0B5 | Complementary | net weight | 0.27 kg
XVBL0B5 | Environment | pollution degree | 2
XVBL0B5 | Environment | product certifications | GOST ¦ UL 508 ¦ CSA C22-2 No 14 ¦ CCC
XVBL0B5 | Environment | standards | EN/IEC 60947-5-1
XVBL0B5 | Environment | protective treatment | TC
XVBL0B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B5 | Offer Sustainability | Mercury free | Yes
XVBL0B5 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B5 | Contractual warranty | Warranty | 18 months
XVBL0B6 | Main | range of product | Harmony XVB Universal
XVBL0B6 | Main | product or component type | Complete beacon
XVBL0B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B6 | Main | signalling type | Steady
XVBL0B6 | Main | mounting diameter | 70 mm
XVBL0B6 | Main | component name | XVBL
XVBL0B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B6 | Main | light source | Integral LED, blue
XVBL0B6 | Main | bulb type | Protected LED
XVBL0B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B6 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0B6 | Complementary | CAD overall width | 70 mm
XVBL0B6 | Complementary | CAD overall height | 139 mm
XVBL0B6 | Complementary | CAD overall depth | 70 mm
XVBL0B6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0B6 | Complementary | net weight | 0.27 kg
XVBL0B6 | Environment | pollution degree | 2
XVBL0B6 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBL0B6 | Environment | standards | EN/IEC 60947-5-1
XVBL0B6 | Environment | protective treatment | TC
XVBL0B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B6 | Offer Sustainability | Mercury free | Yes
XVBL0B6 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B6 | Contractual warranty | Warranty | 18 months
XVBL0B7 | Main | range of product | Harmony XVB Universal
XVBL0B7 | Main | product or component type | Complete beacon
XVBL0B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B7 | Main | signalling type | Steady
XVBL0B7 | Main | mounting diameter | 70 mm
XVBL0B7 | Main | component name | XVBL
XVBL0B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B7 | Main | light source | Integral LED, clear
XVBL0B7 | Main | bulb type | Protected LED
XVBL0B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B7 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0B7 | Complementary | CAD overall width | 70 mm
XVBL0B7 | Complementary | CAD overall height | 139 mm
XVBL0B7 | Complementary | CAD overall depth | 70 mm
XVBL0B7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0B7 | Complementary | net weight | 0.27 kg
XVBL0B7 | Environment | pollution degree | 2
XVBL0B7 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ CCC ¦ UL 508
XVBL0B7 | Environment | standards | EN/IEC 60947-5-1
XVBL0B7 | Environment | protective treatment | TC
XVBL0B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B7 | Offer Sustainability | Mercury free | Yes
XVBL0B7 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B7 | Contractual warranty | Warranty | 18 months
XVBL0B8 | Main | range of product | Harmony XVB Universal
XVBL0B8 | Main | product or component type | Complete beacon
XVBL0B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0B8 | Main | signalling type | Steady
XVBL0B8 | Main | mounting diameter | 70 mm
XVBL0B8 | Main | component name | XVBL
XVBL0B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0B8 | Main | light source | Integral LED, yellow
XVBL0B8 | Main | bulb type | Protected LED
XVBL0B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL0B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0B8 | Complementary | current consumption | < 47 mA AC/DC
XVBL0B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0B8 | Complementary | CAD overall width | 70 mm
XVBL0B8 | Complementary | CAD overall height | 139 mm
XVBL0B8 | Complementary | CAD overall depth | 70 mm
XVBL0B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0B8 | Complementary | net weight | 0.27 kg
XVBL0B8 | Environment | pollution degree | 2
XVBL0B8 | Environment | product certifications | GOST ¦ UL 508 ¦ CSA C22-2 No 14 ¦ CCC
XVBL0B8 | Environment | standards | EN/IEC 60947-5-1
XVBL0B8 | Environment | protective treatment | TC
XVBL0B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0B8 | Offer Sustainability | Mercury free | Yes
XVBL0B8 | Offer Sustainability | RoHS exemption information | Yes
XVBL0B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0B8 | Contractual warranty | Warranty | 18 months
XVBL0G3 | Main | range of product | Harmony XVB Universal
XVBL0G3 | Main | product or component type | Complete beacon
XVBL0G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G3 | Main | signalling type | Steady
XVBL0G3 | Main | mounting diameter | 70 mm
XVBL0G3 | Main | component name | XVBL
XVBL0G3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G3 | Main | light source | Integral LED, green
XVBL0G3 | Main | bulb type | Protected LED
XVBL0G3 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G3 | Complementary | current consumption | < 17 mA AC
XVBL0G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0G3 | Complementary | CAD overall width | 70 mm
XVBL0G3 | Complementary | CAD overall height | 139 mm
XVBL0G3 | Complementary | CAD overall depth | 70 mm
XVBL0G3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0G3 | Complementary | net weight | 0.27 kg
XVBL0G3 | Environment | pollution degree | 2
XVBL0G3 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBL0G3 | Environment | standards | EN/IEC 60947-5-1
XVBL0G3 | Environment | protective treatment | TC
XVBL0G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G3 | Offer Sustainability | Mercury free | Yes
XVBL0G3 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G3 | Contractual warranty | Warranty | 18 months
XVBL0G4 | Main | range of product | Harmony XVB Universal
XVBL0G4 | Main | product or component type | Complete beacon
XVBL0G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G4 | Main | signalling type | Steady
XVBL0G4 | Main | mounting diameter | 70 mm
XVBL0G4 | Main | component name | XVBL
XVBL0G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G4 | Main | light source | Integral LED, red
XVBL0G4 | Main | bulb type | Protected LED
XVBL0G4 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G4 | Complementary | current consumption | < 17 mA AC
XVBL0G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0G4 | Complementary | CAD overall width | 70 mm
XVBL0G4 | Complementary | CAD overall height | 139 mm
XVBL0G4 | Complementary | CAD overall depth | 70 mm
XVBL0G4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0G4 | Complementary | net weight | 0.27 kg
XVBL0G4 | Environment | pollution degree | 2
XVBL0G4 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ GOST ¦ CCC
XVBL0G4 | Environment | standards | EN/IEC 60947-5-1
XVBL0G4 | Environment | protective treatment | TC
XVBL0G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G4 | Offer Sustainability | Mercury free | Yes
XVBL0G4 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G4 | Contractual warranty | Warranty | 18 months
XVBL0G5 | Main | range of product | Harmony XVB Universal
XVBL0G5 | Main | product or component type | Complete beacon
XVBL0G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G5 | Main | signalling type | Steady
XVBL0G5 | Main | mounting diameter | 70 mm
XVBL0G5 | Main | component name | XVBL
XVBL0G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G5 | Main | light source | Integral LED, orange
XVBL0G5 | Main | bulb type | Protected LED
XVBL0G5 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G5 | Complementary | current consumption | < 17 mA AC
XVBL0G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0G5 | Complementary | CAD overall width | 70 mm
XVBL0G5 | Complementary | CAD overall height | 139 mm
XVBL0G5 | Complementary | CAD overall depth | 70 mm
XVBL0G5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0G5 | Complementary | net weight | 0.27 kg
XVBL0G5 | Environment | pollution degree | 2
XVBL0G5 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBL0G5 | Environment | standards | EN/IEC 60947-5-1
XVBL0G5 | Environment | protective treatment | TC
XVBL0G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G5 | Offer Sustainability | Mercury free | Yes
XVBL0G5 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G5 | Contractual warranty | Warranty | 18 months
XVBL0G6 | Main | range of product | Harmony XVB Universal
XVBL0G6 | Main | product or component type | Complete beacon
XVBL0G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G6 | Main | signalling type | Steady
XVBL0G6 | Main | mounting diameter | 70 mm
XVBL0G6 | Main | component name | XVBL
XVBL0G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G6 | Main | light source | Integral LED, blue
XVBL0G6 | Main | bulb type | Protected LED
XVBL0G6 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G6 | Complementary | current consumption | < 17 mA AC
XVBL0G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0G6 | Complementary | CAD overall width | 70 mm
XVBL0G6 | Complementary | CAD overall height | 139 mm
XVBL0G6 | Complementary | CAD overall depth | 70 mm
XVBL0G6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0G6 | Complementary | net weight | 0.27 kg
XVBL0G6 | Environment | pollution degree | 2
XVBL0G6 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ UL 508 ¦ CCC
XVBL0G6 | Environment | standards | EN/IEC 60947-5-1
XVBL0G6 | Environment | protective treatment | TC
XVBL0G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G6 | Offer Sustainability | Mercury free | Yes
XVBL0G6 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G6 | Contractual warranty | Warranty | 18 months
XVBL0G7 | Main | range of product | Harmony XVB Universal
XVBL0G7 | Main | product or component type | Complete beacon
XVBL0G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G7 | Main | signalling type | Steady
XVBL0G7 | Main | mounting diameter | 70 mm
XVBL0G7 | Main | component name | XVBL
XVBL0G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G7 | Main | light source | Integral LED, clear
XVBL0G7 | Main | bulb type | Protected LED
XVBL0G7 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G7 | Complementary | current consumption | < 17 mA AC
XVBL0G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0G7 | Complementary | CAD overall width | 70 mm
XVBL0G7 | Complementary | CAD overall height | 139 mm
XVBL0G7 | Complementary | CAD overall depth | 70 mm
XVBL0G7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0G7 | Complementary | net weight | 0.27 kg
XVBL0G7 | Environment | pollution degree | 2
XVBL0G7 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBL0G7 | Environment | standards | EN/IEC 60947-5-1
XVBL0G7 | Environment | protective treatment | TC
XVBL0G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G7 | Offer Sustainability | Mercury free | Yes
XVBL0G7 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G7 | Contractual warranty | Warranty | 18 months
XVBL0G8 | Main | range of product | Harmony XVB Universal
XVBL0G8 | Main | product or component type | Complete beacon
XVBL0G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0G8 | Main | signalling type | Steady
XVBL0G8 | Main | mounting diameter | 70 mm
XVBL0G8 | Main | component name | XVBL
XVBL0G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0G8 | Main | light source | Integral LED, yellow
XVBL0G8 | Main | bulb type | Protected LED
XVBL0G8 | Main | [Us] rated supply voltage | 120 V AC
XVBL0G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0G8 | Complementary | current consumption | < 17 mA AC
XVBL0G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0G8 | Complementary | CAD overall width | 70 mm
XVBL0G8 | Complementary | CAD overall height | 139 mm
XVBL0G8 | Complementary | CAD overall depth | 70 mm
XVBL0G8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0G8 | Complementary | net weight | 0.27 kg
XVBL0G8 | Environment | pollution degree | 2
XVBL0G8 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL0G8 | Environment | standards | EN/IEC 60947-5-1
XVBL0G8 | Environment | protective treatment | TC
XVBL0G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0G8 | Offer Sustainability | Mercury free | Yes
XVBL0G8 | Offer Sustainability | RoHS exemption information | Yes
XVBL0G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0G8 | Contractual warranty | Warranty | 18 months
XVBL0M3 | Main | range of product | Harmony XVB Universal
XVBL0M3 | Main | product or component type | Complete beacon
XVBL0M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M3 | Main | signalling type | Steady
XVBL0M3 | Main | mounting diameter | 70 mm
XVBL0M3 | Main | component name | XVBL
XVBL0M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M3 | Main | light source | Integral LED, green
XVBL0M3 | Main | bulb type | Protected LED
XVBL0M3 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M3 | Complementary | current consumption | < 17 mA AC
XVBL0M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0M3 | Complementary | CAD overall width | 70 mm
XVBL0M3 | Complementary | CAD overall height | 139 mm
XVBL0M3 | Complementary | CAD overall depth | 70 mm
XVBL0M3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0M3 | Complementary | net weight | 0.27 kg
XVBL0M3 | Environment | pollution degree | 2
XVBL0M3 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL0M3 | Environment | standards | EN/IEC 60947-5-1
XVBL0M3 | Environment | protective treatment | TC
XVBL0M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M3 | Offer Sustainability | Mercury free | Yes
XVBL0M3 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M3 | Contractual warranty | Warranty | 18 months
XVBL0M4 | Main | range of product | Harmony XVB Universal
XVBL0M4 | Main | product or component type | Complete beacon
XVBL0M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M4 | Main | signalling type | Steady
XVBL0M4 | Main | mounting diameter | 70 mm
XVBL0M4 | Main | component name | XVBL
XVBL0M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M4 | Main | light source | Integral LED, red
XVBL0M4 | Main | bulb type | Protected LED
XVBL0M4 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M4 | Complementary | current consumption | < 17 mA AC
XVBL0M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0M4 | Complementary | CAD overall width | 70 mm
XVBL0M4 | Complementary | CAD overall height | 139 mm
XVBL0M4 | Complementary | CAD overall depth | 70 mm
XVBL0M4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL0M4 | Complementary | net weight | 0.27 kg
XVBL0M4 | Environment | pollution degree | 2
XVBL0M4 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBL0M4 | Environment | standards | EN/IEC 60947-5-1
XVBL0M4 | Environment | protective treatment | TC
XVBL0M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M4 | Offer Sustainability | Mercury free | Yes
XVBL0M4 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M4 | Contractual warranty | Warranty | 18 months
XVBL0M5 | Main | range of product | Harmony XVB Universal
XVBL0M5 | Main | product or component type | Complete beacon
XVBL0M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M5 | Main | signalling type | Steady
XVBL0M5 | Main | mounting diameter | 70 mm
XVBL0M5 | Main | component name | XVBL
XVBL0M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M5 | Main | light source | Integral LED, orange
XVBL0M5 | Main | bulb type | Protected LED
XVBL0M5 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M5 | Complementary | current consumption | < 17 mA AC
XVBL0M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0M5 | Complementary | CAD overall width | 70 mm
XVBL0M5 | Complementary | CAD overall height | 139 mm
XVBL0M5 | Complementary | CAD overall depth | 70 mm
XVBL0M5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0M5 | Complementary | net weight | 0.27 kg
XVBL0M5 | Environment | pollution degree | 2
XVBL0M5 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL0M5 | Environment | standards | EN/IEC 60947-5-1
XVBL0M5 | Environment | protective treatment | TC
XVBL0M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M5 | Offer Sustainability | Mercury free | Yes
XVBL0M5 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M5 | Contractual warranty | Warranty | 18 months
XVBL0M6 | Main | range of product | Harmony XVB Universal
XVBL0M6 | Main | product or component type | Complete beacon
XVBL0M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M6 | Main | signalling type | Steady
XVBL0M6 | Main | mounting diameter | 70 mm
XVBL0M6 | Main | component name | XVBL
XVBL0M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M6 | Main | light source | Integral LED, blue
XVBL0M6 | Main | bulb type | Protected LED
XVBL0M6 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M6 | Complementary | current consumption | < 17 mA AC
XVBL0M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0M6 | Complementary | CAD overall width | 70 mm
XVBL0M6 | Complementary | CAD overall height | 139 mm
XVBL0M6 | Complementary | CAD overall depth | 70 mm
XVBL0M6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0M6 | Complementary | net weight | 0.27 kg
XVBL0M6 | Environment | pollution degree | 2
XVBL0M6 | Environment | product certifications | GOST ¦ CCC ¦ UL 508 ¦ CSA C22-2 No 14
XVBL0M6 | Environment | standards | EN/IEC 60947-5-1
XVBL0M6 | Environment | protective treatment | TC
XVBL0M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M6 | Offer Sustainability | Mercury free | Yes
XVBL0M6 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M6 | Contractual warranty | Warranty | 18 months
XVBL0M7 | Main | range of product | Harmony XVB Universal
XVBL0M7 | Main | product or component type | Complete beacon
XVBL0M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M7 | Main | signalling type | Steady
XVBL0M7 | Main | mounting diameter | 70 mm
XVBL0M7 | Main | component name | XVBL
XVBL0M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M7 | Main | light source | Integral LED, clear
XVBL0M7 | Main | bulb type | Protected LED
XVBL0M7 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M7 | Complementary | current consumption | < 17 mA AC
XVBL0M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL0M7 | Complementary | CAD overall width | 70 mm
XVBL0M7 | Complementary | CAD overall height | 139 mm
XVBL0M7 | Complementary | CAD overall depth | 70 mm
XVBL0M7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0M7 | Complementary | net weight | 0.27 kg
XVBL0M7 | Environment | pollution degree | 2
XVBL0M7 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBL0M7 | Environment | standards | EN/IEC 60947-5-1
XVBL0M7 | Environment | protective treatment | TC
XVBL0M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M7 | Offer Sustainability | Mercury free | Yes
XVBL0M7 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M7 | Contractual warranty | Warranty | 18 months
XVBL0M8 | Main | range of product | Harmony XVB Universal
XVBL0M8 | Main | product or component type | Complete beacon
XVBL0M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL0M8 | Main | signalling type | Steady
XVBL0M8 | Main | mounting diameter | 70 mm
XVBL0M8 | Main | component name | XVBL
XVBL0M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL0M8 | Main | light source | Integral LED, yellow
XVBL0M8 | Main | bulb type | Protected LED
XVBL0M8 | Main | [Us] rated supply voltage | 230 V AC
XVBL0M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL0M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL0M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL0M8 | Complementary | current consumption | < 17 mA AC
XVBL0M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL0M8 | Complementary | CAD overall width | 70 mm
XVBL0M8 | Complementary | CAD overall height | 139 mm
XVBL0M8 | Complementary | CAD overall depth | 70 mm
XVBL0M8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL0M8 | Complementary | net weight | 0.27 kg
XVBL0M8 | Environment | pollution degree | 2
XVBL0M8 | Environment | product certifications | CCC ¦ GOST ¦ UL 508 ¦ CSA C22-2 No 14
XVBL0M8 | Environment | standards | EN/IEC 60947-5-1
XVBL0M8 | Environment | protective treatment | TC
XVBL0M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL0M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL0M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL0M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL0M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL0M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL0M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL0M8 | Offer Sustainability | Mercury free | Yes
XVBL0M8 | Offer Sustainability | RoHS exemption information | Yes
XVBL0M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL0M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL0M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL0M8 | Contractual warranty | Warranty | 18 months
XVBL1B3 | Main | range of product | Harmony XVB Universal
XVBL1B3 | Main | product or component type | Complete beacon
XVBL1B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B3 | Main | signalling type | Flashing
XVBL1B3 | Main | mounting diameter | 70 mm
XVBL1B3 | Main | component name | XVBL
XVBL1B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B3 | Main | light source | Integral LED, green
XVBL1B3 | Main | bulb type | Protected LED
XVBL1B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B3 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1B3 | Complementary | flashing frequency | 1 Hz
XVBL1B3 | Complementary | CAD overall width | 70 mm
XVBL1B3 | Complementary | CAD overall height | 139 mm
XVBL1B3 | Complementary | CAD overall depth | 70 mm
XVBL1B3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1B3 | Complementary | net weight | 0.28 kg
XVBL1B3 | Environment | pollution degree | 2
XVBL1B3 | Environment | product certifications | CCC ¦ UL 508 ¦ CSA C22-2 No 14 ¦ GOST
XVBL1B3 | Environment | standards | EN/IEC 60947-5-1
XVBL1B3 | Environment | protective treatment | TC
XVBL1B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B3 | Offer Sustainability | Mercury free | Yes
XVBL1B3 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B3 | Contractual warranty | Warranty | 18 months
XVBL1B4 | Main | range of product | Harmony XVB Universal
XVBL1B4 | Main | product or component type | Complete beacon
XVBL1B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B4 | Main | signalling type | Flashing
XVBL1B4 | Main | mounting diameter | 70 mm
XVBL1B4 | Main | component name | XVBL
XVBL1B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B4 | Main | light source | Integral LED, red
XVBL1B4 | Main | bulb type | Protected LED
XVBL1B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B4 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1B4 | Complementary | flashing frequency | 1 Hz
XVBL1B4 | Complementary | CAD overall width | 70 mm
XVBL1B4 | Complementary | CAD overall height | 139 mm
XVBL1B4 | Complementary | CAD overall depth | 70 mm
XVBL1B4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1B4 | Complementary | net weight | 0.28 kg
XVBL1B4 | Environment | pollution degree | 2
XVBL1B4 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBL1B4 | Environment | standards | EN/IEC 60947-5-1
XVBL1B4 | Environment | protective treatment | TC
XVBL1B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B4 | Offer Sustainability | Mercury free | Yes
XVBL1B4 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B4 | Contractual warranty | Warranty | 18 months
XVBL1B5 | Main | range of product | Harmony XVB Universal
XVBL1B5 | Main | product or component type | Complete beacon
XVBL1B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B5 | Main | signalling type | Flashing
XVBL1B5 | Main | mounting diameter | 70 mm
XVBL1B5 | Main | component name | XVBL
XVBL1B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B5 | Main | light source | Integral LED, orange
XVBL1B5 | Main | bulb type | Protected LED
XVBL1B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B5 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1B5 | Complementary | flashing frequency | 1 Hz
XVBL1B5 | Complementary | CAD overall width | 70 mm
XVBL1B5 | Complementary | CAD overall height | 139 mm
XVBL1B5 | Complementary | CAD overall depth | 70 mm
XVBL1B5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1B5 | Complementary | net weight | 0.28 kg
XVBL1B5 | Environment | pollution degree | 2
XVBL1B5 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBL1B5 | Environment | standards | EN/IEC 60947-5-1
XVBL1B5 | Environment | protective treatment | TC
XVBL1B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B5 | Offer Sustainability | Mercury free | Yes
XVBL1B5 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B5 | Contractual warranty | Warranty | 18 months
XVBL1B6 | Main | range of product | Harmony XVB Universal
XVBL1B6 | Main | product or component type | Complete beacon
XVBL1B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B6 | Main | signalling type | Flashing
XVBL1B6 | Main | mounting diameter | 70 mm
XVBL1B6 | Main | component name | XVBL
XVBL1B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B6 | Main | light source | Integral LED, blue
XVBL1B6 | Main | bulb type | Protected LED
XVBL1B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B6 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1B6 | Complementary | flashing frequency | 1 Hz
XVBL1B6 | Complementary | CAD overall width | 70 mm
XVBL1B6 | Complementary | CAD overall height | 139 mm
XVBL1B6 | Complementary | CAD overall depth | 70 mm
XVBL1B6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1B6 | Complementary | net weight | 0.28 kg
XVBL1B6 | Environment | pollution degree | 2
XVBL1B6 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL1B6 | Environment | standards | EN/IEC 60947-5-1
XVBL1B6 | Environment | protective treatment | TC
XVBL1B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B6 | Offer Sustainability | Mercury free | Yes
XVBL1B6 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B6 | Contractual warranty | Warranty | 18 months
XVBL1B7 | Main | range of product | Harmony XVB Universal
XVBL1B7 | Main | product or component type | Complete beacon
XVBL1B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B7 | Main | signalling type | Flashing
XVBL1B7 | Main | mounting diameter | 70 mm
XVBL1B7 | Main | component name | XVBL
XVBL1B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B7 | Main | light source | Integral LED, clear
XVBL1B7 | Main | bulb type | Protected LED
XVBL1B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B7 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1B7 | Complementary | flashing frequency | 1 Hz
XVBL1B7 | Complementary | CAD overall width | 70 mm
XVBL1B7 | Complementary | CAD overall height | 139 mm
XVBL1B7 | Complementary | CAD overall depth | 70 mm
XVBL1B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1B7 | Complementary | net weight | 0.28 kg
XVBL1B7 | Environment | pollution degree | 2
XVBL1B7 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL1B7 | Environment | standards | EN/IEC 60947-5-1
XVBL1B7 | Environment | protective treatment | TC
XVBL1B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B7 | Offer Sustainability | Mercury free | Yes
XVBL1B7 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B7 | Contractual warranty | Warranty | 18 months
XVBL1B8 | Main | range of product | Harmony XVB Universal
XVBL1B8 | Main | product or component type | Complete beacon
XVBL1B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1B8 | Main | signalling type | Flashing
XVBL1B8 | Main | mounting diameter | 70 mm
XVBL1B8 | Main | component name | XVBL
XVBL1B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1B8 | Main | light source | Integral LED, yellow
XVBL1B8 | Main | bulb type | Protected LED
XVBL1B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL1B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1B8 | Complementary | current consumption | < 47 mA AC/DC
XVBL1B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1B8 | Complementary | flashing frequency | 1 Hz
XVBL1B8 | Complementary | CAD overall width | 70 mm
XVBL1B8 | Complementary | CAD overall height | 139 mm
XVBL1B8 | Complementary | CAD overall depth | 70 mm
XVBL1B8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1B8 | Complementary | net weight | 0.28 kg
XVBL1B8 | Environment | pollution degree | 2
XVBL1B8 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL1B8 | Environment | standards | EN/IEC 60947-5-1
XVBL1B8 | Environment | protective treatment | TC
XVBL1B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1B8 | Offer Sustainability | Mercury free | Yes
XVBL1B8 | Offer Sustainability | RoHS exemption information | Yes
XVBL1B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1B8 | Contractual warranty | Warranty | 18 months
XVBL1G3 | Main | range of product | Harmony XVB Universal
XVBL1G3 | Main | product or component type | Complete beacon
XVBL1G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G3 | Main | signalling type | Flashing
XVBL1G3 | Main | mounting diameter | 70 mm
XVBL1G3 | Main | component name | XVBL
XVBL1G3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G3 | Main | light source | Integral LED, green
XVBL1G3 | Main | bulb type | Protected LED
XVBL1G3 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G3 | Complementary | current consumption | < 17 mA AC
XVBL1G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1G3 | Complementary | flashing frequency | 1 Hz
XVBL1G3 | Complementary | CAD overall width | 70 mm
XVBL1G3 | Complementary | CAD overall height | 139 mm
XVBL1G3 | Complementary | CAD overall depth | 70 mm
XVBL1G3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1G3 | Complementary | net weight | 0.28 kg
XVBL1G3 | Environment | pollution degree | 2
XVBL1G3 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBL1G3 | Environment | standards | EN/IEC 60947-5-1
XVBL1G3 | Environment | protective treatment | TC
XVBL1G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1G3 | Offer Sustainability | Mercury free | Yes
XVBL1G3 | Offer Sustainability | RoHS exemption information | Yes
XVBL1G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1G3 | Contractual warranty | Warranty | 18 months
XVBL1G4 | Main | range of product | Harmony XVB Universal
XVBL1G4 | Main | product or component type | Complete beacon
XVBL1G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G4 | Main | signalling type | Flashing
XVBL1G4 | Main | mounting diameter | 70 mm
XVBL1G4 | Main | component name | XVBL
XVBL1G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G4 | Main | light source | Integral LED, red
XVBL1G4 | Main | bulb type | Protected LED
XVBL1G4 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G4 | Complementary | current consumption | < 17 mA AC
XVBL1G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1G4 | Complementary | flashing frequency | 1 Hz
XVBL1G4 | Complementary | CAD overall width | 70 mm
XVBL1G4 | Complementary | CAD overall height | 139 mm
XVBL1G4 | Complementary | CAD overall depth | 70 mm
XVBL1G4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1G4 | Complementary | net weight | 0.28 kg
XVBL1G4 | Environment | pollution degree | 2
XVBL1G4 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBL1G4 | Environment | standards | EN/IEC 60947-5-1
XVBL1G4 | Environment | protective treatment | TC
XVBL1G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1G4 | Offer Sustainability | Mercury free | Yes
XVBL1G4 | Offer Sustainability | RoHS exemption information | Yes
XVBL1G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1G4 | Contractual warranty | Warranty | 18 months
XVBL1G5 | Main | range of product | Harmony XVB Universal
XVBL1G5 | Main | product or component type | Complete beacon
XVBL1G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G5 | Main | signalling type | Flashing
XVBL1G5 | Main | mounting diameter | 70 mm
XVBL1G5 | Main | component name | XVBL
XVBL1G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G5 | Main | light source | Integral LED, orange
XVBL1G5 | Main | bulb type | Protected LED
XVBL1G5 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G5 | Complementary | current consumption | < 17 mA AC
XVBL1G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1G5 | Complementary | flashing frequency | 1 Hz
XVBL1G5 | Complementary | CAD overall width | 70 mm
XVBL1G5 | Complementary | CAD overall height | 139 mm
XVBL1G5 | Complementary | CAD overall depth | 70 mm
XVBL1G5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1G5 | Complementary | net weight | 0.28 kg
XVBL1G5 | Environment | pollution degree | 2
XVBL1G5 | Environment | product certifications | CCC ¦ GOST ¦ UL 508 ¦ CSA C22-2 No 14
XVBL1G5 | Environment | standards | EN/IEC 60947-5-1
XVBL1G5 | Environment | protective treatment | TC
XVBL1G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1G5 | Offer Sustainability | Mercury free | Yes
XVBL1G5 | Offer Sustainability | RoHS exemption information | Yes
XVBL1G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1G5 | Contractual warranty | Warranty | 18 months
XVBL1G6 | Main | range of product | Harmony XVB Universal
XVBL1G6 | Main | product or component type | Complete beacon
XVBL1G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G6 | Main | signalling type | Flashing
XVBL1G6 | Main | mounting diameter | 70 mm
XVBL1G6 | Main | component name | XVBL
XVBL1G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G6 | Main | light source | Integral LED, blue
XVBL1G6 | Main | bulb type | Protected LED
XVBL1G6 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G6 | Complementary | current consumption | < 17 mA AC
XVBL1G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1G6 | Complementary | flashing frequency | 1 Hz
XVBL1G6 | Complementary | CAD overall width | 70 mm
XVBL1G6 | Complementary | CAD overall height | 139 mm
XVBL1G6 | Complementary | CAD overall depth | 70 mm
XVBL1G6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1G6 | Complementary | net weight | 0.28 kg
XVBL1G6 | Environment | pollution degree | 2
XVBL1G6 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL1G6 | Environment | standards | EN/IEC 60947-5-1
XVBL1G6 | Environment | protective treatment | TC
XVBL1G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1G6 | Offer Sustainability | Mercury free | Yes
XVBL1G6 | Offer Sustainability | RoHS exemption information | Yes
XVBL1G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1G6 | Contractual warranty | Warranty | 18 months
XVBL1G7 | Main | range of product | Harmony XVB Universal
XVBL1G7 | Main | product or component type | Complete beacon
XVBL1G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G7 | Main | signalling type | Flashing
XVBL1G7 | Main | mounting diameter | 70 mm
XVBL1G7 | Main | component name | XVBL
XVBL1G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G7 | Main | light source | Integral LED, clear
XVBL1G7 | Main | bulb type | Protected LED
XVBL1G7 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G7 | Complementary | current consumption | < 17 mA AC
XVBL1G7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1G7 | Complementary | flashing frequency | 1 Hz
XVBL1G7 | Complementary | CAD overall width | 70 mm
XVBL1G7 | Complementary | CAD overall height | 139 mm
XVBL1G7 | Complementary | CAD overall depth | 70 mm
XVBL1G7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1G7 | Complementary | net weight | 0.28 kg
XVBL1G7 | Environment | pollution degree | 2
XVBL1G7 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ CCC ¦ UL 508
XVBL1G7 | Environment | standards | EN/IEC 60947-5-1
XVBL1G7 | Environment | protective treatment | TC
XVBL1G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G7 | Contractual warranty | Warranty | 18 months
XVBL1G8 | Main | range of product | Harmony XVB Universal
XVBL1G8 | Main | product or component type | Complete beacon
XVBL1G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1G8 | Main | signalling type | Flashing
XVBL1G8 | Main | mounting diameter | 70 mm
XVBL1G8 | Main | component name | XVBL
XVBL1G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1G8 | Main | light source | Integral LED, yellow
XVBL1G8 | Main | bulb type | Protected LED
XVBL1G8 | Main | [Us] rated supply voltage | 120 V AC
XVBL1G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1G8 | Complementary | current consumption | < 17 mA AC
XVBL1G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1G8 | Complementary | flashing frequency | 1 Hz
XVBL1G8 | Complementary | CAD overall width | 70 mm
XVBL1G8 | Complementary | CAD overall height | 139 mm
XVBL1G8 | Complementary | CAD overall depth | 70 mm
XVBL1G8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1G8 | Complementary | net weight | 0.28 kg
XVBL1G8 | Environment | pollution degree | 2
XVBL1G8 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBL1G8 | Environment | standards | EN/IEC 60947-5-1
XVBL1G8 | Environment | protective treatment | TC
XVBL1G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1G8 | Offer Sustainability | Mercury free | Yes
XVBL1G8 | Offer Sustainability | RoHS exemption information | Yes
XVBL1G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1G8 | Contractual warranty | Warranty | 18 months
XVBL1M3 | Main | range of product | Harmony XVB Universal
XVBL1M3 | Main | product or component type | Complete beacon
XVBL1M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M3 | Main | signalling type | Flashing
XVBL1M3 | Main | mounting diameter | 70 mm
XVBL1M3 | Main | component name | XVBL
XVBL1M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M3 | Main | light source | Integral LED, green
XVBL1M3 | Main | bulb type | Protected LED
XVBL1M3 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M3 | Complementary | current consumption | < 17 mA AC
XVBL1M3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1M3 | Complementary | flashing frequency | 1 Hz
XVBL1M3 | Complementary | CAD overall width | 70 mm
XVBL1M3 | Complementary | CAD overall height | 139 mm
XVBL1M3 | Complementary | CAD overall depth | 70 mm
XVBL1M3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1M3 | Complementary | net weight | 0.28 kg
XVBL1M3 | Environment | pollution degree | 2
XVBL1M3 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL1M3 | Environment | standards | EN/IEC 60947-5-1
XVBL1M3 | Environment | protective treatment | TC
XVBL1M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M3 | Offer Sustainability | Mercury free | Yes
XVBL1M3 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M3 | Contractual warranty | Warranty | 18 months
XVBL1M4 | Main | range of product | Harmony XVB Universal
XVBL1M4 | Main | product or component type | Complete beacon
XVBL1M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M4 | Main | signalling type | Flashing
XVBL1M4 | Main | mounting diameter | 70 mm
XVBL1M4 | Main | component name | XVBL
XVBL1M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M4 | Main | light source | Integral LED, red
XVBL1M4 | Main | bulb type | Protected LED
XVBL1M4 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M4 | Complementary | current consumption | < 17 mA AC
XVBL1M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1M4 | Complementary | flashing frequency | 1 Hz
XVBL1M4 | Complementary | CAD overall width | 70 mm
XVBL1M4 | Complementary | CAD overall height | 139 mm
XVBL1M4 | Complementary | CAD overall depth | 70 mm
XVBL1M4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1M4 | Complementary | net weight | 0.28 kg
XVBL1M4 | Environment | pollution degree | 2
XVBL1M4 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBL1M4 | Environment | standards | EN/IEC 60947-5-1
XVBL1M4 | Environment | protective treatment | TC
XVBL1M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M4 | Offer Sustainability | Mercury free | Yes
XVBL1M4 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M4 | Contractual warranty | Warranty | 18 months
XVBL1M5 | Main | range of product | Harmony XVB Universal
XVBL1M5 | Main | product or component type | Complete beacon
XVBL1M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M5 | Main | signalling type | Flashing
XVBL1M5 | Main | mounting diameter | 70 mm
XVBL1M5 | Main | component name | XVBL
XVBL1M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M5 | Main | light source | Integral LED, orange
XVBL1M5 | Main | bulb type | Protected LED
XVBL1M5 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M5 | Complementary | current consumption | < 17 mA AC
XVBL1M5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1M5 | Complementary | flashing frequency | 1 Hz
XVBL1M5 | Complementary | CAD overall width | 70 mm
XVBL1M5 | Complementary | CAD overall height | 139 mm
XVBL1M5 | Complementary | CAD overall depth | 70 mm
XVBL1M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1M5 | Complementary | net weight | 0.28 kg
XVBL1M5 | Environment | pollution degree | 2
XVBL1M5 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ UL 508 ¦ CCC
XVBL1M5 | Environment | standards | EN/IEC 60947-5-1
XVBL1M5 | Environment | protective treatment | TC
XVBL1M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M5 | Offer Sustainability | Mercury free | Yes
XVBL1M5 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M5 | Contractual warranty | Warranty | 18 months
XVBL1M6 | Main | range of product | Harmony XVB Universal
XVBL1M6 | Main | product or component type | Complete beacon
XVBL1M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M6 | Main | signalling type | Flashing
XVBL1M6 | Main | mounting diameter | 70 mm
XVBL1M6 | Main | component name | XVBL
XVBL1M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M6 | Main | light source | Integral LED, blue
XVBL1M6 | Main | bulb type | Protected LED
XVBL1M6 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M6 | Complementary | current consumption | < 17 mA AC
XVBL1M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1M6 | Complementary | flashing frequency | 1 Hz
XVBL1M6 | Complementary | CAD overall width | 70 mm
XVBL1M6 | Complementary | CAD overall height | 139 mm
XVBL1M6 | Complementary | CAD overall depth | 70 mm
XVBL1M6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL1M6 | Complementary | net weight | 0.28 kg
XVBL1M6 | Environment | pollution degree | 2
XVBL1M6 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL1M6 | Environment | standards | EN/IEC 60947-5-1
XVBL1M6 | Environment | protective treatment | TC
XVBL1M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M6 | Offer Sustainability | Mercury free | Yes
XVBL1M6 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M6 | Contractual warranty | Warranty | 18 months
XVBL1M7 | Main | range of product | Harmony XVB Universal
XVBL1M7 | Main | product or component type | Complete beacon
XVBL1M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M7 | Main | signalling type | Flashing
XVBL1M7 | Main | mounting diameter | 70 mm
XVBL1M7 | Main | component name | XVBL
XVBL1M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M7 | Main | light source | Integral LED, clear
XVBL1M7 | Main | bulb type | Protected LED
XVBL1M7 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M7 | Complementary | current consumption | < 17 mA AC
XVBL1M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL1M7 | Complementary | flashing frequency | 1 Hz
XVBL1M7 | Complementary | CAD overall width | 70 mm
XVBL1M7 | Complementary | CAD overall height | 139 mm
XVBL1M7 | Complementary | CAD overall depth | 70 mm
XVBL1M7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1M7 | Complementary | net weight | 0.28 kg
XVBL1M7 | Environment | pollution degree | 2
XVBL1M7 | Environment | product certifications | CCC ¦ GOST ¦ UL 508 ¦ CSA C22-2 No 14
XVBL1M7 | Environment | standards | EN/IEC 60947-5-1
XVBL1M7 | Environment | protective treatment | TC
XVBL1M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M7 | Offer Sustainability | Mercury free | Yes
XVBL1M7 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M7 | Contractual warranty | Warranty | 18 months
XVBL1M8 | Main | range of product | Harmony XVB Universal
XVBL1M8 | Main | product or component type | Complete beacon
XVBL1M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL1M8 | Main | signalling type | Flashing
XVBL1M8 | Main | mounting diameter | 70 mm
XVBL1M8 | Main | component name | XVBL
XVBL1M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL1M8 | Main | light source | Integral LED, yellow
XVBL1M8 | Main | bulb type | Protected LED
XVBL1M8 | Main | [Us] rated supply voltage | 230 V AC
XVBL1M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL1M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL1M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL1M8 | Complementary | current consumption | < 17 mA AC
XVBL1M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL1M8 | Complementary | flashing frequency | 1 Hz
XVBL1M8 | Complementary | CAD overall width | 70 mm
XVBL1M8 | Complementary | CAD overall height | 139 mm
XVBL1M8 | Complementary | CAD overall depth | 70 mm
XVBL1M8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL1M8 | Complementary | net weight | 0.28 kg
XVBL1M8 | Environment | pollution degree | 2
XVBL1M8 | Environment | product certifications | UL 508 ¦ GOST ¦ CSA C22-2 No 14 ¦ CCC
XVBL1M8 | Environment | standards | EN/IEC 60947-5-1
XVBL1M8 | Environment | protective treatment | TC
XVBL1M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL1M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL1M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL1M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL1M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL1M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL1M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL1M8 | Offer Sustainability | Mercury free | Yes
XVBL1M8 | Offer Sustainability | RoHS exemption information | Yes
XVBL1M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL1M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL1M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL1M8 | Contractual warranty | Warranty | 18 months
XVBL6B3 | Main | range of product | Harmony XVB Universal
XVBL6B3 | Main | product or component type | Complete beacon
XVBL6B3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B3 | Main | signalling type | Flashing
XVBL6B3 | Main | mounting diameter | 70 mm
XVBL6B3 | Main | component name | XVBL
XVBL6B3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B3 | Main | light source | Integral flash discharge tube, green
XVBL6B3 | Main | bulb type | Flash discharge tube
XVBL6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B3 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6B3 | Complementary | flash energy | 5 J
XVBL6B3 | Complementary | flashing frequency | 1 Hz
XVBL6B3 | Complementary | CAD overall width | 70 mm
XVBL6B3 | Complementary | CAD overall height | 232 mm
XVBL6B3 | Complementary | CAD overall depth | 70 mm
XVBL6B3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6B3 | Complementary | net weight | 0.44 kg
XVBL6B3 | Environment | product certifications | UL 508 ¦ CSA C22-2 No 14 ¦ GOST ¦ CCC
XVBL6B3 | Environment | standards | EN/IEC 60947-5-1
XVBL6B3 | Environment | protective treatment | TC
XVBL6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B3 | Offer Sustainability | Mercury free | Yes
XVBL6B3 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B3 | Contractual warranty | Warranty | 18 months
XVBL6B4 | Main | range of product | Harmony XVB Universal
XVBL6B4 | Main | product or component type | Complete beacon
XVBL6B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B4 | Main | signalling type | Flashing
XVBL6B4 | Main | mounting diameter | 70 mm
XVBL6B4 | Main | component name | XVBL
XVBL6B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B4 | Main | light source | Integral flash discharge tube, red
XVBL6B4 | Main | bulb type | Flash discharge tube
XVBL6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B4 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6B4 | Complementary | flash energy | 5 J
XVBL6B4 | Complementary | flashing frequency | 1 Hz
XVBL6B4 | Complementary | CAD overall width | 70 mm
XVBL6B4 | Complementary | CAD overall height | 232 mm
XVBL6B4 | Complementary | CAD overall depth | 70 mm
XVBL6B4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL6B4 | Complementary | net weight | 0.44 kg
XVBL6B4 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL6B4 | Environment | standards | EN/IEC 60947-5-1
XVBL6B4 | Environment | protective treatment | TC
XVBL6B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B4 | Offer Sustainability | Mercury free | Yes
XVBL6B4 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B4 | Contractual warranty | Warranty | 18 months
XVBL6B5 | Main | range of product | Harmony XVB Universal
XVBL6B5 | Main | product or component type | Complete beacon
XVBL6B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B5 | Main | signalling type | Flashing
XVBL6B5 | Main | mounting diameter | 70 mm
XVBL6B5 | Main | component name | XVBL
XVBL6B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B5 | Main | light source | Integral flash discharge tube, orange
XVBL6B5 | Main | bulb type | Flash discharge tube
XVBL6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B5 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6B5 | Complementary | flash energy | 5 J
XVBL6B5 | Complementary | flashing frequency | 1 Hz
XVBL6B5 | Complementary | CAD overall width | 70 mm
XVBL6B5 | Complementary | CAD overall height | 232 mm
XVBL6B5 | Complementary | CAD overall depth | 70 mm
XVBL6B5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6B5 | Complementary | net weight | 0.44 kg
XVBL6B5 | Environment | product certifications | UL 508 ¦ CSA C22-2 No 14 ¦ CCC ¦ GOST
XVBL6B5 | Environment | standards | EN/IEC 60947-5-1
XVBL6B5 | Environment | protective treatment | TC
XVBL6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B5 | Offer Sustainability | Mercury free | Yes
XVBL6B5 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B5 | Contractual warranty | Warranty | 18 months
XVBL6B6 | Main | range of product | Harmony XVB Universal
XVBL6B6 | Main | product or component type | Complete beacon
XVBL6B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B6 | Main | signalling type | Flashing
XVBL6B6 | Main | mounting diameter | 70 mm
XVBL6B6 | Main | component name | XVBL
XVBL6B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B6 | Main | light source | Integral flash discharge tube, blue
XVBL6B6 | Main | bulb type | Flash discharge tube
XVBL6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B6 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6B6 | Complementary | flash energy | 5 J
XVBL6B6 | Complementary | flashing frequency | 1 Hz
XVBL6B6 | Complementary | CAD overall width | 70 mm
XVBL6B6 | Complementary | CAD overall height | 232 mm
XVBL6B6 | Complementary | CAD overall depth | 70 mm
XVBL6B6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6B6 | Complementary | net weight | 0.44 kg
XVBL6B6 | Environment | product certifications | UL 508 ¦ GOST ¦ CSA C22-2 No 14 ¦ CCC
XVBL6B6 | Environment | standards | EN/IEC 60947-5-1
XVBL6B6 | Environment | protective treatment | TC
XVBL6B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B6 | Offer Sustainability | Mercury free | Yes
XVBL6B6 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B6 | Contractual warranty | Warranty | 18 months
XVBL6B7 | Main | range of product | Harmony XVB Universal
XVBL6B7 | Main | product or component type | Complete beacon
XVBL6B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B7 | Main | signalling type | Flashing
XVBL6B7 | Main | mounting diameter | 70 mm
XVBL6B7 | Main | component name | XVBL
XVBL6B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B7 | Main | light source | Integral flash discharge tube, clear
XVBL6B7 | Main | bulb type | Flash discharge tube
XVBL6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B7 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6B7 | Complementary | flash energy | 5 J
XVBL6B7 | Complementary | flashing frequency | 1 Hz
XVBL6B7 | Complementary | illuminating intensity | 13 cd
XVBL6B7 | Complementary | CAD overall width | 70 mm
XVBL6B7 | Complementary | CAD overall height | 232 mm
XVBL6B7 | Complementary | CAD overall depth | 70 mm
XVBL6B7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6B7 | Complementary | net weight | 0.44 kg
XVBL6B7 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBL6B7 | Environment | standards | EN/IEC 60947-5-1
XVBL6B7 | Environment | protective treatment | TC
XVBL6B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B7 | Offer Sustainability | Mercury free | Yes
XVBL6B7 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B7 | Contractual warranty | Warranty | 18 months
XVBL6B8 | Main | range of product | Harmony XVB Universal
XVBL6B8 | Main | product or component type | Complete beacon
XVBL6B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6B8 | Main | signalling type | Flashing
XVBL6B8 | Main | mounting diameter | 70 mm
XVBL6B8 | Main | component name | XVBL
XVBL6B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6B8 | Main | light source | Integral flash discharge tube, yellow
XVBL6B8 | Main | bulb type | Flash discharge tube
XVBL6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6B8 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBL6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6B8 | Complementary | flash energy | 5 J
XVBL6B8 | Complementary | flashing frequency | 1 Hz
XVBL6B8 | Complementary | CAD overall width | 70 mm
XVBL6B8 | Complementary | CAD overall height | 232 mm
XVBL6B8 | Complementary | CAD overall depth | 70 mm
XVBL6B8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6B8 | Complementary | net weight | 0.44 kg
XVBL6B8 | Environment | product certifications | UL 508 ¦ GOST ¦ CSA C22-2 No 14 ¦ CCC
XVBL6B8 | Environment | standards | EN/IEC 60947-5-1
XVBL6B8 | Environment | protective treatment | TC
XVBL6B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6B8 | Offer Sustainability | Mercury free | Yes
XVBL6B8 | Offer Sustainability | RoHS exemption information | Yes
XVBL6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6B8 | Contractual warranty | Warranty | 18 months
XVBL6G3 | Main | range of product | Harmony XVB Universal
XVBL6G3 | Main | product or component type | Complete beacon
XVBL6G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G3 | Main | signalling type | Flashing
XVBL6G3 | Main | mounting diameter | 70 mm
XVBL6G3 | Main | component name | XVBL
XVBL6G3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G3 | Main | light source | Integral flash discharge tube, green
XVBL6G3 | Main | bulb type | Flash discharge tube
XVBL6G3 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G3 | Complementary | current consumption | < 140 mA AC
XVBL6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6G3 | Complementary | flash energy | 5 J
XVBL6G3 | Complementary | flashing frequency | 1 Hz
XVBL6G3 | Complementary | CAD overall width | 70 mm
XVBL6G3 | Complementary | CAD overall height | 232 mm
XVBL6G3 | Complementary | CAD overall depth | 70 mm
XVBL6G3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6G3 | Complementary | net weight | 0.425 kg
XVBL6G3 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBL6G3 | Environment | standards | EN/IEC 60947-5-1
XVBL6G3 | Environment | protective treatment | TC
XVBL6G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G3 | Offer Sustainability | Mercury free | Yes
XVBL6G3 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G3 | Contractual warranty | Warranty | 18 months
XVBL6G4 | Main | range of product | Harmony XVB Universal
XVBL6G4 | Main | product or component type | Complete beacon
XVBL6G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G4 | Main | signalling type | Flashing
XVBL6G4 | Main | mounting diameter | 70 mm
XVBL6G4 | Main | component name | XVBL
XVBL6G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G4 | Main | light source | Integral flash discharge tube, red
XVBL6G4 | Main | bulb type | Flash discharge tube
XVBL6G4 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G4 | Complementary | current consumption | < 140 mA AC
XVBL6G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6G4 | Complementary | flash energy | 5 J
XVBL6G4 | Complementary | flashing frequency | 1 Hz
XVBL6G4 | Complementary | CAD overall width | 70 mm
XVBL6G4 | Complementary | CAD overall height | 232 mm
XVBL6G4 | Complementary | CAD overall depth | 70 mm
XVBL6G4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6G4 | Complementary | net weight | 0.425 kg
XVBL6G4 | Environment | product certifications | GOST ¦ UL 508 ¦ CCC ¦ CSA C22-2 No 14
XVBL6G4 | Environment | standards | EN/IEC 60947-5-1
XVBL6G4 | Environment | protective treatment | TC
XVBL6G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G4 | Offer Sustainability | Mercury free | Yes
XVBL6G4 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G4 | Contractual warranty | Warranty | 18 months
XVBL6G5 | Main | range of product | Harmony XVB Universal
XVBL6G5 | Main | product or component type | Complete beacon
XVBL6G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G5 | Main | signalling type | Flashing
XVBL6G5 | Main | mounting diameter | 70 mm
XVBL6G5 | Main | component name | XVBL
XVBL6G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G5 | Main | light source | Integral flash discharge tube, orange
XVBL6G5 | Main | bulb type | Flash discharge tube
XVBL6G5 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G5 | Complementary | current consumption | < 140 mA AC
XVBL6G5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6G5 | Complementary | flash energy | 5 J
XVBL6G5 | Complementary | flashing frequency | 1 Hz
XVBL6G5 | Complementary | CAD overall width | 70 mm
XVBL6G5 | Complementary | CAD overall height | 232 mm
XVBL6G5 | Complementary | CAD overall depth | 70 mm
XVBL6G5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL6G5 | Complementary | net weight | 0.425 kg
XVBL6G5 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ GOST ¦ UL 508
XVBL6G5 | Environment | standards | EN/IEC 60947-5-1
XVBL6G5 | Environment | protective treatment | TC
XVBL6G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G5 | Offer Sustainability | Mercury free | Yes
XVBL6G5 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G5 | Contractual warranty | Warranty | 18 months
XVBL6G6 | Main | range of product | Harmony XVB Universal
XVBL6G6 | Main | product or component type | Complete beacon
XVBL6G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G6 | Main | signalling type | Flashing
XVBL6G6 | Main | mounting diameter | 70 mm
XVBL6G6 | Main | component name | XVBL
XVBL6G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G6 | Main | light source | Integral flash discharge tube, blue
XVBL6G6 | Main | bulb type | Flash discharge tube
XVBL6G6 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G6 | Complementary | current consumption | < 140 mA AC
XVBL6G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6G6 | Complementary | flash energy | 5 J
XVBL6G6 | Complementary | flashing frequency | 1 Hz
XVBL6G6 | Complementary | CAD overall width | 70 mm
XVBL6G6 | Complementary | CAD overall height | 232 mm
XVBL6G6 | Complementary | CAD overall depth | 70 mm
XVBL6G6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL6G6 | Complementary | net weight | 0.425 kg
XVBL6G6 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ CCC ¦ GOST
XVBL6G6 | Environment | standards | EN/IEC 60947-5-1
XVBL6G6 | Environment | protective treatment | TC
XVBL6G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G6 | Offer Sustainability | Mercury free | Yes
XVBL6G6 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G6 | Contractual warranty | Warranty | 18 months
XVBL6G7 | Main | range of product | Harmony XVB Universal
XVBL6G7 | Main | product or component type | Complete beacon
XVBL6G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G7 | Main | signalling type | Flashing
XVBL6G7 | Main | mounting diameter | 70 mm
XVBL6G7 | Main | component name | XVBL
XVBL6G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G7 | Main | light source | Integral flash discharge tube, clear
XVBL6G7 | Main | bulb type | Flash discharge tube
XVBL6G7 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G7 | Complementary | current consumption | < 140 mA AC
XVBL6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6G7 | Complementary | flash energy | 5 J
XVBL6G7 | Complementary | flashing frequency | 1 Hz
XVBL6G7 | Complementary | illuminating intensity | 13 cd
XVBL6G7 | Complementary | CAD overall width | 70 mm
XVBL6G7 | Complementary | CAD overall height | 232 mm
XVBL6G7 | Complementary | CAD overall depth | 70 mm
XVBL6G7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6G7 | Complementary | net weight | 0.425 kg
XVBL6G7 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBL6G7 | Environment | standards | EN/IEC 60947-5-1
XVBL6G7 | Environment | protective treatment | TC
XVBL6G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G7 | Offer Sustainability | Mercury free | Yes
XVBL6G7 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G7 | Contractual warranty | Warranty | 18 months
XVBL6G8 | Main | range of product | Harmony XVB Universal
XVBL6G8 | Main | product or component type | Complete beacon
XVBL6G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6G8 | Main | signalling type | Flashing
XVBL6G8 | Main | mounting diameter | 70 mm
XVBL6G8 | Main | component name | XVBL
XVBL6G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6G8 | Main | light source | Integral flash discharge tube, yellow
XVBL6G8 | Main | bulb type | Flash discharge tube
XVBL6G8 | Main | [Us] rated supply voltage | 120 V AC
XVBL6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6G8 | Complementary | current consumption | < 140 mA AC
XVBL6G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6G8 | Complementary | flash energy | 5 J
XVBL6G8 | Complementary | flashing frequency | 1 Hz
XVBL6G8 | Complementary | CAD overall width | 70 mm
XVBL6G8 | Complementary | CAD overall height | 232 mm
XVBL6G8 | Complementary | CAD overall depth | 70 mm
XVBL6G8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL6G8 | Complementary | net weight | 0.425 kg
XVBL6G8 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ CCC ¦ GOST
XVBL6G8 | Environment | standards | EN/IEC 60947-5-1
XVBL6G8 | Environment | protective treatment | TC
XVBL6G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6G8 | Offer Sustainability | Mercury free | Yes
XVBL6G8 | Offer Sustainability | RoHS exemption information | Yes
XVBL6G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6G8 | Contractual warranty | Warranty | 18 months
XVBL6M3 | Main | range of product | Harmony XVB Universal
XVBL6M3 | Main | product or component type | Complete beacon
XVBL6M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M3 | Main | signalling type | Flashing
XVBL6M3 | Main | mounting diameter | 70 mm
XVBL6M3 | Main | component name | XVBL
XVBL6M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M3 | Main | light source | Integral flash discharge tube, green
XVBL6M3 | Main | bulb type | Flash discharge tube
XVBL6M3 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M3 | Complementary | current consumption | < 105 mA AC
XVBL6M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6M3 | Complementary | flash energy | 5 J
XVBL6M3 | Complementary | flashing frequency | 1 Hz
XVBL6M3 | Complementary | CAD overall width | 70 mm
XVBL6M3 | Complementary | CAD overall height | 232 mm
XVBL6M3 | Complementary | CAD overall depth | 70 mm
XVBL6M3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6M3 | Complementary | net weight | 0.435 kg
XVBL6M3 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ GOST ¦ UL 508
XVBL6M3 | Environment | standards | EN/IEC 60947-5-1
XVBL6M3 | Environment | protective treatment | TC
XVBL6M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M3 | Offer Sustainability | Mercury free | Yes
XVBL6M3 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M3 | Contractual warranty | Warranty | 18 months
XVBL6M4 | Main | range of product | Harmony XVB Universal
XVBL6M4 | Main | product or component type | Complete beacon
XVBL6M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M4 | Main | signalling type | Flashing
XVBL6M4 | Main | mounting diameter | 70 mm
XVBL6M4 | Main | component name | XVBL
XVBL6M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M4 | Main | light source | Integral flash discharge tube, red
XVBL6M4 | Main | bulb type | Flash discharge tube
XVBL6M4 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M4 | Complementary | current consumption | < 105 mA AC
XVBL6M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBL6M4 | Complementary | flash energy | 5 J
XVBL6M4 | Complementary | flashing frequency | 1 Hz
XVBL6M4 | Complementary | CAD overall width | 70 mm
XVBL6M4 | Complementary | CAD overall height | 232 mm
XVBL6M4 | Complementary | CAD overall depth | 70 mm
XVBL6M4 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL6M4 | Complementary | net weight | 0.435 kg
XVBL6M4 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBL6M4 | Environment | standards | EN/IEC 60947-5-1
XVBL6M4 | Environment | protective treatment | TC
XVBL6M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M4 | Offer Sustainability | Mercury free | Yes
XVBL6M4 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M4 | Contractual warranty | Warranty | 18 months
XVBL6M5 | Main | range of product | Harmony XVB Universal
XVBL6M5 | Main | product or component type | Complete beacon
XVBL6M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M5 | Main | signalling type | Flashing
XVBL6M5 | Main | mounting diameter | 70 mm
XVBL6M5 | Main | component name | XVBL
XVBL6M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M5 | Main | light source | Integral flash discharge tube, orange
XVBL6M5 | Main | bulb type | Flash discharge tube
XVBL6M5 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M5 | Complementary | current consumption | < 105 mA AC
XVBL6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6M5 | Complementary | flash energy | 5 J
XVBL6M5 | Complementary | flashing frequency | 1 Hz
XVBL6M5 | Complementary | CAD overall width | 70 mm
XVBL6M5 | Complementary | CAD overall height | 232 mm
XVBL6M5 | Complementary | CAD overall depth | 70 mm
XVBL6M5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6M5 | Complementary | net weight | 0.435 kg
XVBL6M5 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBL6M5 | Environment | standards | EN/IEC 60947-5-1
XVBL6M5 | Environment | protective treatment | TC
XVBL6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M5 | Offer Sustainability | Mercury free | Yes
XVBL6M5 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M5 | Contractual warranty | Warranty | 18 months
XVBL6M6 | Main | range of product | Harmony XVB Universal
XVBL6M6 | Main | product or component type | Complete beacon
XVBL6M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M6 | Main | signalling type | Flashing
XVBL6M6 | Main | mounting diameter | 70 mm
XVBL6M6 | Main | component name | XVBL
XVBL6M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M6 | Main | light source | Integral flash discharge tube, blue
XVBL6M6 | Main | bulb type | Flash discharge tube
XVBL6M6 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M6 | Complementary | current consumption | < 105 mA AC
XVBL6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6M6 | Complementary | flash energy | 5 J
XVBL6M6 | Complementary | flashing frequency | 1 Hz
XVBL6M6 | Complementary | CAD overall width | 70 mm
XVBL6M6 | Complementary | CAD overall height | 232 mm
XVBL6M6 | Complementary | CAD overall depth | 70 mm
XVBL6M6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6M6 | Complementary | net weight | 0.435 kg
XVBL6M6 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBL6M6 | Environment | standards | EN/IEC 60947-5-1
XVBL6M6 | Environment | protective treatment | TC
XVBL6M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M6 | Offer Sustainability | Mercury free | Yes
XVBL6M6 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M6 | Contractual warranty | Warranty | 18 months
XVBL6M7 | Main | range of product | Harmony XVB Universal
XVBL6M7 | Main | product or component type | Complete beacon
XVBL6M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M7 | Main | signalling type | Flashing
XVBL6M7 | Main | mounting diameter | 70 mm
XVBL6M7 | Main | component name | XVBL
XVBL6M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M7 | Main | light source | Integral flash discharge tube, clear
XVBL6M7 | Main | bulb type | Flash discharge tube
XVBL6M7 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M7 | Complementary | current consumption | < 105 mA AC
XVBL6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6M7 | Complementary | flash energy | 5 J
XVBL6M7 | Complementary | flashing frequency | 1 Hz
XVBL6M7 | Complementary | illuminating intensity | 13 cd
XVBL6M7 | Complementary | CAD overall width | 70 mm
XVBL6M7 | Complementary | CAD overall height | 232 mm
XVBL6M7 | Complementary | CAD overall depth | 70 mm
XVBL6M7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6M7 | Complementary | net weight | 0.435 kg
XVBL6M7 | Environment | product certifications | GOST ¦ UL 508 ¦ CSA C22-2 No 14 ¦ CCC
XVBL6M7 | Environment | standards | EN/IEC 60947-5-1
XVBL6M7 | Environment | protective treatment | TC
XVBL6M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M7 | Offer Sustainability | Mercury free | Yes
XVBL6M7 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M7 | Contractual warranty | Warranty | 18 months
XVBL6M8 | Main | range of product | Harmony XVB Universal
XVBL6M8 | Main | product or component type | Complete beacon
XVBL6M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL6M8 | Main | signalling type | Flashing
XVBL6M8 | Main | mounting diameter | 70 mm
XVBL6M8 | Main | component name | XVBL
XVBL6M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL6M8 | Main | light source | Integral flash discharge tube, yellow
XVBL6M8 | Main | bulb type | Flash discharge tube
XVBL6M8 | Main | [Us] rated supply voltage | 230 V AC
XVBL6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL6M8 | Complementary | current consumption | < 105 mA AC
XVBL6M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL6M8 | Complementary | flash energy | 5 J
XVBL6M8 | Complementary | flashing frequency | 1 Hz
XVBL6M8 | Complementary | CAD overall width | 70 mm
XVBL6M8 | Complementary | CAD overall height | 232 mm
XVBL6M8 | Complementary | CAD overall depth | 70 mm
XVBL6M8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL6M8 | Complementary | net weight | 0.435 kg
XVBL6M8 | Environment | product certifications | UL 508 ¦ GOST ¦ CSA C22-2 No 14 ¦ CCC
XVBL6M8 | Environment | standards | EN/IEC 60947-5-1
XVBL6M8 | Environment | protective treatment | TC
XVBL6M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL6M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL6M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL6M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL6M8 | Offer Sustainability | Mercury free | Yes
XVBL6M8 | Offer Sustainability | RoHS exemption information | Yes
XVBL6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL6M8 | Contractual warranty | Warranty | 18 months
XVBL8B4 | Main | range of product | Harmony XVB Universal
XVBL8B4 | Main | product or component type | Complete beacon
XVBL8B4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8B4 | Main | signalling type | Flashing
XVBL8B4 | Main | mounting diameter | 70 mm
XVBL8B4 | Main | component name | XVBL
XVBL8B4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8B4 | Main | light source | Integral flash discharge tube, red
XVBL8B4 | Main | bulb type | Flash discharge tube
XVBL8B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL8B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8B4 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBL8B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8B4 | Complementary | flash energy | 10 J
XVBL8B4 | Complementary | flashing frequency | 1 Hz
XVBL8B4 | Complementary | CAD overall width | 70 mm
XVBL8B4 | Complementary | CAD overall height | 232 mm
XVBL8B4 | Complementary | CAD overall depth | 70 mm
XVBL8B4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8B4 | Complementary | net weight | 0.45 kg
XVBL8B4 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBL8B4 | Environment | standards | EN/IEC 60947-5-1
XVBL8B4 | Environment | protective treatment | TC
XVBL8B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8B4 | Offer Sustainability | Mercury free | Yes
XVBL8B4 | Offer Sustainability | RoHS exemption information | Yes
XVBL8B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8B4 | Contractual warranty | Warranty | 18 months
XVBL8B5 | Main | range of product | Harmony XVB Universal
XVBL8B5 | Main | product or component type | Complete beacon
XVBL8B5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8B5 | Main | signalling type | Flashing
XVBL8B5 | Main | mounting diameter | 70 mm
XVBL8B5 | Main | component name | XVBL
XVBL8B5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8B5 | Main | light source | Integral flash discharge tube, orange
XVBL8B5 | Main | bulb type | Flash discharge tube
XVBL8B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL8B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8B5 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBL8B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8B5 | Complementary | flash energy | 10 J
XVBL8B5 | Complementary | flashing frequency | 1 Hz
XVBL8B5 | Complementary | CAD overall width | 70 mm
XVBL8B5 | Complementary | CAD overall height | 232 mm
XVBL8B5 | Complementary | CAD overall depth | 70 mm
XVBL8B5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8B5 | Complementary | net weight | 0.45 kg
XVBL8B5 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBL8B5 | Environment | standards | EN/IEC 60947-5-1
XVBL8B5 | Environment | protective treatment | TC
XVBL8B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8B5 | Offer Sustainability | Mercury free | Yes
XVBL8B5 | Offer Sustainability | RoHS exemption information | Yes
XVBL8B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8B5 | Contractual warranty | Warranty | 18 months
XVBL8B6 | Main | range of product | Harmony XVB Universal
XVBL8B6 | Main | product or component type | Complete beacon
XVBL8B6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8B6 | Main | signalling type | Flashing
XVBL8B6 | Main | mounting diameter | 70 mm
XVBL8B6 | Main | component name | XVBL
XVBL8B6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8B6 | Main | light source | Integral flash discharge tube, blue
XVBL8B6 | Main | bulb type | Flash discharge tube
XVBL8B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL8B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8B6 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBL8B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8B6 | Complementary | flash energy | 10 J
XVBL8B6 | Complementary | flashing frequency | 1 Hz
XVBL8B6 | Complementary | CAD overall width | 70 mm
XVBL8B6 | Complementary | CAD overall height | 232 mm
XVBL8B6 | Complementary | CAD overall depth | 70 mm
XVBL8B6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8B6 | Complementary | net weight | 0.45 kg
XVBL8B6 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ CCC ¦ GOST
XVBL8B6 | Environment | standards | EN/IEC 60947-5-1
XVBL8B6 | Environment | protective treatment | TC
XVBL8B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8B6 | Offer Sustainability | Mercury free | Yes
XVBL8B6 | Offer Sustainability | RoHS exemption information | Yes
XVBL8B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8B6 | Contractual warranty | Warranty | 18 months
XVBL8B7 | Main | range of product | Harmony XVB Universal
XVBL8B7 | Main | product or component type | Complete beacon
XVBL8B7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8B7 | Main | signalling type | Flashing
XVBL8B7 | Main | mounting diameter | 70 mm
XVBL8B7 | Main | component name | XVBL
XVBL8B7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8B7 | Main | light source | Integral flash discharge tube, clear
XVBL8B7 | Main | bulb type | Flash discharge tube
XVBL8B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL8B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8B7 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBL8B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8B7 | Complementary | flash energy | 10 J
XVBL8B7 | Complementary | flashing frequency | 1 Hz
XVBL8B7 | Complementary | illuminating intensity | 26 cd
XVBL8B7 | Complementary | CAD overall width | 70 mm
XVBL8B7 | Complementary | CAD overall height | 232 mm
XVBL8B7 | Complementary | CAD overall depth | 70 mm
XVBL8B7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8B7 | Complementary | net weight | 0.45 kg
XVBL8B7 | Environment | product certifications | GOST ¦ CCC ¦ UL 508 ¦ CSA C22-2 No 14
XVBL8B7 | Environment | standards | EN/IEC 60947-5-1
XVBL8B7 | Environment | protective treatment | TC
XVBL8B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8B7 | Offer Sustainability | Mercury free | Yes
XVBL8B7 | Offer Sustainability | RoHS exemption information | Yes
XVBL8B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8B7 | Contractual warranty | Warranty | 18 months
XVBL8B8 | Main | range of product | Harmony XVB Universal
XVBL8B8 | Main | product or component type | Complete beacon
XVBL8B8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8B8 | Main | signalling type | Flashing
XVBL8B8 | Main | mounting diameter | 70 mm
XVBL8B8 | Main | component name | XVBL
XVBL8B8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8B8 | Main | light source | Integral flash discharge tube, yellow
XVBL8B8 | Main | bulb type | Flash discharge tube
XVBL8B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBL8B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8B8 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBL8B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8B8 | Complementary | flash energy | 10 J
XVBL8B8 | Complementary | flashing frequency | 1 Hz
XVBL8B8 | Complementary | CAD overall width | 70 mm
XVBL8B8 | Complementary | CAD overall height | 232 mm
XVBL8B8 | Complementary | CAD overall depth | 70 mm
XVBL8B8 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8B8 | Complementary | net weight | 0.45 kg
XVBL8B8 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ UL 508 ¦ CCC
XVBL8B8 | Environment | standards | EN/IEC 60947-5-1
XVBL8B8 | Environment | protective treatment | TC
XVBL8B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8B8 | Offer Sustainability | Mercury free | Yes
XVBL8B8 | Offer Sustainability | RoHS exemption information | Yes
XVBL8B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8B8 | Contractual warranty | Warranty | 18 months
XVBL8G3 | Main | range of product | Harmony XVB Universal
XVBL8G3 | Main | product or component type | Complete beacon
XVBL8G3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G3 | Main | signalling type | Flashing
XVBL8G3 | Main | mounting diameter | 70 mm
XVBL8G3 | Main | component name | XVBL
XVBL8G3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G3 | Main | light source | Integral flash discharge tube, green
XVBL8G3 | Main | bulb type | Flash discharge tube
XVBL8G3 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G3 | Complementary | current consumption | < 290 mA AC
XVBL8G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G3 | Complementary | flash energy | 10 J
XVBL8G3 | Complementary | flashing frequency | 1 Hz
XVBL8G3 | Complementary | CAD overall width | 70 mm
XVBL8G3 | Complementary | CAD overall height | 232 mm
XVBL8G3 | Complementary | CAD overall depth | 70 mm
XVBL8G3 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8G3 | Complementary | net weight | 0.46 kg
XVBL8G3 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBL8G3 | Environment | standards | EN/IEC 60947-5-1
XVBL8G3 | Environment | protective treatment | TC
XVBL8G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G3 | Offer Sustainability | Mercury free | Yes
XVBL8G3 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G3 | Contractual warranty | Warranty | 18 months
XVBL8G4 | Main | range of product | Harmony XVB Universal
XVBL8G4 | Main | product or component type | Complete beacon
XVBL8G4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G4 | Main | signalling type | Flashing
XVBL8G4 | Main | mounting diameter | 70 mm
XVBL8G4 | Main | component name | XVBL
XVBL8G4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G4 | Main | light source | Integral flash discharge tube, red
XVBL8G4 | Main | bulb type | Flash discharge tube
XVBL8G4 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G4 | Complementary | current consumption | < 290 mA AC
XVBL8G4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G4 | Complementary | flash energy | 10 J
XVBL8G4 | Complementary | flashing frequency | 1 Hz
XVBL8G4 | Complementary | CAD overall width | 70 mm
XVBL8G4 | Complementary | CAD overall height | 232 mm
XVBL8G4 | Complementary | CAD overall depth | 70 mm
XVBL8G4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8G4 | Complementary | net weight | 0.46 kg
XVBL8G4 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL8G4 | Environment | standards | EN/IEC 60947-5-1
XVBL8G4 | Environment | protective treatment | TC
XVBL8G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G4 | Offer Sustainability | Mercury free | Yes
XVBL8G4 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G4 | Contractual warranty | Warranty | 18 months
XVBL8G5 | Main | range of product | Harmony XVB Universal
XVBL8G5 | Main | product or component type | Complete beacon
XVBL8G5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G5 | Main | signalling type | Flashing
XVBL8G5 | Main | mounting diameter | 70 mm
XVBL8G5 | Main | component name | XVBL
XVBL8G5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G5 | Main | light source | Integral flash discharge tube, orange
XVBL8G5 | Main | bulb type | Flash discharge tube
XVBL8G5 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G5 | Complementary | current consumption | < 290 mA AC
XVBL8G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G5 | Complementary | flash energy | 10 J
XVBL8G5 | Complementary | flashing frequency | 1 Hz
XVBL8G5 | Complementary | CAD overall width | 70 mm
XVBL8G5 | Complementary | CAD overall height | 232 mm
XVBL8G5 | Complementary | CAD overall depth | 70 mm
XVBL8G5 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8G5 | Complementary | net weight | 0.46 kg
XVBL8G5 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBL8G5 | Environment | standards | EN/IEC 60947-5-1
XVBL8G5 | Environment | protective treatment | TC
XVBL8G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G5 | Offer Sustainability | Mercury free | Yes
XVBL8G5 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G5 | Contractual warranty | Warranty | 18 months
XVBL8G6 | Main | range of product | Harmony XVB Universal
XVBL8G6 | Main | product or component type | Complete beacon
XVBL8G6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G6 | Main | signalling type | Flashing
XVBL8G6 | Main | mounting diameter | 70 mm
XVBL8G6 | Main | component name | XVBL
XVBL8G6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G6 | Main | light source | Integral flash discharge tube, blue
XVBL8G6 | Main | bulb type | Flash discharge tube
XVBL8G6 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G6 | Complementary | current consumption | < 290 mA AC
XVBL8G6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G6 | Complementary | flash energy | 10 J
XVBL8G6 | Complementary | flashing frequency | 1 Hz
XVBL8G6 | Complementary | CAD overall width | 70 mm
XVBL8G6 | Complementary | CAD overall height | 232 mm
XVBL8G6 | Complementary | CAD overall depth | 70 mm
XVBL8G6 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8G6 | Complementary | net weight | 0.46 kg
XVBL8G6 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ UL 508 ¦ GOST
XVBL8G6 | Environment | standards | EN/IEC 60947-5-1
XVBL8G6 | Environment | protective treatment | TC
XVBL8G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G6 | Offer Sustainability | Mercury free | Yes
XVBL8G6 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G6 | Contractual warranty | Warranty | 18 months
XVBL8G7 | Main | range of product | Harmony XVB Universal
XVBL8G7 | Main | product or component type | Complete beacon
XVBL8G7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G7 | Main | signalling type | Flashing
XVBL8G7 | Main | mounting diameter | 70 mm
XVBL8G7 | Main | component name | XVBL
XVBL8G7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G7 | Main | light source | Integral flash discharge tube, clear
XVBL8G7 | Main | bulb type | Flash discharge tube
XVBL8G7 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G7 | Complementary | current consumption | < 290 mA AC
XVBL8G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G7 | Complementary | flash energy | 10 J
XVBL8G7 | Complementary | flashing frequency | 1 Hz
XVBL8G7 | Complementary | illuminating intensity | 26 cd
XVBL8G7 | Complementary | CAD overall width | 70 mm
XVBL8G7 | Complementary | CAD overall height | 232 mm
XVBL8G7 | Complementary | CAD overall depth | 70 mm
XVBL8G7 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8G7 | Complementary | net weight | 0.46 kg
XVBL8G7 | Environment | product certifications | CCC ¦ UL 508 ¦ GOST ¦ CSA C22-2 No 14
XVBL8G7 | Environment | standards | EN/IEC 60947-5-1
XVBL8G7 | Environment | protective treatment | TC
XVBL8G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G7 | Offer Sustainability | Mercury free | Yes
XVBL8G7 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G7 | Contractual warranty | Warranty | 18 months
XVBL8G8 | Main | range of product | Harmony XVB Universal
XVBL8G8 | Main | product or component type | Complete beacon
XVBL8G8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8G8 | Main | signalling type | Flashing
XVBL8G8 | Main | mounting diameter | 70 mm
XVBL8G8 | Main | component name | XVBL
XVBL8G8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8G8 | Main | light source | Integral flash discharge tube, yellow
XVBL8G8 | Main | bulb type | Flash discharge tube
XVBL8G8 | Main | [Us] rated supply voltage | 120 V AC
XVBL8G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8G8 | Complementary | current consumption | < 290 mA AC
XVBL8G8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8G8 | Complementary | flash energy | 10 J
XVBL8G8 | Complementary | flashing frequency | 1 Hz
XVBL8G8 | Complementary | CAD overall width | 70 mm
XVBL8G8 | Complementary | CAD overall height | 232 mm
XVBL8G8 | Complementary | CAD overall depth | 70 mm
XVBL8G8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8G8 | Complementary | net weight | 0.46 kg
XVBL8G8 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBL8G8 | Environment | standards | EN/IEC 60947-5-1
XVBL8G8 | Environment | protective treatment | TC
XVBL8G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8G8 | Offer Sustainability | Mercury free | Yes
XVBL8G8 | Offer Sustainability | RoHS exemption information | Yes
XVBL8G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8G8 | Contractual warranty | Warranty | 18 months
XVBL8M3 | Main | range of product | Harmony XVB Universal
XVBL8M3 | Main | product or component type | Complete beacon
XVBL8M3 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M3 | Main | signalling type | Flashing
XVBL8M3 | Main | mounting diameter | 70 mm
XVBL8M3 | Main | component name | XVBL
XVBL8M3 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M3 | Main | light source | Integral flash discharge tube, green
XVBL8M3 | Main | bulb type | Flash discharge tube
XVBL8M3 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M3 | Complementary | current consumption | < 280 mA AC
XVBL8M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M3 | Complementary | flash energy | 10 J
XVBL8M3 | Complementary | flashing frequency | 1 Hz
XVBL8M3 | Complementary | CAD overall width | 70 mm
XVBL8M3 | Complementary | CAD overall height | 232 mm
XVBL8M3 | Complementary | CAD overall depth | 70 mm
XVBL8M3 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8M3 | Complementary | net weight | 0.46 kg
XVBL8M3 | Environment | product certifications | GOST ¦ UL 508 ¦ CCC ¦ CSA C22-2 No 14
XVBL8M3 | Environment | standards | EN/IEC 60947-5-1
XVBL8M3 | Environment | protective treatment | TC
XVBL8M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M3 | Offer Sustainability | Mercury free | Yes
XVBL8M3 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M3 | Contractual warranty | Warranty | 18 months
XVBL8M4 | Main | range of product | Harmony XVB Universal
XVBL8M4 | Main | product or component type | Complete beacon
XVBL8M4 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M4 | Main | signalling type | Flashing
XVBL8M4 | Main | mounting diameter | 70 mm
XVBL8M4 | Main | component name | XVBL
XVBL8M4 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M4 | Main | light source | Integral flash discharge tube, red
XVBL8M4 | Main | bulb type | Flash discharge tube
XVBL8M4 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M4 | Complementary | current consumption | < 280 mA AC
XVBL8M4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M4 | Complementary | flash energy | 10 J
XVBL8M4 | Complementary | flashing frequency | 1 Hz
XVBL8M4 | Complementary | CAD overall width | 70 mm
XVBL8M4 | Complementary | CAD overall height | 232 mm
XVBL8M4 | Complementary | CAD overall depth | 70 mm
XVBL8M4 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8M4 | Complementary | net weight | 0.46 kg
XVBL8M4 | Environment | product certifications | GOST ¦ UL 508 ¦ CCC ¦ CSA C22-2 No 14
XVBL8M4 | Environment | standards | EN/IEC 60947-5-1
XVBL8M4 | Environment | protective treatment | TC
XVBL8M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M4 | Offer Sustainability | Mercury free | Yes
XVBL8M4 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M4 | Contractual warranty | Warranty | 18 months
XVBL8M5 | Main | range of product | Harmony XVB Universal
XVBL8M5 | Main | product or component type | Complete beacon
XVBL8M5 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M5 | Main | signalling type | Flashing
XVBL8M5 | Main | mounting diameter | 70 mm
XVBL8M5 | Main | component name | XVBL
XVBL8M5 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M5 | Main | light source | Integral flash discharge tube, orange
XVBL8M5 | Main | bulb type | Flash discharge tube
XVBL8M5 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M5 | Complementary | current consumption | < 280 mA AC
XVBL8M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M5 | Complementary | flash energy | 10 J
XVBL8M5 | Complementary | flashing frequency | 1 Hz
XVBL8M5 | Complementary | CAD overall width | 70 mm
XVBL8M5 | Complementary | CAD overall height | 232 mm
XVBL8M5 | Complementary | CAD overall depth | 70 mm
XVBL8M5 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8M5 | Complementary | net weight | 0.46 kg
XVBL8M5 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ GOST ¦ CCC
XVBL8M5 | Environment | standards | EN/IEC 60947-5-1
XVBL8M5 | Environment | protective treatment | TC
XVBL8M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M5 | Offer Sustainability | Mercury free | Yes
XVBL8M5 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M5 | Contractual warranty | Warranty | 18 months
XVBL8M6 | Main | range of product | Harmony XVB Universal
XVBL8M6 | Main | product or component type | Complete beacon
XVBL8M6 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M6 | Main | signalling type | Flashing
XVBL8M6 | Main | mounting diameter | 70 mm
XVBL8M6 | Main | component name | XVBL
XVBL8M6 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M6 | Main | light source | Integral flash discharge tube, blue
XVBL8M6 | Main | bulb type | Flash discharge tube
XVBL8M6 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M6 | Complementary | current consumption | < 280 mA AC
XVBL8M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M6 | Complementary | flash energy | 10 J
XVBL8M6 | Complementary | flashing frequency | 1 Hz
XVBL8M6 | Complementary | CAD overall width | 70 mm
XVBL8M6 | Complementary | CAD overall height | 232 mm
XVBL8M6 | Complementary | CAD overall depth | 70 mm
XVBL8M6 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8M6 | Complementary | net weight | 0.46 kg
XVBL8M6 | Environment | product certifications | GOST ¦ UL 508 ¦ CSA C22-2 No 14 ¦ CCC
XVBL8M6 | Environment | standards | EN/IEC 60947-5-1
XVBL8M6 | Environment | protective treatment | TC
XVBL8M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M6 | Offer Sustainability | Mercury free | Yes
XVBL8M6 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M6 | Contractual warranty | Warranty | 18 months
XVBL8M7 | Main | range of product | Harmony XVB Universal
XVBL8M7 | Main | product or component type | Complete beacon
XVBL8M7 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M7 | Main | signalling type | Flashing
XVBL8M7 | Main | mounting diameter | 70 mm
XVBL8M7 | Main | component name | XVBL
XVBL8M7 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M7 | Main | light source | Integral flash discharge tube, clear
XVBL8M7 | Main | bulb type | Flash discharge tube
XVBL8M7 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M7 | Complementary | current consumption | < 280 mA AC
XVBL8M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M7 | Complementary | flash energy | 10 J
XVBL8M7 | Complementary | flashing frequency | 1 Hz
XVBL8M7 | Complementary | illuminating intensity | 26 cd
XVBL8M7 | Complementary | CAD overall width | 70 mm
XVBL8M7 | Complementary | CAD overall height | 232 mm
XVBL8M7 | Complementary | CAD overall depth | 70 mm
XVBL8M7 | Complementary | terminals description ISO n°1 | (GND)GROUND ¦ (COM-1)PW
XVBL8M7 | Complementary | net weight | 0.46 kg
XVBL8M7 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBL8M7 | Environment | standards | EN/IEC 60947-5-1
XVBL8M7 | Environment | protective treatment | TC
XVBL8M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M7 | Offer Sustainability | Mercury free | Yes
XVBL8M7 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M7 | Contractual warranty | Warranty | 18 months
XVBL8M8 | Main | range of product | Harmony XVB Universal
XVBL8M8 | Main | product or component type | Complete beacon
XVBL8M8 | Main | beacon or indicator bank unit type | Base unit direct or tube fixing ¦ Illuminated unit
XVBL8M8 | Main | signalling type | Flashing
XVBL8M8 | Main | mounting diameter | 70 mm
XVBL8M8 | Main | component name | XVBL
XVBL8M8 | Main | material | Glass reinforced polyamide: base unit ¦ Polycarbonate: illuminated unit
XVBL8M8 | Main | light source | Integral flash discharge tube, yellow
XVBL8M8 | Main | bulb type | Flash discharge tube
XVBL8M8 | Main | [Us] rated supply voltage | 230 V AC
XVBL8M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBL8M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBL8M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBL8M8 | Complementary | current consumption | < 280 mA AC
XVBL8M8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBL8M8 | Complementary | flash energy | 10 J
XVBL8M8 | Complementary | flashing frequency | 1 Hz
XVBL8M8 | Complementary | CAD overall width | 70 mm
XVBL8M8 | Complementary | CAD overall height | 232 mm
XVBL8M8 | Complementary | CAD overall depth | 70 mm
XVBL8M8 | Complementary | terminals description ISO n°1 | (COM-1)PW ¦ (GND)GROUND
XVBL8M8 | Complementary | net weight | 0.46 kg
XVBL8M8 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBL8M8 | Environment | standards | EN/IEC 60947-5-1
XVBL8M8 | Environment | protective treatment | TC
XVBL8M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBL8M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBL8M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBL8M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBL8M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBL8M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBL8M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBL8M8 | Offer Sustainability | Mercury free | Yes
XVBL8M8 | Offer Sustainability | RoHS exemption information | Yes
XVBL8M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBL8M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBL8M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBL8M8 | Contractual warranty | Warranty | 18 months
XVBC6B3 | Main | range of product | Harmony XVB Universal
XVBC6B3 | Main | product or component type | Indicator bank
XVBC6B3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B3 | Main | signalling type | Flashing
XVBC6B3 | Main | mounting diameter | 70 mm
XVBC6B3 | Main | component name | XVBC
XVBC6B3 | Main | material | Polycarbonate
XVBC6B3 | Main | light source | Integral flash discharge tube, green
XVBC6B3 | Main | bulb type | Flash discharge tube
XVBC6B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B3 | Main | flash energy | 5 J
XVBC6B3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B3 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B3 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6B3 | Complementary | flashing frequency | 1 Hz
XVBC6B3 | Complementary | CAD overall width | 70 mm
XVBC6B3 | Complementary | CAD overall height | 157 mm
XVBC6B3 | Complementary | CAD overall depth | 70 mm
XVBC6B3 | Complementary | net weight | 0.295 kg
XVBC6B3 | Environment | product certifications | UL 508 ¦ CSA C22-2 No 14 ¦ CCC ¦ GOST
XVBC6B3 | Environment | standards | EN/IEC 60947-5-1
XVBC6B3 | Environment | protective treatment | TC
XVBC6B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B3 | Offer Sustainability | Mercury free | Yes
XVBC6B3 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B3 | Contractual warranty | Warranty | 18 months
XVBC6B4 | Main | range of product | Harmony XVB Universal
XVBC6B4 | Main | product or component type | Indicator bank
XVBC6B4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B4 | Main | signalling type | Flashing
XVBC6B4 | Main | mounting diameter | 70 mm
XVBC6B4 | Main | component name | XVBC
XVBC6B4 | Main | material | Polycarbonate
XVBC6B4 | Main | light source | Integral flash discharge tube, red
XVBC6B4 | Main | bulb type | Flash discharge tube
XVBC6B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B4 | Main | flash energy | 5 J
XVBC6B4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B4 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6B4 | Complementary | flashing frequency | 1 Hz
XVBC6B4 | Complementary | CAD overall width | 70 mm
XVBC6B4 | Complementary | CAD overall height | 157 mm
XVBC6B4 | Complementary | CAD overall depth | 70 mm
XVBC6B4 | Complementary | net weight | 0.295 kg
XVBC6B4 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBC6B4 | Environment | standards | EN/IEC 60947-5-1
XVBC6B4 | Environment | protective treatment | TC
XVBC6B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B4 | Offer Sustainability | Mercury free | Yes
XVBC6B4 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B4 | Contractual warranty | Warranty | 18 months
XVBC6B5 | Main | range of product | Harmony XVB Universal
XVBC6B5 | Main | product or component type | Indicator bank
XVBC6B5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B5 | Main | signalling type | Flashing
XVBC6B5 | Main | mounting diameter | 70 mm
XVBC6B5 | Main | component name | XVBC
XVBC6B5 | Main | material | Polycarbonate
XVBC6B5 | Main | light source | Integral flash discharge tube, orange
XVBC6B5 | Main | bulb type | Flash discharge tube
XVBC6B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B5 | Main | flash energy | 5 J
XVBC6B5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B5 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6B5 | Complementary | flashing frequency | 1 Hz
XVBC6B5 | Complementary | CAD overall width | 70 mm
XVBC6B5 | Complementary | CAD overall height | 157 mm
XVBC6B5 | Complementary | CAD overall depth | 70 mm
XVBC6B5 | Complementary | net weight | 0.295 kg
XVBC6B5 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBC6B5 | Environment | standards | EN/IEC 60947-5-1
XVBC6B5 | Environment | protective treatment | TC
XVBC6B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B5 | Offer Sustainability | Mercury free | Yes
XVBC6B5 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B5 | Contractual warranty | Warranty | 18 months
XVBC6B6 | Main | range of product | Harmony XVB Universal
XVBC6B6 | Main | product or component type | Indicator bank
XVBC6B6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B6 | Main | signalling type | Flashing
XVBC6B6 | Main | mounting diameter | 70 mm
XVBC6B6 | Main | component name | XVBC
XVBC6B6 | Main | material | Polycarbonate
XVBC6B6 | Main | light source | Integral flash discharge tube, blue
XVBC6B6 | Main | bulb type | Flash discharge tube
XVBC6B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B6 | Main | flash energy | 5 J
XVBC6B6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B6 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6B6 | Complementary | flashing frequency | 1 Hz
XVBC6B6 | Complementary | CAD overall width | 70 mm
XVBC6B6 | Complementary | CAD overall height | 157 mm
XVBC6B6 | Complementary | CAD overall depth | 70 mm
XVBC6B6 | Complementary | net weight | 0.295 kg
XVBC6B6 | Environment | product certifications | CCC ¦ UL 508 ¦ CSA C22-2 No 14 ¦ GOST
XVBC6B6 | Environment | standards | EN/IEC 60947-5-1
XVBC6B6 | Environment | protective treatment | TC
XVBC6B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B6 | Offer Sustainability | Mercury free | Yes
XVBC6B6 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B6 | Contractual warranty | Warranty | 18 months
XVBC6B7 | Main | range of product | Harmony XVB Universal
XVBC6B7 | Main | product or component type | Indicator bank
XVBC6B7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B7 | Main | signalling type | Flashing
XVBC6B7 | Main | mounting diameter | 70 mm
XVBC6B7 | Main | component name | XVBC
XVBC6B7 | Main | material | Polycarbonate
XVBC6B7 | Main | light source | Integral flash discharge tube, clear
XVBC6B7 | Main | bulb type | Flash discharge tube
XVBC6B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B7 | Main | flash energy | 5 J
XVBC6B7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B7 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6B7 | Complementary | flashing frequency | 1 Hz
XVBC6B7 | Complementary | illuminating intensity | 13 cd
XVBC6B7 | Complementary | CAD overall width | 70 mm
XVBC6B7 | Complementary | CAD overall height | 157 mm
XVBC6B7 | Complementary | CAD overall depth | 70 mm
XVBC6B7 | Complementary | net weight | 0.295 kg
XVBC6B7 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ GOST ¦ CCC
XVBC6B7 | Environment | standards | EN/IEC 60947-5-1
XVBC6B7 | Environment | protective treatment | TC
XVBC6B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B7 | Offer Sustainability | Mercury free | Yes
XVBC6B7 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B7 | Contractual warranty | Warranty | 18 months
XVBC6B8 | Main | range of product | Harmony XVB Universal
XVBC6B8 | Main | product or component type | Indicator bank
XVBC6B8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6B8 | Main | signalling type | Flashing
XVBC6B8 | Main | mounting diameter | 70 mm
XVBC6B8 | Main | component name | XVBC
XVBC6B8 | Main | material | Polycarbonate
XVBC6B8 | Main | light source | Integral flash discharge tube, yellow
XVBC6B8 | Main | bulb type | Flash discharge tube
XVBC6B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC6B8 | Main | flash energy | 5 J
XVBC6B8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6B8 | Complementary | current consumption | < 350 mA DC ¦ < 550 mA AC
XVBC6B8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6B8 | Complementary | flashing frequency | 1 Hz
XVBC6B8 | Complementary | CAD overall width | 70 mm
XVBC6B8 | Complementary | CAD overall height | 157 mm
XVBC6B8 | Complementary | CAD overall depth | 70 mm
XVBC6B8 | Complementary | net weight | 0.295 kg
XVBC6B8 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBC6B8 | Environment | standards | EN/IEC 60947-5-1
XVBC6B8 | Environment | protective treatment | TC
XVBC6B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6B8 | Offer Sustainability | Mercury free | Yes
XVBC6B8 | Offer Sustainability | RoHS exemption information | Yes
XVBC6B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6B8 | Contractual warranty | Warranty | 18 months
XVBC6G3 | Main | range of product | Harmony XVB Universal
XVBC6G3 | Main | product or component type | Indicator bank
XVBC6G3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G3 | Main | signalling type | Flashing
XVBC6G3 | Main | mounting diameter | 70 mm
XVBC6G3 | Main | component name | XVBC
XVBC6G3 | Main | material | Polycarbonate
XVBC6G3 | Main | light source | Integral flash discharge tube, green
XVBC6G3 | Main | bulb type | Flash discharge tube
XVBC6G3 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G3 | Main | flash energy | 5 J
XVBC6G3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G3 | Complementary | current consumption | < 140 mA AC
XVBC6G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6G3 | Complementary | flashing frequency | 1 Hz
XVBC6G3 | Complementary | CAD overall width | 70 mm
XVBC6G3 | Complementary | CAD overall height | 157 mm
XVBC6G3 | Complementary | CAD overall depth | 70 mm
XVBC6G3 | Complementary | net weight | 0.28 kg
XVBC6G3 | Environment | product certifications | CCC ¦ UL 508 ¦ CSA C22-2 No 14 ¦ GOST
XVBC6G3 | Environment | standards | EN/IEC 60947-5-1
XVBC6G3 | Environment | protective treatment | TC
XVBC6G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G3 | Offer Sustainability | Mercury free | Yes
XVBC6G3 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G3 | Contractual warranty | Warranty | 18 months
XVBC6G4 | Main | range of product | Harmony XVB Universal
XVBC6G4 | Main | product or component type | Indicator bank
XVBC6G4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G4 | Main | signalling type | Flashing
XVBC6G4 | Main | mounting diameter | 70 mm
XVBC6G4 | Main | component name | XVBC
XVBC6G4 | Main | material | Polycarbonate
XVBC6G4 | Main | light source | Integral flash discharge tube, red
XVBC6G4 | Main | bulb type | Flash discharge tube
XVBC6G4 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G4 | Main | flash energy | 5 J
XVBC6G4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G4 | Complementary | current consumption | < 140 mA AC
XVBC6G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6G4 | Complementary | flashing frequency | 1 Hz
XVBC6G4 | Complementary | CAD overall width | 70 mm
XVBC6G4 | Complementary | CAD overall height | 157 mm
XVBC6G4 | Complementary | CAD overall depth | 70 mm
XVBC6G4 | Complementary | net weight | 0.28 kg
XVBC6G4 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBC6G4 | Environment | standards | EN/IEC 60947-5-1
XVBC6G4 | Environment | protective treatment | TC
XVBC6G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G4 | Offer Sustainability | Mercury free | Yes
XVBC6G4 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G4 | Contractual warranty | Warranty | 18 months
XVBC6G5 | Main | range of product | Harmony XVB Universal
XVBC6G5 | Main | product or component type | Indicator bank
XVBC6G5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G5 | Main | signalling type | Flashing
XVBC6G5 | Main | mounting diameter | 70 mm
XVBC6G5 | Main | component name | XVBC
XVBC6G5 | Main | material | Polycarbonate
XVBC6G5 | Main | light source | Integral flash discharge tube, orange
XVBC6G5 | Main | bulb type | Flash discharge tube
XVBC6G5 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G5 | Main | flash energy | 5 J
XVBC6G5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G5 | Complementary | current consumption | < 140 mA AC
XVBC6G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6G5 | Complementary | flashing frequency | 1 Hz
XVBC6G5 | Complementary | CAD overall width | 70 mm
XVBC6G5 | Complementary | CAD overall height | 157 mm
XVBC6G5 | Complementary | CAD overall depth | 70 mm
XVBC6G5 | Complementary | net weight | 0.28 kg
XVBC6G5 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ UL 508 ¦ GOST
XVBC6G5 | Environment | standards | EN/IEC 60947-5-1
XVBC6G5 | Environment | protective treatment | TC
XVBC6G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G5 | Offer Sustainability | Mercury free | Yes
XVBC6G5 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G5 | Contractual warranty | Warranty | 18 months
XVBC6G6 | Main | range of product | Harmony XVB Universal
XVBC6G6 | Main | product or component type | Indicator bank
XVBC6G6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G6 | Main | signalling type | Flashing
XVBC6G6 | Main | mounting diameter | 70 mm
XVBC6G6 | Main | component name | XVBC
XVBC6G6 | Main | material | Polycarbonate
XVBC6G6 | Main | light source | Integral flash discharge tube, blue
XVBC6G6 | Main | bulb type | Flash discharge tube
XVBC6G6 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G6 | Main | flash energy | 5 J
XVBC6G6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G6 | Complementary | current consumption | < 140 mA AC
XVBC6G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6G6 | Complementary | flashing frequency | 1 Hz
XVBC6G6 | Complementary | CAD overall width | 70 mm
XVBC6G6 | Complementary | CAD overall height | 157 mm
XVBC6G6 | Complementary | CAD overall depth | 70 mm
XVBC6G6 | Complementary | net weight | 0.28 kg
XVBC6G6 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ UL 508 ¦ GOST
XVBC6G6 | Environment | standards | EN/IEC 60947-5-1
XVBC6G6 | Environment | protective treatment | TC
XVBC6G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G6 | Offer Sustainability | Mercury free | Yes
XVBC6G6 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G6 | Contractual warranty | Warranty | 18 months
XVBC6G7 | Main | range of product | Harmony XVB Universal
XVBC6G7 | Main | product or component type | Indicator bank
XVBC6G7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G7 | Main | signalling type | Flashing
XVBC6G7 | Main | mounting diameter | 70 mm
XVBC6G7 | Main | component name | XVBC
XVBC6G7 | Main | material | Polycarbonate
XVBC6G7 | Main | light source | Integral flash discharge tube, clear
XVBC6G7 | Main | bulb type | Flash discharge tube
XVBC6G7 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G7 | Main | flash energy | 5 J
XVBC6G7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G7 | Complementary | current consumption | < 140 mA AC
XVBC6G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6G7 | Complementary | flashing frequency | 1 Hz
XVBC6G7 | Complementary | illuminating intensity | 13 cd
XVBC6G7 | Complementary | CAD overall width | 70 mm
XVBC6G7 | Complementary | CAD overall height | 157 mm
XVBC6G7 | Complementary | CAD overall depth | 70 mm
XVBC6G7 | Complementary | net weight | 0.28 kg
XVBC6G7 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBC6G7 | Environment | standards | EN/IEC 60947-5-1
XVBC6G7 | Environment | protective treatment | TC
XVBC6G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G7 | Offer Sustainability | Mercury free | Yes
XVBC6G7 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G7 | Contractual warranty | Warranty | 18 months
XVBC6G8 | Main | range of product | Harmony XVB Universal
XVBC6G8 | Main | product or component type | Indicator bank
XVBC6G8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6G8 | Main | signalling type | Flashing
XVBC6G8 | Main | mounting diameter | 70 mm
XVBC6G8 | Main | component name | XVBC
XVBC6G8 | Main | material | Polycarbonate
XVBC6G8 | Main | light source | Integral flash discharge tube, yellow
XVBC6G8 | Main | bulb type | Flash discharge tube
XVBC6G8 | Main | [Us] rated supply voltage | 120 V AC
XVBC6G8 | Main | flash energy | 5 J
XVBC6G8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6G8 | Complementary | current consumption | < 140 mA AC
XVBC6G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6G8 | Complementary | flashing frequency | 1 Hz
XVBC6G8 | Complementary | CAD overall width | 70 mm
XVBC6G8 | Complementary | CAD overall height | 157 mm
XVBC6G8 | Complementary | CAD overall depth | 70 mm
XVBC6G8 | Complementary | net weight | 0.28 kg
XVBC6G8 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ GOST ¦ CCC
XVBC6G8 | Environment | standards | EN/IEC 60947-5-1
XVBC6G8 | Environment | protective treatment | TC
XVBC6G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6G8 | Offer Sustainability | Mercury free | Yes
XVBC6G8 | Offer Sustainability | RoHS exemption information | Yes
XVBC6G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6G8 | Contractual warranty | Warranty | 18 months
XVBC6M3 | Main | range of product | Harmony XVB Universal
XVBC6M3 | Main | product or component type | Indicator bank
XVBC6M3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M3 | Main | signalling type | Flashing
XVBC6M3 | Main | mounting diameter | 70 mm
XVBC6M3 | Main | component name | XVBC
XVBC6M3 | Main | material | Polycarbonate
XVBC6M3 | Main | light source | Integral flash discharge tube, green
XVBC6M3 | Main | bulb type | Flash discharge tube
XVBC6M3 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M3 | Main | flash energy | 5 J
XVBC6M3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M3 | Complementary | current consumption | < 105 mA AC
XVBC6M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6M3 | Complementary | flashing frequency | 1 Hz
XVBC6M3 | Complementary | CAD overall width | 70 mm
XVBC6M3 | Complementary | CAD overall height | 157 mm
XVBC6M3 | Complementary | CAD overall depth | 70 mm
XVBC6M3 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ UL 508 ¦ CCC
XVBC6M3 | Environment | standards | EN/IEC 60947-5-1
XVBC6M3 | Environment | protective treatment | TC
XVBC6M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M3 | Offer Sustainability | Mercury free | Yes
XVBC6M3 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M3 | Contractual warranty | Warranty | 18 months
XVBC6M4 | Main | range of product | Harmony XVB Universal
XVBC6M4 | Main | product or component type | Indicator bank
XVBC6M4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M4 | Main | signalling type | Flashing
XVBC6M4 | Main | mounting diameter | 70 mm
XVBC6M4 | Main | component name | XVBC
XVBC6M4 | Main | material | Polycarbonate
XVBC6M4 | Main | light source | Integral flash discharge tube, red
XVBC6M4 | Main | bulb type | Flash discharge tube
XVBC6M4 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M4 | Main | flash energy | 5 J
XVBC6M4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M4 | Complementary | current consumption | < 105 mA AC
XVBC6M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6M4 | Complementary | flashing frequency | 1 Hz
XVBC6M4 | Complementary | CAD overall width | 70 mm
XVBC6M4 | Complementary | CAD overall height | 157 mm
XVBC6M4 | Complementary | CAD overall depth | 70 mm
XVBC6M4 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBC6M4 | Environment | standards | EN/IEC 60947-5-1
XVBC6M4 | Environment | protective treatment | TC
XVBC6M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M4 | Offer Sustainability | Mercury free | Yes
XVBC6M4 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M4 | Contractual warranty | Warranty | 18 months
XVBC6M5 | Main | range of product | Harmony XVB Universal
XVBC6M5 | Main | product or component type | Indicator bank
XVBC6M5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M5 | Main | signalling type | Flashing
XVBC6M5 | Main | mounting diameter | 70 mm
XVBC6M5 | Main | component name | XVBC
XVBC6M5 | Main | material | Polycarbonate
XVBC6M5 | Main | light source | Integral flash discharge tube, orange
XVBC6M5 | Main | bulb type | Flash discharge tube
XVBC6M5 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M5 | Main | flash energy | 5 J
XVBC6M5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M5 | Complementary | current consumption | < 105 mA AC
XVBC6M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6M5 | Complementary | flashing frequency | 1 Hz
XVBC6M5 | Complementary | CAD overall width | 70 mm
XVBC6M5 | Complementary | CAD overall height | 157 mm
XVBC6M5 | Complementary | CAD overall depth | 70 mm
XVBC6M5 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBC6M5 | Environment | standards | EN/IEC 60947-5-1
XVBC6M5 | Environment | protective treatment | TC
XVBC6M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M5 | Offer Sustainability | Mercury free | Yes
XVBC6M5 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M5 | Contractual warranty | Warranty | 18 months
XVBC6M6 | Main | range of product | Harmony XVB Universal
XVBC6M6 | Main | product or component type | Indicator bank
XVBC6M6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M6 | Main | signalling type | Flashing
XVBC6M6 | Main | mounting diameter | 70 mm
XVBC6M6 | Main | component name | XVBC
XVBC6M6 | Main | material | Polycarbonate
XVBC6M6 | Main | light source | Integral flash discharge tube, blue
XVBC6M6 | Main | bulb type | Flash discharge tube
XVBC6M6 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M6 | Main | flash energy | 5 J
XVBC6M6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M6 | Complementary | current consumption | < 105 mA AC
XVBC6M6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6M6 | Complementary | flashing frequency | 1 Hz
XVBC6M6 | Complementary | CAD overall width | 70 mm
XVBC6M6 | Complementary | CAD overall height | 157 mm
XVBC6M6 | Complementary | CAD overall depth | 70 mm
XVBC6M6 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBC6M6 | Environment | standards | EN/IEC 60947-5-1
XVBC6M6 | Environment | protective treatment | TC
XVBC6M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M6 | Offer Sustainability | Mercury free | Yes
XVBC6M6 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M6 | Contractual warranty | Warranty | 18 months
XVBC6M7 | Main | range of product | Harmony XVB Universal
XVBC6M7 | Main | product or component type | Indicator bank
XVBC6M7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M7 | Main | signalling type | Flashing
XVBC6M7 | Main | mounting diameter | 70 mm
XVBC6M7 | Main | component name | XVBC
XVBC6M7 | Main | material | Polycarbonate
XVBC6M7 | Main | light source | Integral flash discharge tube, clear
XVBC6M7 | Main | bulb type | Flash discharge tube
XVBC6M7 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M7 | Main | flash energy | 5 J
XVBC6M7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M7 | Complementary | current consumption | < 105 mA AC
XVBC6M7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC6M7 | Complementary | flashing frequency | 1 Hz
XVBC6M7 | Complementary | illuminating intensity | 13 cd
XVBC6M7 | Complementary | CAD overall width | 70 mm
XVBC6M7 | Complementary | CAD overall height | 157 mm
XVBC6M7 | Complementary | CAD overall depth | 70 mm
XVBC6M7 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBC6M7 | Environment | standards | EN/IEC 60947-5-1
XVBC6M7 | Environment | protective treatment | TC
XVBC6M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M7 | Offer Sustainability | Mercury free | Yes
XVBC6M7 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M7 | Contractual warranty | Warranty | 18 months
XVBC6M8 | Main | range of product | Harmony XVB Universal
XVBC6M8 | Main | product or component type | Indicator bank
XVBC6M8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC6M8 | Main | signalling type | Flashing
XVBC6M8 | Main | mounting diameter | 70 mm
XVBC6M8 | Main | component name | XVBC
XVBC6M8 | Main | material | Polycarbonate
XVBC6M8 | Main | light source | Integral flash discharge tube, yellow
XVBC6M8 | Main | bulb type | Flash discharge tube
XVBC6M8 | Main | [Us] rated supply voltage | 230 V AC
XVBC6M8 | Main | flash energy | 5 J
XVBC6M8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC6M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC6M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC6M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC6M8 | Complementary | current consumption | < 105 mA AC
XVBC6M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC6M8 | Complementary | flashing frequency | 1 Hz
XVBC6M8 | Complementary | CAD overall width | 70 mm
XVBC6M8 | Complementary | CAD overall height | 157 mm
XVBC6M8 | Complementary | CAD overall depth | 70 mm
XVBC6M8 | Environment | product certifications | UL 508 ¦ CSA C22-2 No 14 ¦ GOST ¦ CCC
XVBC6M8 | Environment | standards | EN/IEC 60947-5-1
XVBC6M8 | Environment | protective treatment | TC
XVBC6M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC6M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC6M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC6M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC6M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC6M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC6M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC6M8 | Offer Sustainability | Mercury free | Yes
XVBC6M8 | Offer Sustainability | RoHS exemption information | Yes
XVBC6M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC6M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC6M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC6M8 | Contractual warranty | Warranty | 18 months
XVBC8B3 | Main | range of product | Harmony XVB Universal
XVBC8B3 | Main | product or component type | Indicator bank
XVBC8B3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B3 | Main | signalling type | Flashing
XVBC8B3 | Main | mounting diameter | 70 mm
XVBC8B3 | Main | component name | XVBC
XVBC8B3 | Main | material | Polycarbonate
XVBC8B3 | Main | light source | Integral flash discharge tube, green
XVBC8B3 | Main | bulb type | Flash discharge tube
XVBC8B3 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B3 | Main | flash energy | 10 J
XVBC8B3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B3 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8B3 | Complementary | flashing frequency | 1 Hz
XVBC8B3 | Complementary | CAD overall width | 70 mm
XVBC8B3 | Complementary | CAD overall height | 157 mm
XVBC8B3 | Complementary | CAD overall depth | 70 mm
XVBC8B3 | Complementary | net weight | 0.305 kg
XVBC8B3 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBC8B3 | Environment | standards | EN/IEC 60947-5-1
XVBC8B3 | Environment | protective treatment | TC
XVBC8B3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B3 | Offer Sustainability | Mercury free | Yes
XVBC8B3 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B3 | Contractual warranty | Warranty | 18 months
XVBC8B4 | Main | range of product | Harmony XVB Universal
XVBC8B4 | Main | product or component type | Indicator bank
XVBC8B4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B4 | Main | signalling type | Flashing
XVBC8B4 | Main | mounting diameter | 70 mm
XVBC8B4 | Main | component name | XVBC
XVBC8B4 | Main | material | Polycarbonate
XVBC8B4 | Main | light source | Integral flash discharge tube, red
XVBC8B4 | Main | bulb type | Flash discharge tube
XVBC8B4 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B4 | Main | flash energy | 10 J
XVBC8B4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B4 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B4 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8B4 | Complementary | flashing frequency | 1 Hz
XVBC8B4 | Complementary | CAD overall width | 70 mm
XVBC8B4 | Complementary | CAD overall height | 157 mm
XVBC8B4 | Complementary | CAD overall depth | 70 mm
XVBC8B4 | Complementary | net weight | 0.305 kg
XVBC8B4 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ GOST ¦ UL 508
XVBC8B4 | Environment | standards | EN/IEC 60947-5-1
XVBC8B4 | Environment | protective treatment | TC
XVBC8B4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B4 | Offer Sustainability | Mercury free | Yes
XVBC8B4 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B4 | Contractual warranty | Warranty | 18 months
XVBC8B5 | Main | range of product | Harmony XVB Universal
XVBC8B5 | Main | product or component type | Indicator bank
XVBC8B5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B5 | Main | signalling type | Flashing
XVBC8B5 | Main | mounting diameter | 70 mm
XVBC8B5 | Main | component name | XVBC
XVBC8B5 | Main | material | Polycarbonate
XVBC8B5 | Main | light source | Integral flash discharge tube, orange
XVBC8B5 | Main | bulb type | Flash discharge tube
XVBC8B5 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B5 | Main | flash energy | 10 J
XVBC8B5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B5 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B5 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8B5 | Complementary | flashing frequency | 1 Hz
XVBC8B5 | Complementary | CAD overall width | 70 mm
XVBC8B5 | Complementary | CAD overall height | 157 mm
XVBC8B5 | Complementary | CAD overall depth | 70 mm
XVBC8B5 | Complementary | net weight | 0.305 kg
XVBC8B5 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBC8B5 | Environment | standards | EN/IEC 60947-5-1
XVBC8B5 | Environment | protective treatment | TC
XVBC8B5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B5 | Offer Sustainability | Mercury free | Yes
XVBC8B5 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B5 | Contractual warranty | Warranty | 18 months
XVBC8B6 | Main | range of product | Harmony XVB Universal
XVBC8B6 | Main | product or component type | Indicator bank
XVBC8B6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B6 | Main | signalling type | Flashing
XVBC8B6 | Main | mounting diameter | 70 mm
XVBC8B6 | Main | component name | XVBC
XVBC8B6 | Main | material | Polycarbonate
XVBC8B6 | Main | light source | Integral flash discharge tube, blue
XVBC8B6 | Main | bulb type | Flash discharge tube
XVBC8B6 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B6 | Main | flash energy | 10 J
XVBC8B6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B6 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B6 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8B6 | Complementary | flashing frequency | 1 Hz
XVBC8B6 | Complementary | CAD overall width | 70 mm
XVBC8B6 | Complementary | CAD overall height | 157 mm
XVBC8B6 | Complementary | CAD overall depth | 70 mm
XVBC8B6 | Complementary | net weight | 0.305 kg
XVBC8B6 | Environment | product certifications | UL 508 ¦ GOST ¦ CCC ¦ CSA C22-2 No 14
XVBC8B6 | Environment | standards | EN/IEC 60947-5-1
XVBC8B6 | Environment | protective treatment | TC
XVBC8B6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B6 | Offer Sustainability | Mercury free | Yes
XVBC8B6 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B6 | Contractual warranty | Warranty | 18 months
XVBC8B7 | Main | range of product | Harmony XVB Universal
XVBC8B7 | Main | product or component type | Indicator bank
XVBC8B7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B7 | Main | signalling type | Flashing
XVBC8B7 | Main | mounting diameter | 70 mm
XVBC8B7 | Main | component name | XVBC
XVBC8B7 | Main | material | Polycarbonate
XVBC8B7 | Main | light source | Integral flash discharge tube, clear
XVBC8B7 | Main | bulb type | Flash discharge tube
XVBC8B7 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B7 | Main | flash energy | 10 J
XVBC8B7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B7 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8B7 | Complementary | flashing frequency | 1 Hz
XVBC8B7 | Complementary | illuminating intensity | 26 cd
XVBC8B7 | Complementary | CAD overall width | 70 mm
XVBC8B7 | Complementary | CAD overall height | 157 mm
XVBC8B7 | Complementary | CAD overall depth | 70 mm
XVBC8B7 | Complementary | net weight | 0.305 kg
XVBC8B7 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ UL 508 ¦ GOST
XVBC8B7 | Environment | standards | EN/IEC 60947-5-1
XVBC8B7 | Environment | protective treatment | TC
XVBC8B7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B7 | Offer Sustainability | Mercury free | Yes
XVBC8B7 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B7 | Contractual warranty | Warranty | 18 months
XVBC8B8 | Main | range of product | Harmony XVB Universal
XVBC8B8 | Main | product or component type | Indicator bank
XVBC8B8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8B8 | Main | signalling type | Flashing
XVBC8B8 | Main | mounting diameter | 70 mm
XVBC8B8 | Main | component name | XVBC
XVBC8B8 | Main | material | Polycarbonate
XVBC8B8 | Main | light source | Integral flash discharge tube, yellow
XVBC8B8 | Main | bulb type | Flash discharge tube
XVBC8B8 | Main | [Us] rated supply voltage | 24 V AC/DC
XVBC8B8 | Main | flash energy | 10 J
XVBC8B8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8B8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8B8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8B8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8B8 | Complementary | current consumption | < 1300 mA AC ¦ < 850 mA DC
XVBC8B8 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8B8 | Complementary | flashing frequency | 1 Hz
XVBC8B8 | Complementary | CAD overall width | 70 mm
XVBC8B8 | Complementary | CAD overall height | 157 mm
XVBC8B8 | Complementary | CAD overall depth | 70 mm
XVBC8B8 | Complementary | net weight | 0.305 kg
XVBC8B8 | Environment | product certifications | CSA C22-2 No 14 ¦ GOST ¦ UL 508 ¦ CCC
XVBC8B8 | Environment | standards | EN/IEC 60947-5-1
XVBC8B8 | Environment | protective treatment | TC
XVBC8B8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8B8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8B8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8B8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8B8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8B8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8B8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8B8 | Offer Sustainability | Mercury free | Yes
XVBC8B8 | Offer Sustainability | RoHS exemption information | Yes
XVBC8B8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8B8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8B8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8B8 | Contractual warranty | Warranty | 18 months
XVBC8G3 | Main | range of product | Harmony XVB Universal
XVBC8G3 | Main | product or component type | Indicator bank
XVBC8G3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G3 | Main | signalling type | Flashing
XVBC8G3 | Main | mounting diameter | 70 mm
XVBC8G3 | Main | component name | XVBC
XVBC8G3 | Main | material | Polycarbonate
XVBC8G3 | Main | light source | Integral flash discharge tube, green
XVBC8G3 | Main | bulb type | Flash discharge tube
XVBC8G3 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G3 | Main | flash energy | 10 J
XVBC8G3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G3 | Complementary | current consumption | < 290 mA AC
XVBC8G3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8G3 | Complementary | flashing frequency | 1 Hz
XVBC8G3 | Complementary | CAD overall width | 70 mm
XVBC8G3 | Complementary | CAD overall height | 157 mm
XVBC8G3 | Complementary | CAD overall depth | 70 mm
XVBC8G3 | Complementary | net weight | 0.315 kg
XVBC8G3 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ GOST ¦ UL 508
XVBC8G3 | Environment | standards | EN/IEC 60947-5-1
XVBC8G3 | Environment | protective treatment | TC
XVBC8G3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G3 | Offer Sustainability | Mercury free | Yes
XVBC8G3 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G3 | Contractual warranty | Warranty | 18 months
XVBC8G4 | Main | range of product | Harmony XVB Universal
XVBC8G4 | Main | product or component type | Indicator bank
XVBC8G4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G4 | Main | signalling type | Flashing
XVBC8G4 | Main | mounting diameter | 70 mm
XVBC8G4 | Main | component name | XVBC
XVBC8G4 | Main | material | Polycarbonate
XVBC8G4 | Main | light source | Integral flash discharge tube, red
XVBC8G4 | Main | bulb type | Flash discharge tube
XVBC8G4 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G4 | Main | flash energy | 10 J
XVBC8G4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G4 | Complementary | current consumption | < 290 mA AC
XVBC8G4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8G4 | Complementary | flashing frequency | 1 Hz
XVBC8G4 | Complementary | CAD overall width | 70 mm
XVBC8G4 | Complementary | CAD overall height | 157 mm
XVBC8G4 | Complementary | CAD overall depth | 70 mm
XVBC8G4 | Complementary | net weight | 0.315 kg
XVBC8G4 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBC8G4 | Environment | standards | EN/IEC 60947-5-1
XVBC8G4 | Environment | protective treatment | TC
XVBC8G4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G4 | Offer Sustainability | Mercury free | Yes
XVBC8G4 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G4 | Contractual warranty | Warranty | 18 months
XVBC8G5 | Main | range of product | Harmony XVB Universal
XVBC8G5 | Main | product or component type | Indicator bank
XVBC8G5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G5 | Main | signalling type | Flashing
XVBC8G5 | Main | mounting diameter | 70 mm
XVBC8G5 | Main | component name | XVBC
XVBC8G5 | Main | material | Polycarbonate
XVBC8G5 | Main | light source | Integral flash discharge tube, orange
XVBC8G5 | Main | bulb type | Flash discharge tube
XVBC8G5 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G5 | Main | flash energy | 10 J
XVBC8G5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G5 | Complementary | current consumption | < 290 mA AC
XVBC8G5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8G5 | Complementary | flashing frequency | 1 Hz
XVBC8G5 | Complementary | CAD overall width | 70 mm
XVBC8G5 | Complementary | CAD overall height | 157 mm
XVBC8G5 | Complementary | CAD overall depth | 70 mm
XVBC8G5 | Complementary | net weight | 0.315 kg
XVBC8G5 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBC8G5 | Environment | standards | EN/IEC 60947-5-1
XVBC8G5 | Environment | protective treatment | TC
XVBC8G5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G5 | Offer Sustainability | Mercury free | Yes
XVBC8G5 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G5 | Contractual warranty | Warranty | 18 months
XVBC8G6 | Main | range of product | Harmony XVB Universal
XVBC8G6 | Main | product or component type | Indicator bank
XVBC8G6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G6 | Main | signalling type | Flashing
XVBC8G6 | Main | mounting diameter | 70 mm
XVBC8G6 | Main | component name | XVBC
XVBC8G6 | Main | material | Polycarbonate
XVBC8G6 | Main | light source | Integral flash discharge tube, blue
XVBC8G6 | Main | bulb type | Flash discharge tube
XVBC8G6 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G6 | Main | flash energy | 10 J
XVBC8G6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G6 | Complementary | current consumption | < 290 mA AC
XVBC8G6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8G6 | Complementary | flashing frequency | 1 Hz
XVBC8G6 | Complementary | CAD overall width | 70 mm
XVBC8G6 | Complementary | CAD overall height | 157 mm
XVBC8G6 | Complementary | CAD overall depth | 70 mm
XVBC8G6 | Complementary | net weight | 0.315 kg
XVBC8G6 | Environment | product certifications | UL 508 ¦ CCC ¦ GOST ¦ CSA C22-2 No 14
XVBC8G6 | Environment | standards | EN/IEC 60947-5-1
XVBC8G6 | Environment | protective treatment | TC
XVBC8G6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G6 | Offer Sustainability | Mercury free | Yes
XVBC8G6 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G6 | Contractual warranty | Warranty | 18 months
XVBC8G7 | Main | range of product | Harmony XVB Universal
XVBC8G7 | Main | product or component type | Indicator bank
XVBC8G7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G7 | Main | signalling type | Flashing
XVBC8G7 | Main | mounting diameter | 70 mm
XVBC8G7 | Main | component name | XVBC
XVBC8G7 | Main | material | Polycarbonate
XVBC8G7 | Main | light source | Integral flash discharge tube, clear
XVBC8G7 | Main | bulb type | Flash discharge tube
XVBC8G7 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G7 | Main | flash energy | 10 J
XVBC8G7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G7 | Complementary | current consumption | < 290 mA AC
XVBC8G7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8G7 | Complementary | flashing frequency | 1 Hz
XVBC8G7 | Complementary | illuminating intensity | 26 cd
XVBC8G7 | Complementary | CAD overall width | 70 mm
XVBC8G7 | Complementary | CAD overall height | 157 mm
XVBC8G7 | Complementary | CAD overall depth | 70 mm
XVBC8G7 | Complementary | net weight | 0.315 kg
XVBC8G7 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ CCC ¦ UL 508
XVBC8G7 | Environment | standards | EN/IEC 60947-5-1
XVBC8G7 | Environment | protective treatment | TC
XVBC8G7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G7 | Offer Sustainability | Mercury free | Yes
XVBC8G7 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G7 | Contractual warranty | Warranty | 18 months
XVBC8G8 | Main | range of product | Harmony XVB Universal
XVBC8G8 | Main | product or component type | Indicator bank
XVBC8G8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8G8 | Main | signalling type | Flashing
XVBC8G8 | Main | mounting diameter | 70 mm
XVBC8G8 | Main | component name | XVBC
XVBC8G8 | Main | material | Polycarbonate
XVBC8G8 | Main | light source | Integral flash discharge tube, yellow
XVBC8G8 | Main | bulb type | Flash discharge tube
XVBC8G8 | Main | [Us] rated supply voltage | 120 V AC
XVBC8G8 | Main | flash energy | 10 J
XVBC8G8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8G8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8G8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8G8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8G8 | Complementary | current consumption | < 290 mA AC
XVBC8G8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8G8 | Complementary | flashing frequency | 1 Hz
XVBC8G8 | Complementary | CAD overall width | 70 mm
XVBC8G8 | Complementary | CAD overall height | 157 mm
XVBC8G8 | Complementary | CAD overall depth | 70 mm
XVBC8G8 | Complementary | net weight | 0.315 kg
XVBC8G8 | Environment | product certifications | GOST ¦ CSA C22-2 No 14 ¦ UL 508 ¦ CCC
XVBC8G8 | Environment | standards | EN/IEC 60947-5-1
XVBC8G8 | Environment | protective treatment | TC
XVBC8G8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8G8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8G8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8G8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8G8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8G8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8G8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8G8 | Offer Sustainability | Mercury free | Yes
XVBC8G8 | Offer Sustainability | RoHS exemption information | Yes
XVBC8G8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8G8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8G8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8G8 | Contractual warranty | Warranty | 18 months
XVBC8M3 | Main | range of product | Harmony XVB Universal
XVBC8M3 | Main | product or component type | Indicator bank
XVBC8M3 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M3 | Main | signalling type | Flashing
XVBC8M3 | Main | mounting diameter | 70 mm
XVBC8M3 | Main | component name | XVBC
XVBC8M3 | Main | material | Polycarbonate
XVBC8M3 | Main | light source | Integral flash discharge tube, green
XVBC8M3 | Main | bulb type | Flash discharge tube
XVBC8M3 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M3 | Main | flash energy | 10 J
XVBC8M3 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M3 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M3 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M3 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M3 | Complementary | current consumption | < 280 mA AC
XVBC8M3 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8M3 | Complementary | flashing frequency | 1 Hz
XVBC8M3 | Complementary | CAD overall width | 70 mm
XVBC8M3 | Complementary | CAD overall height | 157 mm
XVBC8M3 | Complementary | CAD overall depth | 70 mm
XVBC8M3 | Complementary | net weight | 0.315 kg
XVBC8M3 | Environment | product certifications | CSA C22-2 No 14 ¦ CCC ¦ UL 508 ¦ GOST
XVBC8M3 | Environment | standards | EN/IEC 60947-5-1
XVBC8M3 | Environment | protective treatment | TC
XVBC8M3 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M3 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M3 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M3 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M3 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M3 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M3 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M3 | Offer Sustainability | Mercury free | Yes
XVBC8M3 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M3 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M3 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M3 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M3 | Contractual warranty | Warranty | 18 months
XVBC8M4 | Main | range of product | Harmony XVB Universal
XVBC8M4 | Main | product or component type | Indicator bank
XVBC8M4 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M4 | Main | signalling type | Flashing
XVBC8M4 | Main | mounting diameter | 70 mm
XVBC8M4 | Main | component name | XVBC
XVBC8M4 | Main | material | Polycarbonate
XVBC8M4 | Main | light source | Integral flash discharge tube, red
XVBC8M4 | Main | bulb type | Flash discharge tube
XVBC8M4 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M4 | Main | flash energy | 10 J
XVBC8M4 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M4 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M4 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M4 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M4 | Complementary | current consumption | < 280 mA AC
XVBC8M4 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8M4 | Complementary | flashing frequency | 1 Hz
XVBC8M4 | Complementary | CAD overall width | 70 mm
XVBC8M4 | Complementary | CAD overall height | 157 mm
XVBC8M4 | Complementary | CAD overall depth | 70 mm
XVBC8M4 | Complementary | net weight | 0.315 kg
XVBC8M4 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBC8M4 | Environment | standards | EN/IEC 60947-5-1
XVBC8M4 | Environment | protective treatment | TC
XVBC8M4 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M4 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M4 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M4 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M4 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M4 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M4 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M4 | Offer Sustainability | Mercury free | Yes
XVBC8M4 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M4 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M4 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M4 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M4 | Contractual warranty | Warranty | 18 months
XVBC8M5 | Main | range of product | Harmony XVB Universal
XVBC8M5 | Main | product or component type | Indicator bank
XVBC8M5 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M5 | Main | signalling type | Flashing
XVBC8M5 | Main | mounting diameter | 70 mm
XVBC8M5 | Main | component name | XVBC
XVBC8M5 | Main | material | Polycarbonate
XVBC8M5 | Main | light source | Integral flash discharge tube, orange
XVBC8M5 | Main | bulb type | Flash discharge tube
XVBC8M5 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M5 | Main | flash energy | 10 J
XVBC8M5 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M5 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M5 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M5 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M5 | Complementary | current consumption | < 280 mA AC
XVBC8M5 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
XVBC8M5 | Complementary | flashing frequency | 1 Hz
XVBC8M5 | Complementary | CAD overall width | 70 mm
XVBC8M5 | Complementary | CAD overall height | 157 mm
XVBC8M5 | Complementary | CAD overall depth | 70 mm
XVBC8M5 | Complementary | net weight | 0.315 kg
XVBC8M5 | Environment | product certifications | CSA C22-2 No 14 ¦ UL 508 ¦ CCC ¦ GOST
XVBC8M5 | Environment | standards | EN/IEC 60947-5-1
XVBC8M5 | Environment | protective treatment | TC
XVBC8M5 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M5 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M5 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M5 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M5 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M5 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M5 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M5 | Offer Sustainability | Mercury free | Yes
XVBC8M5 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M5 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M5 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M5 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M5 | Contractual warranty | Warranty | 18 months
XVBC8M6 | Main | range of product | Harmony XVB Universal
XVBC8M6 | Main | product or component type | Indicator bank
XVBC8M6 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M6 | Main | signalling type | Flashing
XVBC8M6 | Main | mounting diameter | 70 mm
XVBC8M6 | Main | component name | XVBC
XVBC8M6 | Main | material | Polycarbonate
XVBC8M6 | Main | light source | Integral flash discharge tube, blue
XVBC8M6 | Main | bulb type | Flash discharge tube
XVBC8M6 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M6 | Main | flash energy | 10 J
XVBC8M6 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M6 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M6 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M6 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M6 | Complementary | current consumption | < 280 mA AC
XVBC8M6 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8M6 | Complementary | flashing frequency | 1 Hz
XVBC8M6 | Complementary | CAD overall width | 70 mm
XVBC8M6 | Complementary | CAD overall height | 157 mm
XVBC8M6 | Complementary | CAD overall depth | 70 mm
XVBC8M6 | Complementary | net weight | 0.315 kg
XVBC8M6 | Environment | product certifications | CCC ¦ CSA C22-2 No 14 ¦ GOST ¦ UL 508
XVBC8M6 | Environment | standards | EN/IEC 60947-5-1
XVBC8M6 | Environment | protective treatment | TC
XVBC8M6 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M6 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M6 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M6 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M6 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M6 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M6 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M6 | Offer Sustainability | Mercury free | Yes
XVBC8M6 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M6 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M6 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M6 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M6 | Contractual warranty | Warranty | 18 months
XVBC8M7 | Main | range of product | Harmony XVB Universal
XVBC8M7 | Main | product or component type | Indicator bank
XVBC8M7 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M7 | Main | signalling type | Flashing
XVBC8M7 | Main | mounting diameter | 70 mm
XVBC8M7 | Main | component name | XVBC
XVBC8M7 | Main | material | Polycarbonate
XVBC8M7 | Main | light source | Integral flash discharge tube, clear
XVBC8M7 | Main | bulb type | Flash discharge tube
XVBC8M7 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M7 | Main | flash energy | 10 J
XVBC8M7 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M7 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M7 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M7 | Complementary | current consumption | < 280 mA AC
XVBC8M7 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8M7 | Complementary | flashing frequency | 1 Hz
XVBC8M7 | Complementary | illuminating intensity | 26 cd
XVBC8M7 | Complementary | CAD overall width | 70 mm
XVBC8M7 | Complementary | CAD overall height | 157 mm
XVBC8M7 | Complementary | CAD overall depth | 70 mm
XVBC8M7 | Complementary | net weight | 0.315 kg
XVBC8M7 | Environment | product certifications | CCC ¦ GOST ¦ CSA C22-2 No 14 ¦ UL 508
XVBC8M7 | Environment | standards | EN/IEC 60947-5-1
XVBC8M7 | Environment | protective treatment | TC
XVBC8M7 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M7 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M7 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M7 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M7 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M7 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M7 | Offer Sustainability | Mercury free | Yes
XVBC8M7 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M7 | Contractual warranty | Warranty | 18 months
XVBC8M8 | Main | range of product | Harmony XVB Universal
XVBC8M8 | Main | product or component type | Indicator bank
XVBC8M8 | Main | beacon or indicator bank unit type | Illuminated unit
XVBC8M8 | Main | signalling type | Flashing
XVBC8M8 | Main | mounting diameter | 70 mm
XVBC8M8 | Main | component name | XVBC
XVBC8M8 | Main | material | Polycarbonate
XVBC8M8 | Main | light source | Integral flash discharge tube, yellow
XVBC8M8 | Main | bulb type | Flash discharge tube
XVBC8M8 | Main | [Us] rated supply voltage | 230 V AC
XVBC8M8 | Main | flash energy | 10 J
XVBC8M8 | Complementary | assembly style | Customer assembly, up to 5 units
XVBC8M8 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
XVBC8M8 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
XVBC8M8 | Complementary | nominal voltage limit | 0.85...1.1 Un conforming to IEC 60947-5-1
XVBC8M8 | Complementary | current consumption | < 280 mA AC
XVBC8M8 | Complementary | [Uimp] rated impulse withstand voltage | IEC 60947-1 4 kV
XVBC8M8 | Complementary | flashing frequency | 1 Hz
XVBC8M8 | Complementary | CAD overall width | 70 mm
XVBC8M8 | Complementary | CAD overall height | 157 mm
XVBC8M8 | Complementary | CAD overall depth | 70 mm
XVBC8M8 | Complementary | net weight | 0.315 kg
XVBC8M8 | Environment | product certifications | UL 508 ¦ CCC ¦ CSA C22-2 No 14 ¦ GOST
XVBC8M8 | Environment | standards | EN/IEC 60947-5-1
XVBC8M8 | Environment | protective treatment | TC
XVBC8M8 | Environment | ambient air temperature for storage | -40…70 °C
XVBC8M8 | Environment | electrical shock protection class | Class I on support tube conforming to IEC 61140 ¦ Class II on base unit conforming to IEC 61140
XVBC8M8 | Environment | IP degree of protection | IP65 on fixing base XVBZ0. conforming to IEC 60529 ¦ IP66 on base unit conforming to IEC 60529
XVBC8M8 | Environment | NEMA degree of protection | NEMA 4X conforming to UL 508 (indoor)
XVBC8M8 | Offer Sustainability | Sustainable offer status | Green Premium product
XVBC8M8 | Offer Sustainability | REACh Regulation | REACh Declaration
XVBC8M8 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
XVBC8M8 | Offer Sustainability | Mercury free | Yes
XVBC8M8 | Offer Sustainability | RoHS exemption information | Yes
XVBC8M8 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
XVBC8M8 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
XVBC8M8 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
XVBC8M8 | Contractual warranty | Warranty | 18 months