## Sheet1
Reference | Section | Parameters | Value
RM17JC00MW | Main | range of product | Zelio Control
RM17JC00MW | Main | product or component type | Modular measurement and control relays
RM17JC00MW | Main | relay type | Current control relay
RM17JC00MW | Main | relay name | RM17JC
RM17JC00MW | Main | relay monitored parameters | Overcurrent detection
RM17JC00MW | Main | time delay | Without
RM17JC00MW | Main | switching capacity in VA | 1250 VA
RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC
RM17JC00MW | Main | maximum power consumption in VA | 3 VA
RM17JC00MW | Main | measurement range | 2...20 A current
RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1 ¦ DC-14 conforming to IEC 60947-5-1
RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC
RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
RM17JC00MW | Complementary | maximum power consumption in W | 1 W
RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal
RM17JC00MW | Complementary | output contacts | 1 C/O
RM17JC00MW | Complementary | nominal output current | 5 A
RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting
RM17JC00MW | Complementary | delay at power up | 0.5 s
RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault)
RM17JC00MW | Complementary | polarity | Yes DC
RM17JC00MW | Complementary | threshold setting | 10...100 %
RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C ¦ 300000 mA non repetitive < 3 s at 25 °C
RM17JC00MW | Complementary | marking | CE : 73/23/EEC ¦ CE : EMC 89/336/EEC
RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17JC00MW | Complementary | insulation | Between supply and measurement
RM17JC00MW | Complementary | operating position | Any position without derating
RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17JC00MW | Complementary | housing material | Self-extinguishing plastic
RM17JC00MW | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17JC00MW | Complementary | electrical durability | 100000 cycles
RM17JC00MW | Complementary | mechanical durability | 30000000 cycles
RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load
RM17JC00MW | Complementary | contacts material | Cadmium free
RM17JC00MW | Complementary | width | 17.5 mm
RM17JC00MW | Complementary | net weight | 0.13 kg
RM17JC00MW | Environment | immunity to microbreaks | 10 ms
RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
RM17JC00MW | Environment | standards | EN/IEC 60255-6
RM17JC00MW | Environment | product certifications | GL ¦ C-Tick ¦ GOST ¦ UL ¦ CSA
RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C
RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C
RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
RM17JC00MW | Environment | non-dissipating shock wave | 4 kV
RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product
RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration
RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17JC00MW | Offer Sustainability | Mercury free | Yes
RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes
RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information
RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17JC00MW | Contractual warranty | Warranty | 18 months
RM17TA00 | Main | range of product | Zelio Control
RM17TA00 | Main | product or component type | Modular measurement and control relays
RM17TA00 | Main | relay type | Multifunction control relay
RM17TA00 | Main | product specific application | For 3-phase supply
RM17TA00 | Main | relay name | RM17TA
RM17TA00 | Main | relay monitored parameters | Asymmetry ¦ Phase sequence ¦ Phase failure detection
RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM17TA00 | Main | switching capacity in VA | 1250 VA
RM17TA00 | Main | measurement range | 208...480 V voltage AC
RM17TA00 | Complementary | reset time | 1500 ms time delay
RM17TA00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TA00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TA00 | Complementary | supply voltage limits | 183…528 V AC
RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TA00 | Complementary | output contacts | 1 C/O
RM17TA00 | Complementary | nominal output current | 5 A
RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TA00 | Complementary | hysteresis | 2 %
RM17TA00 | Complementary | delay at power up | 650 ms
RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC ¦ 2...20 % of Un selected ¦ -2...-17 % in the range 220 V AC ¦ -2...-12 % in the range 208 V AC
RM17TA00 | Complementary | voltage range | 208...480 V phase to phase
RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TA00 | Complementary | marking | CE
RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TA00 | Complementary | operating position | Any position without derating
RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TA00 | Complementary | housing material | Self-extinguishing plastic
RM17TA00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TA00 | Complementary | electrical durability | 100000 cycles
RM17TA00 | Complementary | mechanical durability | 30000000 cycles
RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TA00 | Complementary | width | 17.5 mm
RM17TA00 | Complementary | net weight | 0.13 kg
RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TA00 | Environment | standards | EN/IEC 60255-1
RM17TA00 | Environment | product certifications | GOST ¦ CSA ¦ GL ¦ C-Tick ¦ UL
RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TA00 | Offer Sustainability | Mercury free | Yes
RM17TA00 | Offer Sustainability | RoHS exemption information | Yes
RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TA00 | Contractual warranty | Warranty | 18 months
RM17TE00 | Main | range of product | Zelio Control
RM17TE00 | Main | product or component type | Modular measurement and control relays
RM17TE00 | Main | relay type | Multifunction control relay
RM17TE00 | Main | product specific application | For 3-phase supply
RM17TE00 | Main | relay name | RM17TE
RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode ¦ Asymmetry ¦ Phase sequence ¦ Phase failure detection
RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
RM17TE00 | Main | switching capacity in VA | 1250 VA
RM17TE00 | Main | measurement range | 208...480 V voltage AC
RM17TE00 | Complementary | reset time | 1500 ms time delay
RM17TE00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TE00 | Complementary | maximum switching current | 5 A AC ¦ 5 A DC
RM17TE00 | Complementary | supply voltage limits | 183…528 V AC
RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TE00 | Complementary | output contacts | 1 C/O
RM17TE00 | Complementary | nominal output current | 5 A
RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TE00 | Complementary | hysteresis | 2 %
RM17TE00 | Complementary | delay at power up | 650 ms
RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC ¦ +2...+17 % in the range 480 V AC ¦ -2...-12 % in the range 208 V AC ¦ 2...20 % of Un selected
RM17TE00 | Complementary | voltage range | 208...480 V phase to phase
RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit ¦ 3 % for time delay
RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation ¦ < 1 % over the whole range with voltage variation
RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un
RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault)
RM17TE00 | Complementary | marking | CE
RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TE00 | Complementary | operating position | Any position without derating
RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TE00 | Complementary | housing material | Self-extinguishing plastic
RM17TE00 | Complementary | local signalling | LED (green) for power ON ¦ LED (yellow) for relay ON
RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TE00 | Complementary | electrical durability | 100000 cycles
RM17TE00 | Complementary | mechanical durability | 30000000 cycles
RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years ¦ B10d = 470000
RM17TE00 | Complementary | width | 17.5 mm
RM17TE00 | Complementary | net weight | 0.13 kg
RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TE00 | Environment | standards | EN/IEC 60255-1
RM17TE00 | Environment | product certifications | GOST ¦ C-Tick ¦ CSA ¦ UL ¦ GL
RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility ¦ 73/23/EEC - low voltage directive
RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 ¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 ¦ 4 kV conforming to IEC 60664-1 ¦ 4 kV conforming to IEC 61000-4-5
RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TE00 | Offer Sustainability | Mercury free | Yes
RM17TE00 | Offer Sustainability | RoHS exemption information | Yes
RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TE00 | Contractual warranty | Warranty | 18 months
RM17TG00 | Main | range of product | Zelio Control
RM17TG00 | Main | product or component type | Modular measurement and control relays
RM17TG00 | Main | relay type | Control relay
RM17TG00 | Main | product specific application | For 3-phase supply
RM17TG00 | Main | relay name | RM17TG
RM17TG00 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection (2 or more phase cut)
RM17TG00 | Main | time delay | Without
RM17TG00 | Main | switching capacity in VA | 1250 VA
RM17TG00 | Main | measurement range | 208...480 V voltage AC
RM17TG00 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TG00 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TG00 | Complementary | supply voltage limits | 183…528 V AC
RM17TG00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TG00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TG00 | Complementary | voltage detection threshold | < 100 V AC
RM17TG00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TG00 | Complementary | output contacts | 1 C/O
RM17TG00 | Complementary | nominal output current | 5 A
RM17TG00 | Complementary | measurement voltage limits | 183…528 V AC
RM17TG00 | Complementary | delay at power up | 650 ms
RM17TG00 | Complementary | voltage range | 183...528 V
RM17TG00 | Complementary | response time | <= 130 ms (in the event of a fault)
RM17TG00 | Complementary | marking | CE
RM17TG00 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TG00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TG00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TG00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TG00 | Complementary | operating position | Any position without derating
RM17TG00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TG00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TG00 | Complementary | housing material | Self-extinguishing plastic
RM17TG00 | Complementary | local signalling | LED (yellow) for relay ON
RM17TG00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TG00 | Complementary | electrical durability | 100000 cycles
RM17TG00 | Complementary | mechanical durability | 30000000 cycles
RM17TG00 | Complementary | operating rate | <= 360 operations/hour full load
RM17TG00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TG00 | Complementary | safety reliability data | MTTFd = 924.6 years ¦ B10d = 850000
RM17TG00 | Complementary | width | 17.5 mm
RM17TG00 | Complementary | net weight | 0.13 kg
RM17TG00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TG00 | Environment | standards | EN/IEC 60255-1
RM17TG00 | Environment | product certifications | C-Tick ¦ GL ¦ CSA ¦ UL ¦ GOST
RM17TG00 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TG00 | Environment | ambient air temperature for storage | -40…70 °C
RM17TG00 | Environment | ambient air temperature for operation | -20…50 °C
RM17TG00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TG00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TG00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TG00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TG00 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TG00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM17TG00 | Environment | non-dissipating shock wave | 4 kV
RM17TG00 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TG00 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TG00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TG00 | Offer Sustainability | Mercury free | Yes
RM17TG00 | Offer Sustainability | RoHS exemption information | Yes
RM17TG00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TG00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TG00 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TG00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TG00 | Contractual warranty | Warranty | 18 months
RM17TG20 | Main | range of product | Zelio Control
RM17TG20 | Main | product or component type | Modular measurement and control relays
RM17TG20 | Main | relay type | Control relay
RM17TG20 | Main | product specific application | For 3-phase supply
RM17TG20 | Main | relay name | RM17TG
RM17TG20 | Main | relay monitored parameters | Phase sequence ¦ Phase failure detection (2 or more phase cut)
RM17TG20 | Main | time delay | Without
RM17TG20 | Main | switching capacity in VA | 1250 VA
RM17TG20 | Main | measurement range | 208...480 V voltage AC
RM17TG20 | Complementary | maximum switching voltage | 250 V AC ¦ 250 V DC
RM17TG20 | Complementary | minimum switching current | 10 mA at 5 V DC
RM17TG20 | Complementary | supply voltage limits | 183…484 V AC
RM17TG20 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
RM17TG20 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
RM17TG20 | Complementary | voltage detection threshold | < 100 V AC
RM17TG20 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
RM17TG20 | Complementary | output contacts | 2 C/O
RM17TG20 | Complementary | nominal output current | 5 A
RM17TG20 | Complementary | measurement voltage limits | 183…528 V AC
RM17TG20 | Complementary | delay at power up | 650 ms
RM17TG20 | Complementary | voltage range | 183...484 V
RM17TG20 | Complementary | response time | <= 130 ms (in the event of a fault)
RM17TG20 | Complementary | marking | CE
RM17TG20 | Complementary | overvoltage category | III conforming to IEC 60664-1
RM17TG20 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 ¦ > 500 MOhm at 500 V DC conforming to IEC 60664-1
RM17TG20 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
RM17TG20 | Complementary | supply frequency | 50/60 Hz +/- 10 %
RM17TG20 | Complementary | operating position | Any position without derating
RM17TG20 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end ¦ Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end ¦ Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end ¦ Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
RM17TG20 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
RM17TG20 | Complementary | housing material | Self-extinguishing plastic
RM17TG20 | Complementary | local signalling | LED (yellow) for relay ON
RM17TG20 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
RM17TG20 | Complementary | electrical durability | 10000 cycles
RM17TG20 | Complementary | mechanical durability | 30000000 cycles
RM17TG20 | Complementary | operating rate | <= 360 operations/hour full load
RM17TG20 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 ¦ AC-13 conforming to IEC 60947-5-1 ¦ AC-14 conforming to IEC 60947-5-1 ¦ AC-15 conforming to IEC 60947-5-1 ¦ DC-12 conforming to IEC 60947-5-1 ¦ DC-13 conforming to IEC 60947-5-1
RM17TG20 | Complementary | safety reliability data | B10d = 850000 ¦ MTTFd = 924.6 years
RM17TG20 | Complementary | width | 17.5 mm
RM17TG20 | Complementary | net weight | 0.13 kg
RM17TG20 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 ¦ Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 ¦ Immunity for industrial environments conforming to EN/IEC 61000-6-2
RM17TG20 | Environment | standards | EN/IEC 60255-1
RM17TG20 | Environment | product certifications | GOST ¦ C-Tick ¦ UL ¦ CSA ¦ GL
RM17TG20 | Environment | directives | 73/23/EEC - low voltage directive ¦ 89/336/EEC - electromagnetic compatibility
RM17TG20 | Environment | ambient air temperature for storage | -40…70 °C
RM17TG20 | Environment | ambient air temperature for operation | -20…50 °C
RM17TG20 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
RM17TG20 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 ¦ 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
RM17TG20 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
RM17TG20 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 ¦ IP30 (casing) conforming to IEC 60529
RM17TG20 | Environment | pollution degree | 3 conforming to IEC 60664-1
RM17TG20 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz
RM17TG20 | Environment | non-dissipating shock wave | 4 kV
RM17TG20 | Offer Sustainability | Sustainable offer status | Green Premium product
RM17TG20 | Offer Sustainability | REACh Regulation | REACh Declaration
RM17TG20 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
RM17TG20 | Offer Sustainability | Mercury free | Yes
RM17TG20 | Offer Sustainability | RoHS exemption information | Yes
RM17TG20 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
RM17TG20 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
RM17TG20 | Offer Sustainability | Circularity Profile | End of Life Information
RM17TG20 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
RM17TG20 | Contractual warranty | Warranty | 18 months