## status
0 | RM17JC00MW | https://www.se.com/sg/en/product/RM17JC00MW/ | Found
1 | RM17TA00 | https://www.se.com/sg/en/product/RM17TA00/ | Found
2 | RM17TE00 | https://www.se.com/sg/en/product/RM17TE00/ | Found
3 | RM10TE00 | https://www.se.com/sg/en/product/RM10TE00/ | Not Found
4 | RE22R2AMR | https://www.se.com/sg/en/product/RE22R2AMR/ | Found
5 | RE22R2CMR | https://www.se.com/sg/en/product/RE22R2CMR/ | Found
6 | RMTJ60BD | https://www.se.com/sg/en/product/RMTJ60BD/ | Found
7 | XVDLS37 | https://www.se.com/sg/en/product/XVDLS37/ | Found
8 | XVDLS38 | https://www.se.com/sg/en/product/XVDLS38/ | Found
9 | RHT428B | https://www.se.com/sg/en/product/RHT428B/ | Found
10 | RHT418BE | https://www.se.com/sg/en/product/RHT418BE/ | Not Found
11 | RSB1A160M7S | https://www.se.com/sg/en/product/RSB1A160M7S/ | Not Found
12 | RSB1A160NDS | https://www.se.com/sg/en/product/RSB1A160NDS/ | Not Found
13 | RSB2A080P7S | https://www.se.com/sg/en/product/RSB2A080P7S/ | Found
14 | RSB2A080RDS | https://www.se.com/sg/en/product/RSB2A080RDS/ | Not Found
15 | RSB2A080U7S | https://www.se.com/sg/en/product/RSB2A080U7S/ | Not Found
16 | RSB2A080M7S | https://www.se.com/sg/en/product/RSB2A080M7S/ | Not Found

## raw_datasheet
| Reference | Section | Parameters | Value
0 | RM17JC00MW | Main | range of product | Zelio Control
1 | RM17JC00MW | Main | product or component type | Modular measurement and control relays
2 | RM17JC00MW | Main | relay type | Current control relay
3 | RM17JC00MW | Main | relay name | RM17JC
4 | RM17JC00MW | Main | relay monitored parameters | Overcurrent detection
5 | RM17JC00MW | Main | time delay | Without
6 | RM17JC00MW | Main | switching capacity in VA | 1250 VA
7 | RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC
8 | RM17JC00MW | Main | maximum power consumption in VA | 3 VA
9 | RM17JC00MW | Main | measurement range | 2...20 A current
10 | RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
11 | RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC
12 | RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 %
13 | RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC
14 | RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un
15 | RM17JC00MW | Complementary | maximum power consumption in W | 1 W
16 | RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal
17 | RM17JC00MW | Complementary | output contacts | 1 C/O
18 | RM17JC00MW | Complementary | nominal output current | 5 A
19 | RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value
20 | RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting
21 | RM17JC00MW | Complementary | delay at power up | 0.5 s
22 | RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value
23 | RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit
24 | RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
25 | RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault)
26 | RM17JC00MW | Complementary | polarity | Yes DC
27 | RM17JC00MW | Complementary | threshold setting | 10...100 %
28 | RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
29 | RM17JC00MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC
30 | RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1
31 | RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
32 | RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
33 | RM17JC00MW | Complementary | insulation | Between supply and measurement
34 | RM17JC00MW | Complementary | operating position | Any position without derating
35 | RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
36 | RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
37 | RM17JC00MW | Complementary | housing material | Self-extinguishing plastic
38 | RM17JC00MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
39 | RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
40 | RM17JC00MW | Complementary | electrical durability | 100000 cycles
41 | RM17JC00MW | Complementary | mechanical durability | 30000000 cycles
42 | RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load
43 | RM17JC00MW | Complementary | contacts material | Cadmium free
44 | RM17JC00MW | Complementary | width | 17.5 mm
45 | RM17JC00MW | Complementary | net weight | 0.13 kg
46 | RM17JC00MW | Environment | immunity to microbreaks | 10 ms
47 | RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2
48 | RM17JC00MW | Environment | standards | EN/IEC 60255-6
49 | RM17JC00MW | Environment | product certifications | GL C-Tick GOST UL CSA
50 | RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C
51 | RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C
52 | RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
53 | RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
54 | RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
55 | RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
56 | RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1
57 | RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz
58 | RM17JC00MW | Environment | non-dissipating shock wave | 4 kV
59 | RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product
60 | RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration
61 | RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
62 | RM17JC00MW | Offer Sustainability | Mercury free | Yes
63 | RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes
64 | RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration
65 | RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
66 | RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information
67 | RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
68 | RM17JC00MW | Contractual warranty | Warranty | 18 months
69 | RM17TA00 | Main | range of product | Zelio Control
70 | RM17TA00 | Main | product or component type | Modular measurement and control relays
71 | RM17TA00 | Main | relay type | Multifunction control relay
72 | RM17TA00 | Main | product specific application | For 3-phase supply
73 | RM17TA00 | Main | relay name | RM17TA
74 | RM17TA00 | Main | relay monitored parameters | Asymmetry Phase sequence Phase failure detection
75 | RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
76 | RM17TA00 | Main | switching capacity in VA | 1250 VA
77 | RM17TA00 | Main | measurement range | 208...480 V voltage AC
78 | RM17TA00 | Complementary | reset time | 1500 ms time delay
79 | RM17TA00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
80 | RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC
81 | RM17TA00 | Complementary | maximum switching current | 5 A AC 5 A DC
82 | RM17TA00 | Complementary | supply voltage limits | 183…528 V AC
83 | RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
84 | RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
85 | RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
86 | RM17TA00 | Complementary | output contacts | 1 C/O
87 | RM17TA00 | Complementary | nominal output current | 5 A
88 | RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC
89 | RM17TA00 | Complementary | hysteresis | 2 %
90 | RM17TA00 | Complementary | delay at power up | 650 ms
91 | RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
92 | RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC
93 | RM17TA00 | Complementary | voltage range | 208...480 V phase to phase
94 | RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
95 | RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
96 | RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
97 | RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un
98 | RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault)
99 | RM17TA00 | Complementary | marking | CE
100 | RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1
101 | RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
102 | RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
103 | RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
104 | RM17TA00 | Complementary | operating position | Any position without derating
105 | RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
106 | RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
107 | RM17TA00 | Complementary | housing material | Self-extinguishing plastic
108 | RM17TA00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
109 | RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
110 | RM17TA00 | Complementary | electrical durability | 100000 cycles
111 | RM17TA00 | Complementary | mechanical durability | 30000000 cycles
112 | RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load
113 | RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
114 | RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
115 | RM17TA00 | Complementary | width | 17.5 mm
116 | RM17TA00 | Complementary | net weight | 0.13 kg
117 | RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
118 | RM17TA00 | Environment | standards | EN/IEC 60255-1
119 | RM17TA00 | Environment | product certifications | GOST CSA GL C-Tick UL
120 | RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
121 | RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C
122 | RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C
123 | RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
124 | RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
125 | RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
126 | RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
127 | RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1
128 | RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
129 | RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
130 | RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product
131 | RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration
132 | RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
133 | RM17TA00 | Offer Sustainability | Mercury free | Yes
134 | RM17TA00 | Offer Sustainability | RoHS exemption information | Yes
135 | RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
136 | RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
137 | RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information
138 | RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
139 | RM17TA00 | Contractual warranty | Warranty | 18 months
140 | RM17TE00 | Main | range of product | Zelio Control
141 | RM17TE00 | Main | product or component type | Modular measurement and control relays
142 | RM17TE00 | Main | relay type | Multifunction control relay
143 | RM17TE00 | Main | product specific application | For 3-phase supply
144 | RM17TE00 | Main | relay name | RM17TE
145 | RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
146 | RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value
147 | RM17TE00 | Main | switching capacity in VA | 1250 VA
148 | RM17TE00 | Main | measurement range | 208...480 V voltage AC
149 | RM17TE00 | Complementary | reset time | 1500 ms time delay
150 | RM17TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC
151 | RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC
152 | RM17TE00 | Complementary | maximum switching current | 5 A AC 5 A DC
153 | RM17TE00 | Complementary | supply voltage limits | 183…528 V AC
154 | RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un
155 | RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz
156 | RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 %
157 | RM17TE00 | Complementary | output contacts | 1 C/O
158 | RM17TE00 | Complementary | nominal output current | 5 A
159 | RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC
160 | RM17TE00 | Complementary | hysteresis | 2 %
161 | RM17TE00 | Complementary | delay at power up | 650 ms
162 | RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value
163 | RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
164 | RM17TE00 | Complementary | voltage range | 208...480 V phase to phase
165 | RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected
166 | RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay
167 | RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
168 | RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un
169 | RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault)
170 | RM17TE00 | Complementary | marking | CE
171 | RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1
172 | RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
173 | RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1
174 | RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 %
175 | RM17TE00 | Complementary | operating position | Any position without derating
176 | RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
177 | RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
178 | RM17TE00 | Complementary | housing material | Self-extinguishing plastic
179 | RM17TE00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON
180 | RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
181 | RM17TE00 | Complementary | electrical durability | 100000 cycles
182 | RM17TE00 | Complementary | mechanical durability | 30000000 cycles
183 | RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load
184 | RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
185 | RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000
186 | RM17TE00 | Complementary | width | 17.5 mm
187 | RM17TE00 | Complementary | net weight | 0.13 kg
188 | RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
189 | RM17TE00 | Environment | standards | EN/IEC 60255-1
190 | RM17TE00 | Environment | product certifications | GOST C-Tick CSA UL GL
191 | RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
192 | RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C
193 | RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C
194 | RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30
195 | RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1
196 | RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1
197 | RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529
198 | RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1
199 | RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
200 | RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
201 | RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product
202 | RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration
203 | RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
204 | RM17TE00 | Offer Sustainability | Mercury free | Yes
205 | RM17TE00 | Offer Sustainability | RoHS exemption information | Yes
206 | RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
207 | RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
208 | RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information
209 | RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
210 | RM17TE00 | Contractual warranty | Warranty | 18 months
211 | RE22R2AMR | Main | range of product | Zelio Time
212 | RE22R2AMR | Main | product or component type | Modular timing relay
213 | RE22R2AMR | Main | discrete output type | Relay
214 | RE22R2AMR | Main | device short name | RE22
215 | RE22R2AMR | Main | nominal output current | 8 A
216 | RE22R2AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
217 | RE22R2AMR | Complementary | time delay type | Aw A
218 | RE22R2AMR | Complementary | time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min
219 | RE22R2AMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external
220 | RE22R2AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
221 | RE22R2AMR | Complementary | Release input voltage | <= 2.4 V
222 | RE22R2AMR | Complementary | voltage range | 0.85...1.1 Us
223 | RE22R2AMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
224 | RE22R2AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
225 | RE22R2AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
226 | RE22R2AMR | Complementary | housing material | Self-extinguishing
227 | RE22R2AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
228 | RE22R2AMR | Complementary | temperature drift | +/- 0.05 %/°C
229 | RE22R2AMR | Complementary | voltage drift | +/- 0.2 %/V
230 | RE22R2AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
231 | RE22R2AMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
232 | RE22R2AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
233 | RE22R2AMR | Complementary | Recovery time | 120 ms on de-energisation
234 | RE22R2AMR | Complementary | immunity to microbreaks | 10 ms
235 | RE22R2AMR | Complementary | power consumption in VA | 3 VA at 240 V AC
236 | RE22R2AMR | Complementary | power consumption in W | 1.5 W at 240 V DC
237 | RE22R2AMR | Complementary | switching capacity in VA | 2000 VA
238 | RE22R2AMR | Complementary | minimum switching current | 10 mA at 5 V DC
239 | RE22R2AMR | Complementary | maximum switching current | 8 A
240 | RE22R2AMR | Complementary | maximum switching voltage | 250 V AC
241 | RE22R2AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
242 | RE22R2AMR | Complementary | mechanical durability | 10000000 cycles
243 | RE22R2AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
244 | RE22R2AMR | Complementary | Power on delay | 100 ms
245 | RE22R2AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
246 | RE22R2AMR | Complementary | overvoltage category | III conforming to IEC 60664-1
247 | RE22R2AMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years
248 | RE22R2AMR | Complementary | mounting position | Any position
249 | RE22R2AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
250 | RE22R2AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
251 | RE22R2AMR | Complementary | width | 22.5 mm
252 | RE22R2AMR | Complementary | net weight | 0.105 kg
253 | RE22R2AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
254 | RE22R2AMR | Environment | standards | UL 508 IEC 61812-1
255 | RE22R2AMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive
256 | RE22R2AMR | Environment | product certifications | CE CCC GL China RoHS UL RCM EAC CSA
257 | RE22R2AMR | Environment | ambient air temperature for operation | -20…60 °C
258 | RE22R2AMR | Environment | ambient air temperature for storage | -40…70 °C
259 | RE22R2AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
260 | RE22R2AMR | Environment | pollution degree | 3 conforming to IEC 60664-1
261 | RE22R2AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
262 | RE22R2AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
263 | RE22R2AMR | Environment | relative humidity | 95 % at 25…55 °C
264 | RE22R2AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
265 | RE22R2AMR | Offer Sustainability | Sustainable offer status | Green Premium product
266 | RE22R2AMR | Offer Sustainability | REACh Regulation | REACh Declaration
267 | RE22R2AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
268 | RE22R2AMR | Offer Sustainability | Mercury free | Yes
269 | RE22R2AMR | Offer Sustainability | RoHS exemption information | Yes
270 | RE22R2AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
271 | RE22R2AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
272 | RE22R2AMR | Offer Sustainability | Circularity Profile | End of Life Information
273 | RE22R2CMR | Main | range of product | Zelio Time
274 | RE22R2CMR | Main | product or component type | Modular timing relay
275 | RE22R2CMR | Main | discrete output type | Relay
276 | RE22R2CMR | Main | device short name | RE22
277 | RE22R2CMR | Main | nominal output current | 8 A
278 | RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
279 | RE22R2CMR | Complementary | time delay type | C
280 | RE22R2CMR | Complementary | time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
281 | RE22R2CMR | Complementary | control type | Rotary knob Diagnostic button
282 | RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz
283 | RE22R2CMR | Complementary | Release input voltage | <= 2.4 V
284 | RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us
285 | RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 %
286 | RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
287 | RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1
288 | RE22R2CMR | Complementary | housing material | Self-extinguishing
289 | RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1
290 | RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C
291 | RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V
292 | RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
293 | RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms
294 | RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1
295 | RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation
296 | RE22R2CMR | Complementary | immunity to microbreaks | 10 ms
297 | RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC
298 | RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC
299 | RE22R2CMR | Complementary | switching capacity in VA | 2000 VA
300 | RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC
301 | RE22R2CMR | Complementary | maximum switching current | 8 A
302 | RE22R2CMR | Complementary | maximum switching voltage | 250 V AC
303 | RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1
304 | RE22R2CMR | Complementary | mechanical durability | 10000000 cycles
305 | RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1
306 | RE22R2CMR | Complementary | Power on delay | 100 ms
307 | RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1
308 | RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1
309 | RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000
310 | RE22R2CMR | Complementary | mounting position | Any position
311 | RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715
312 | RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
313 | RE22R2CMR | Complementary | width | 22.5 mm
314 | RE22R2CMR | Complementary | net weight | 0.105 kg
315 | RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1
316 | RE22R2CMR | Environment | standards | UL 508 IEC 61812-1
317 | RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
318 | RE22R2CMR | Environment | product certifications | CSA CCC RCM China RoHS CE GL UL EAC
319 | RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C
320 | RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C
321 | RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529
322 | RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1
323 | RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6
324 | RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27
325 | RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C
326 | RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
327 | RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product
328 | RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration
329 | RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
330 | RE22R2CMR | Offer Sustainability | Mercury free | Yes
331 | RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes
332 | RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration
333 | RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
334 | RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information
335 | RMTJ60BD | Main | range of product | Zelio Analog
336 | RMTJ60BD | Main | product or component type | Converter for thermocouples
337 | RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
338 | RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
339 | RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
340 | RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
341 | RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken
342 | RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated
343 | RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output
344 | RMTJ60BD | Complementary | local signalling | LED (green)power ON:
345 | RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
346 | RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
347 | RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C
348 | RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C
349 | RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
350 | RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m
351 | RMTJ60BD | Complementary | marking | CE
352 | RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
353 | RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV
354 | RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
355 | RMTJ60BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years
356 | RMTJ60BD | Complementary | net weight | 0.12 kg
357 | RMTJ60BD | Environment | standards | IEC 60584-1 IEC 60947-1
358 | RMTJ60BD | Environment | product certifications | CSA GL UL
359 | RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing)
360 | RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
361 | RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27
362 | RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6
363 | RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
364 | RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
365 | RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
366 | RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C
367 | RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing
368 | RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1
369 | RMTJ60BD | Packing Units | Package 1 Weight | 0.101 kg
370 | RMTJ60BD | Packing Units | Package 1 Height | 0.270 dm
371 | RMTJ60BD | Packing Units | Package 1 width | 0.820 dm
372 | RMTJ60BD | Packing Units | Package 1 Length | 0.850 dm
373 | RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product
374 | RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration
375 | RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
376 | RMTJ60BD | Offer Sustainability | Mercury free | Yes
377 | RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes
378 | RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration
379 | RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
380 | RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information
381 | RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
382 | RMTJ60BD | Contractual warranty | Warranty | 18 months
383 | XVDLS37 | Main | range of product | Harmony XVD Optimum
384 | XVDLS37 | Main | product or component type | Complete miniature beacon
385 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
386 | XVDLS37 | Main | signalling type | Steady
387 | XVDLS37 | Main | mounting diameter | 45 mm
388 | XVDLS37 | Main | component name | XVDLS
389 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
390 | XVDLS37 | Main | light source | Bulb not included, clear
391 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base
392 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V
393 | XVDLS37 | Main | maximum power dissipation in W | 5 W
394 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
395 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7
396 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
397 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
398 | XVDLS37 | Complementary | CAD overall width | 45 mm
399 | XVDLS37 | Complementary | CAD overall height | 104 mm
400 | XVDLS37 | Complementary | CAD overall depth | 45 mm
401 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW
402 | XVDLS37 | Complementary | net weight | 0.08 kg
403 | XVDLS37 | Environment | product certifications | CSA UL
404 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1
405 | XVDLS37 | Environment | protective treatment | TC
406 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C
407 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C
408 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536
409 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529
410 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product
411 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration
412 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
413 | XVDLS37 | Offer Sustainability | Mercury free | Yes
414 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes
415 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
416 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
417 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
418 | XVDLS37 | Contractual warranty | Warranty | 18 months
419 | XVDLS38 | Main | range of product | Harmony XVD Optimum
420 | XVDLS38 | Main | product or component type | Complete miniature beacon
421 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit
422 | XVDLS38 | Main | signalling type | Steady
423 | XVDLS38 | Main | mounting diameter | 45 mm
424 | XVDLS38 | Main | component name | XVDLS
425 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
426 | XVDLS38 | Main | light source | Bulb not included, yellow
427 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base
428 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V
429 | XVDLS38 | Main | maximum power dissipation in W | 5 W
430 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
431 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7
432 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1
433 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1
434 | XVDLS38 | Complementary | CAD overall width | 45 mm
435 | XVDLS38 | Complementary | CAD overall height | 104 mm
436 | XVDLS38 | Complementary | CAD overall depth | 45 mm
437 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND
438 | XVDLS38 | Complementary | net weight | 0.08 kg
439 | XVDLS38 | Environment | product certifications | CSA UL
440 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1
441 | XVDLS38 | Environment | protective treatment | TC
442 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C
443 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C
444 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536
445 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529
446 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg
447 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product
448 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration
449 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
450 | XVDLS38 | Offer Sustainability | Mercury free | Yes
451 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes
452 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration
453 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
454 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
455 | XVDLS38 | Contractual warranty | Warranty | 18 months
456 | RHT428B | Main | range of product | Zelio Relay
457 | RHT428B | Main | product or component type | Plug-in relay Timing relay
458 | RHT428B | Main | device short name | RHT
459 | RHT428B | Main | contacts type and composition | 4 C/O
460 | RHT428B | Main | contact operation | Low level
461 | RHT428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz
462 | RHT428B | Main | time delay type | On-delay
463 | RHT428B | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s
464 | RHT428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C
465 | RHT428B | Main | status LED | With
466 | RHT428B | Main | control type | Selector switch
467 | RHT428B | Main | coil interference suppression | With
468 | RHT428B | Complementary | [Ui] rated insulation voltage | 250 V
469 | RHT428B | Complementary | operating position | Any position
470 | RHT428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V
471 | RHT428B | Complementary | contact bounce time | <= 10 ms
472 | RHT428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V
473 | RHT428B | Complementary | average resistance | 30 mOhm at 20 °C
474 | RHT428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
475 | RHT428B | Complementary | average coil consumption | 2.5 W at 20 °C
476 | RHT428B | Complementary | average coil consumption in VA | 2.9 at 20 °C
477 | RHT428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255
478 | RHT428B | Complementary | mechanical durability | 20000000 cycles
479 | RHT428B | Complementary | repeat accuracy | +/- 1 %
480 | RHT428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale
481 | RHT428B | Complementary | reset time | 100 ms
482 | RHT428B | Complementary | CAD overall width | 33 mm
483 | RHT428B | Complementary | CAD overall height | 43 mm
484 | RHT428B | Complementary | CAD overall depth | 108 mm
485 | RHT428B | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
486 | RHT428B | Complementary | net weight | 0.13 kg
487 | RHT428B | Environment | standards | IEC 60255 NF C 45-250 VDE 0435
488 | RHT428B | Environment | product certifications | USSR EDF ASE BV CSA
489 | RHT428B | Environment | protective treatment | TC
490 | RHT428B | Environment | dielectric strength | 2500 V
491 | RHT428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255
492 | RHT428B | Environment | ambient air temperature for storage | -40…70 °C
493 | RHT428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616
494 | RHT428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608
495 | RHT428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay
496 | RHT428B | Contractual warranty | Warranty | 18 months
497 | RSB2A080P7S | Main | range of product | Zelio Relay
498 | RSB2A080P7S | Main | series name | Interface relay
499 | RSB2A080P7S | Main | product or component type | Plug-in relay
500 | RSB2A080P7S | Main | device short name | RSB
501 | RSB2A080P7S | Main | contacts type and composition | 2 C/O
502 | RSB2A080P7S | Main | contact operation | Standard
503 | RSB2A080P7S | Main | [Uc] control circuit voltage | 230 V AC
504 | RSB2A080P7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C
505 | RSB2A080P7S | Main | status LED | Without
506 | RSB2A080P7S | Main | control type | Without push-button
507 | RSB2A080P7S | Complementary | shape of pin | Flat
508 | RSB2A080P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 %
509 | RSB2A080P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
510 | RSB2A080P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947
511 | RSB2A080P7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5
512 | RSB2A080P7S | Complementary | contacts material | Silver alloy (Ag/Ni)
513 | RSB2A080P7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
514 | RSB2A080P7S | Complementary | minimum switching current | 5 mA
515 | RSB2A080P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC
516 | RSB2A080P7S | Complementary | minimum switching voltage | 5 V
517 | RSB2A080P7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC
518 | RSB2A080P7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
519 | RSB2A080P7S | Complementary | minimum switching capacity | 300 mW at 5 mA
520 | RSB2A080P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
521 | RSB2A080P7S | Complementary | mechanical durability | 30000000 cycles
522 | RSB2A080P7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
523 | RSB2A080P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
524 | RSB2A080P7S | Complementary | marking | CE
525 | RSB2A080P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz
526 | RSB2A080P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC
527 | RSB2A080P7S | Complementary | safety reliability data | B10d = 100000
528 | RSB2A080P7S | Complementary | protection category | RT I
529 | RSB2A080P7S | Complementary | operating position | Any position
530 | RSB2A080P7S | Complementary | sale per indivisible quantity | 10
531 | RSB2A080P7S | Complementary | device presentation | Complete product
532 | RSB2A080P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
533 | RSB2A080P7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1
534 | RSB2A080P7S | Environment | product certifications | GOST CSA UL
535 | RSB2A080P7S | Environment | ambient air temperature for storage | -40…85 °C
536 | RSB2A080P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
537 | RSB2A080P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529
538 | RSB2A080P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
539 | RSB2A080P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC)
540 | RSB2A080P7S | Offer Sustainability | Sustainable offer status | Green Premium product
541 | RSB2A080P7S | Offer Sustainability | REACh free of SVHC | Yes
542 | RSB2A080P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
543 | RSB2A080P7S | Offer Sustainability | Toxic heavy metal free | Yes
544 | RSB2A080P7S | Offer Sustainability | Mercury free | Yes
545 | RSB2A080P7S | Offer Sustainability | RoHS exemption information | Yes
546 | RSB2A080P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration
547 | RSB2A080P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile
548 | RSB2A080P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
549 | RSB2A080P7S | Contractual warranty | Warranty | 18 months

## pivot_datasheet
Value
| Reference | RE22R2AMR | RE22R2CMR | RHT428B | RM17JC00MW | RM17TA00 | RM17TE00 | RMTJ60BD | RSB2A080P7S | XVDLS37 | XVDLS38
Section | Parameters
Complementary | CAD overall depth |  |  | 108 mm | [5 empty] | 45 mm | 45 mm
| CAD overall height |  |  | 43 mm | [5 empty] | 104 mm | 104 mm
| CAD overall width |  |  | 33 mm | [5 empty] | 45 mm | 45 mm
| Control signal pulse width | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms
| Power on delay | 100 ms | 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation | 120 ms on de-energisation
| Release input voltage | <= 2.4 V | <= 2.4 V
| [Ie] rated operational current | [7 empty] | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
| [Ue] rated operational voltage | [7 empty] | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
| [Ui] rated insulation voltage |  |  | 250 V | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 2 kV | 400 V conforming to EN/IEC 60947 | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1
| [Uimp] rated impulse withstand voltage | [7 empty] | 3.6 kV IEC 61000-4-5 | 4 kV IEC 60947-1 | 4 kV IEC 60947-1
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz |  | 24...240 V AC/DC 50/60 Hz +/- 10 % |  |  | 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | [6 empty] | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | [6 empty] | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold |  |  |  |  | 5...15 % of Un selected | 5...15 % of Un selected
| average coil consumption |  |  | 2.5 W at 20 °C |  |  |  |  | 0.75 VA AC 60 Hz
| average coil consumption in VA |  |  | 2.9 at 20 °C
| average coil resistance | [7 empty] | 38500 Ohm network: AC at 20 °C +/- 15 %
| average resistance |  |  | 30 mOhm at 20 °C
| cable entry | [8 empty] | 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7
| clamping connection capacity | [6 empty] | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | [6 empty] | Built-in, measurement: between 0 and 60 °C
| connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  |  | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time |  |  | <= 10 ms
| contacts material |  |  |  | Cadmium free |  |  |  | Silver alloy (Ag/Ni)
| contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency |  |  |  | 40...70 Hz sinusoidal | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 %
| control circuit voltage limits |  |  | 0.8...1.1 Uc conforming to IEC 60255 |  | - 12 % + 10 % Un | - 12 % + 10 % Un
| control type | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button
| creepage distance | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1
| current consumption | [6 empty] | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up |  |  |  | 0.5 s | 650 ms | 650 ms
| device presentation | [7 empty] | Complete product
| drop-out voltage threshold | [7 empty] | >= 0.15 Uc AC
| electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 |  | 100000 cycles | 100000 cycles | 100000 cycles |  | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
| fixing mode | [6 empty] | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing | Self-extinguishing |  | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic
| hysteresis |  |  |  | 15 % fixed of threshold setting | 2 % | 2 %
| immunity to microbreaks | 10 ms | 10 ms
| input current |  |  |  | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation |  |  |  | Between supply and measurement
| insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 |  | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
| local signalling |  |  |  | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green)power ON:
| marking |  |  |  | CE : 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE
| maximum measuring cycle |  |  |  | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value
| maximum power consumption in W |  |  |  | 1 W
| maximum switching capacity | [7 empty] | 2000 VA AC 224 W DC
| maximum switching current | 8 A | 8 A |  |  | 5 A AC 5 A DC | 5 A AC 5 A DC
| maximum switching voltage | 250 V AC | 250 V AC |  | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC |  | 300 V DC 400 V AC
| maximum voltage drop |  |  | <100 V for 3 A at 24 V
| measurement accuracy |  |  |  | +/- 10 % of the full scale value
| measurement error |  |  |  | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits |  |  |  |  | 183…528 V AC | 183…528 V AC
| mechanical durability | 10000000 cycles | 10000000 cycles | 20000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles |  | 30000000 cycles
| minimum switching capacity |  |  | 50 mVA at 1 mA, 1 V |  |  |  |  | 300 mW at 5 mA
| minimum switching current | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  | 10 mA at 5 V DC | 10 mA at 5 V DC |  | 5 mA
| minimum switching voltage | [7 empty] | 5 V
| mounting position | Any position | Any position
| mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 |  | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
| net weight | 0.105 kg | 0.105 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.12 kg |  | 0.08 kg | 0.08 kg
| nominal output current |  |  |  | 5 A | 5 A | 5 A
| operating position |  |  | Any position | Any position without derating | Any position without derating | Any position without derating |  | Any position
| operating rate |  |  |  | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load |  | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
| operating time | [7 empty] | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance |  |  |  | - 15 % + 10 % Un
| output contacts |  |  |  | 1 C/O | 1 C/O | 1 C/O
| overvoltage category | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1
| phase failure sensitivity |  |  |  |  | 0.7 Un | 0.7 Un
| polarity |  |  |  | Yes DC
| power consumption in VA | 3 VA at 240 V AC | 3 VA at 240 V AC |  |  | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz
| power consumption in W | 1.5 W at 240 V DC | 1.5 W at 240 V DC
| protection category | [7 empty] | RT I
| protection type | [6 empty] | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 1 % | +/- 0.5 % for input and measurement circuit | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
| reset time |  |  | 100 ms |  | 1500 ms time delay | 1500 ms time delay
| resistive rated load | [7 empty] | 8 A at 250 V AC 8 A at 28 V DC
| response time |  |  |  | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault)
| safety reliability data | B10d = 200000 MTTFd = 216.8 years | MTTFd = 251.1 years B10d = 230000 |  |  | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 | B10d = 45447 MTTFd = 49.2 years | B10d = 100000
| sale per indivisible quantity | [7 empty] | 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 15 % of full scale
| shape of pin | [7 empty] | Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
| supply frequency | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % |  |  | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 %
| supply voltage limits |  |  |  | 20.4…264 V AC/DC | 183…528 V AC | 183…528 V AC
| surge withstand | [6 empty] | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA | 2000 VA
| switching time |  |  | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | [6 empty] | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C | +/- 0.05 %/°C
| terminals description ISO n°1 |  |  | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | [5 empty] | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND
| threshold adjustment voltage |  |  |  |  | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting |  |  |  | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 |  | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m
| time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | Aw A | C
| utilisation category |  |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| voltage drift | +/- 0.2 %/V | +/- 0.2 %/V
| voltage range | 0.85...1.1 Us | 0.85...1.1 Us |  |  | 208...480 V phase to phase | 208...480 V phase to phase
| width | 22.5 mm | 22.5 mm |  | 17.5 mm | 17.5 mm | 17.5 mm
Contractual warranty | Warranty |  |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months
Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 |  | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP40 conforming to EN/IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529
| ambient air temperature for operation | -20…60 °C | -20…60 °C | -5…40 °C conforming to IEC 60255 | -20…50 °C | -20…50 °C | -20…50 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -40…70 °C (AC) -40…85 °C (DC) | -25…70 °C | -25…70 °C
| ambient air temperature for storage | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2500 V |  |  |  |  | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
| dielectric test voltage |  |  |  | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility |  |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
| disturbance radiated/conducted | [6 empty] | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | [8 empty] | Class II conforming to IEC 60536 | Class II conforming to IEC 60536
| electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 |  | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
| fire resistance | [6 empty] | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks |  |  | 10 ms during time delay 2 ms after time delay | 10 ms
| non-dissipating shock wave |  |  |  | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| pollution degree | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1
| product certifications | CE CCC GL China RoHS UL RCM EAC CSA | CSA CCC RCM China RoHS CE GL UL EAC | USSR EDF ASE BV CSA | GL C-Tick GOST UL CSA | GOST CSA GL C-Tick UL | GOST C-Tick CSA UL GL | CSA GL UL | GOST CSA UL | CSA UL | CSA UL
| protective treatment |  |  | TC | [5 empty] | TC | TC
| relative humidity | 95 % at 25…55 °C | 95 % at 25…55 °C |  | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30
| resistance to electrostatic discharge | [6 empty] | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | [6 empty] | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to NF C 20-608 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
| standards | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | IEC 60255 NF C 45-250 VDE 0435 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | IEC 60584-1 IEC 60947-1 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1
| vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
Main | [Ithe] conventional enclosed thermal current |  |  | 1 A 40 °C |  |  |  |  | 8 A at -40…40 °C
| [Uc] control circuit voltage |  |  | 24 V AC/DC 50/60 Hz |  |  |  |  | 230 V AC
| [Us] rated supply voltage | [8 empty] | <= 230 V | <= 230 V
| analogue input type | [6 empty] | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | [6 empty] | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | [8 empty] | Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit
| bulb type | [8 empty] | Incandescent with BA 15d base | Incandescent with BA 15d base
| coil interference suppression |  |  | With
| component name | [8 empty] | XVDLS | XVDLS
| contact operation |  |  | Low level |  |  |  |  | Standard
| contacts type and composition |  |  | 4 C/O |  |  |  |  | 2 C/O
| control type |  |  | Selector switch |  |  |  |  | Without push-button
| device short name | RE22 | RE22 | RHT |  |  |  |  | RSB
| discrete output type | Relay | Relay
| light source | [8 empty] | Bulb not included, clear | Bulb not included, yellow
| material | [8 empty] | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA |  |  |  | 3 VA
| maximum power dissipation in W | [8 empty] | 5 W | 5 W
| measurement range |  |  |  | 2...20 A current | 208...480 V voltage AC | 208...480 V voltage AC
| minimum switching current |  |  |  | 10 mA at 5 V DC
| mounting diameter | [8 empty] | 45 mm | 45 mm
| nominal output current | 8 A | 8 A
| product or component type | Modular timing relay | Modular timing relay | Plug-in relay Timing relay | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Converter for thermocouples | Plug-in relay | Complete miniature beacon | Complete miniature beacon
| product specific application |  |  |  |  | For 3-phase supply | For 3-phase supply
| range of product | Zelio Time | Zelio Time | Zelio Relay | Zelio Control | Zelio Control | Zelio Control | Zelio Analog | Zelio Relay | Harmony XVD Optimum | Harmony XVD Optimum
| relay monitored parameters |  |  |  | Overcurrent detection | Asymmetry Phase sequence Phase failure detection | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name |  |  |  | RM17JC | RM17TA | RM17TE
| relay type |  |  |  | Current control relay | Multifunction control relay | Multifunction control relay
| series name | [7 empty] | Interface relay
| signalling type | [8 empty] | Steady | Steady
| status LED |  |  | With |  |  |  |  | Without
| switching capacity in VA |  |  |  | 1250 VA | 1250 VA | 1250 VA
| time delay |  |  |  | Without | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range |  |  | 15...300 s 0.2...3 s 1.5...30 s
| time delay type |  |  | On-delay
| utilisation category |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
Offer Sustainability | China RoHS Regulation | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration
| Circularity Profile | End of Life Information | End of Life Information |  | End of Life Information | End of Life Information | End of Life Information | End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile
| Mercury free | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| REACh Regulation | REACh Declaration | REACh Declaration |  | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration |  | REACh Declaration | REACh Declaration
| REACh free of SVHC | [7 empty] | Yes
| RoHS exemption information | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes | Yes
| Sustainable offer status | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product
| Toxic heavy metal free | [7 empty] | Yes
| WEEE |  |  |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Height | [6 empty] | 0.270 dm
| Package 1 Length | [6 empty] | 0.850 dm
| Package 1 Weight | [6 empty] | 0.101 kg |  |  | 0.100 kg
| Package 1 width | [6 empty] | 0.820 dm

## pivot1_datasheet
Section | Parameters | Value
Complementary | CAD overall depth | 45 mm 45 mm 108 mm
| CAD overall height | 104 mm 104 mm 43 mm
| CAD overall width | 45 mm 45 mm 33 mm
| Control signal pulse width | 100 ms with load in parallel 30 ms 100 ms with load in parallel 30 ms
| Power on delay | 100 ms 100 ms
| Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 120 ms on de-energisation 120 ms on de-energisation
| Release input voltage | <= 2.4 V <= 2.4 V
| [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
| [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz
| [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 2 kV 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 250 V 400 V conforming to EN/IEC 60947
| [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 4 kV IEC 60947-1 3.6 kV IEC 61000-4-5
| [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % 24...240 V AC/DC 50/60 Hz 24...240 V AC/DC 50/60 Hz 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold | 5...15 % of Un selected 5...15 % of Un selected
| average coil consumption | 2.5 W at 20 °C 0.75 VA AC 60 Hz
| average coil consumption in VA | 2.9 at 20 °C
| average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 %
| average resistance | 30 mOhm at 20 °C
| cable entry | 1 entry tapped for Pg 7 1 entry tapped for Pg 7
| clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | Built-in, measurement: between 0 and 60 °C
| connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time | <= 10 ms
| contacts material | Cadmium free Silver alloy (Ag/Ni)
| contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency | 40...70 Hz sinusoidal 50...60 Hz +/- 10 % 50...60 Hz +/- 10 %
| control circuit voltage limits | - 12 % + 10 % Un - 12 % + 10 % Un 0.8...1.1 Uc conforming to IEC 60255
| control type | Rotary knob Diagnostic button Potentiometer external Rotary knob Diagnostic button
| creepage distance | 4 kV/3 conforming to IEC 60664-1 4 kV/3 conforming to IEC 60664-1
| current consumption | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up | 0.5 s 650 ms 650 ms
| device presentation | Complete product
| drop-out voltage threshold | >= 0.15 Uc AC
| electrical durability | 100000 cycles 100000 cycles 100000 cycles 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC
| fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing Self-extinguishing
| hysteresis | 15 % fixed of threshold setting 2 % 2 %
| immunity to microbreaks | 10 ms 10 ms
| input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | Between supply and measurement
| insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1
| local signalling | LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green)power ON:
| marking | CE : 73/23/EEC CE : EMC 89/336/EEC CE CE CE CE
| maximum measuring cycle | 30 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value
| maximum power consumption in W | 1 W
| maximum switching capacity | 2000 VA AC 224 W DC
| maximum switching current | 5 A AC 5 A DC 5 A AC 5 A DC 8 A 8 A
| maximum switching voltage | 250 V AC/DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 250 V AC 300 V DC 400 V AC
| maximum voltage drop | <100 V for 3 A at 24 V
| measurement accuracy | +/- 10 % of the full scale value
| measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | 183…528 V AC 183…528 V AC
| mechanical durability | 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 10000000 cycles 20000000 cycles 30000000 cycles
| minimum switching capacity | 50 mVA at 1 mA, 1 V 300 mW at 5 mA
| minimum switching current | 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 5 mA
| minimum switching voltage | 5 V
| mounting position | Any position Any position
| mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715
| net weight | 0.13 kg 0.13 kg 0.13 kg 0.105 kg 0.105 kg 0.12 kg 0.08 kg 0.08 kg 0.13 kg
| nominal output current | 5 A 5 A 5 A
| operating position | Any position without derating Any position without derating Any position without derating Any position Any position
| operating rate | <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 600 cycles/hour under load <= 72000 cycles/hour no-load
| operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | - 15 % + 10 % Un
| output contacts | 1 C/O 1 C/O 1 C/O
| overvoltage category | III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1
| phase failure sensitivity | 0.7 Un 0.7 Un
| polarity | Yes DC
| power consumption in VA | 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 3 VA at 240 V AC 3 VA at 240 V AC
| power consumption in W | 1.5 W at 240 V DC 1.5 W at 240 V DC
| protection category | RT I
| protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| repeat accuracy | +/- 0.5 % for input and measurement circuit 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay +/- 0.5 % conforming to IEC 61812-1 +/- 0.5 % conforming to IEC 61812-1 +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C +/- 1 %
| reset time | 1500 ms time delay 1500 ms time delay 100 ms
| resistive rated load | 8 A at 250 V AC 8 A at 28 V DC
| response time | < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault)
| safety reliability data | MTTFd = 502.2 years B10d = 470000 MTTFd = 502.2 years B10d = 470000 B10d = 200000 MTTFd = 216.8 years MTTFd = 251.1 years B10d = 230000 B10d = 45447 MTTFd = 49.2 years B10d = 100000
| sale per indivisible quantity | 10
| setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 15 % of full scale
| shape of pin | Flat
| status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
| supply frequency | 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50...60 Hz +/- 5 % 50...60 Hz +/- 5 %
| supply voltage limits | 20.4…264 V AC/DC 183…528 V AC 183…528 V AC
| surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2000 VA 2000 VA
| switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | 200 ppm/°C
| temperature drift | +/- 0.05 %/°C +/- 0.05 %/°C
| terminals description ISO n°1 | (GND)GROUND (COM-1)PW (COM-1)PW (GND)GROUND (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC
| threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting | 10...100 %
| tightening torque | 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1.1 N.m
| time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | Aw A C
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| voltage drift | +/- 0.2 %/V +/- 0.2 %/V
| voltage range | 208...480 V phase to phase 208...480 V phase to phase 0.85...1.1 Us 0.85...1.1 Us
| width | 17.5 mm 17.5 mm 17.5 mm 22.5 mm 22.5 mm
Contractual warranty | Warranty | 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months
Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP20 (terminal block) IP50 (housing) IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 IP40 conforming to EN/IEC 60529
| ambient air temperature for operation | -20…50 °C -20…50 °C -20…50 °C -20…60 °C -20…60 °C 0…50 °C mounting side by side 0…60 °C 2 cm spacing -25…70 °C -25…70 °C -5…40 °C conforming to IEC 60255 -40…70 °C (AC) -40…85 °C (DC)
| ambient air temperature for storage | -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C
| dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2500 V 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
| dielectric test voltage | 2 kV AC 50 Hz 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility
| disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | Class II conforming to IEC 60536 Class II conforming to IEC 60536
| electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11
| fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks | 10 ms 10 ms during time delay 2 ms after time delay
| non-dissipating shock wave | 4 kV 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| pollution degree | 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 2 conforming to IEC 60664-1
| product certifications | GL C-Tick GOST UL CSA GOST CSA GL C-Tick UL GOST C-Tick CSA UL GL CE CCC GL China RoHS UL RCM EAC CSA CSA CCC RCM China RoHS CE GL UL EAC CSA GL UL CSA UL CSA UL USSR EDF ASE BV CSA GOST CSA UL
| protective treatment | TC TC TC
| relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 25…55 °C 95 % at 25…55 °C
| resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to NF C 20-608 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
| standards | EN/IEC 60255-6 EN/IEC 60255-1 EN/IEC 60255-1 UL 508 IEC 61812-1 UL 508 IEC 61812-1 IEC 60584-1 IEC 60947-1 EN/IEC 60947-5-1 EN/IEC 60947-5-1 IEC 60255 NF C 45-250 VDE 0435 UL 508 CSA C22.2 No 14 EN/IEC 61810-1
| vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C 8 A at -40…40 °C
| [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz 230 V AC
| [Us] rated supply voltage | <= 230 V <= 230 V
| analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit
| bulb type | Incandescent with BA 15d base Incandescent with BA 15d base
| coil interference suppression | With
| component name | XVDLS XVDLS
| contact operation | Low level Standard
| contacts type and composition | 4 C/O 2 C/O
| control type | Selector switch Without push-button
| device short name | RE22 RE22 RHT RSB
| discrete output type | Relay Relay
| light source | Bulb not included, clear Bulb not included, yellow
| material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | 3 VA
| maximum power dissipation in W | 5 W 5 W
| measurement range | 2...20 A current 208...480 V voltage AC 208...480 V voltage AC
| minimum switching current | 10 mA at 5 V DC
| mounting diameter | 45 mm 45 mm
| nominal output current | 8 A 8 A
| product or component type | Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular timing relay Modular timing relay Converter for thermocouples Complete miniature beacon Complete miniature beacon Plug-in relay Timing relay Plug-in relay
| product specific application | For 3-phase supply For 3-phase supply
| range of product | Zelio Control Zelio Control Zelio Control Zelio Time Zelio Time Zelio Analog Harmony XVD Optimum Harmony XVD Optimum Zelio Relay Zelio Relay
| relay monitored parameters | Overcurrent detection Asymmetry Phase sequence Phase failure detection Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name | RM17JC RM17TA RM17TE
| relay type | Current control relay Multifunction control relay Multifunction control relay
| series name | Interface relay
| signalling type | Steady Steady
| status LED | With Without
| switching capacity in VA | 1250 VA 1250 VA 1250 VA
| time delay | Without Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range | 15...300 s 0.2...3 s 1.5...30 s
| time delay type | On-delay
| utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
Offer Sustainability | China RoHS Regulation | China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration
| Circularity Profile | End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information
| EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile
| Mercury free | Yes Yes Yes Yes Yes Yes Yes Yes Yes
| REACh Regulation | REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration
| REACh free of SVHC | Yes
| RoHS exemption information | Yes Yes Yes Yes Yes Yes Yes Yes Yes
| Sustainable offer status | Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product
| Toxic heavy metal free | Yes
| WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Height | 0.270 dm
| Package 1 Length | 0.850 dm
| Package 1 Weight | 0.101 kg 0.100 kg
| Package 1 width | 0.820 dm