## status
0 | RM17JC00MW | https://www.se.com/ww/en/product/RM17JC00MW/ | Found
1 | RM17TA00 | https://www.se.com/ww/en/product/RM17TA00/ | Found
2 | RM17TE00 | https://www.se.com/ww/en/product/RM17TE00/ | Found
3 | RM10TE00 | https://www.se.com/ww/en/product/RM10TE00/ | Not Found
4 | RM10TE00 | https://www.se.com/us/en/product/RM10TE00/ | Not Found
5 | RM10TE00 | https://www.se.com/in/en/product/RM10TE00/ | Found
6 | RE22R2AMR | https://www.se.com/ww/en/product/RE22R2AMR/ | Found
7 | RE22R2CMR | https://www.se.com/ww/en/product/RE22R2CMR/ | Found
8 | RMTJ60BD | https://www.se.com/ww/en/product/RMTJ60BD/ | Found
9 | XVDLS37 | https://www.se.com/ww/en/product/XVDLS37/ | Found
10 | XVDLS38 | https://www.se.com/ww/en/product/XVDLS38/ | Found
11 | RHT428B | https://www.se.com/ww/en/product/RHT428B/ | Found
12 | RHT418BE | https://www.se.com/ww/en/product/RHT418BE/ | Found
13 | RSB1A160M7S | https://www.se.com/ww/en/product/RSB1A160M7S/ | Found
14 | RSB1A160NDS | https://www.se.com/ww/en/product/RSB1A160NDS/ | Found
15 | RSB2A080P7S | https://www.se.com/ww/en/product/RSB2A080P7S/ | Found
16 | RSB2A080RDS | https://www.se.com/ww/en/product/RSB2A080RDS/ | Found
17 | RSB2A080U7S | https://www.se.com/ww/en/product/RSB2A080U7S/ | Found
18 | RSB2A080M7S | https://www.se.com/ww/en/product/RSB2A080M7S/ | Found
19 | RXG11RD | https://www.se.com/ww/en/product/RXG11RD/ | Found
20 | RXM2AB1B7 | https://www.se.com/ww/en/product/RXM2AB1B7/ | Found
21 | RXM4AB1B7 | https://www.se.com/ww/en/product/RXM4AB1B7/ | Found

## raw_datasheet
| Reference | Section | Parameters | Value | Temp_Parameters | Param_ID
0 | RM17JC00MW | Main | range of product | Zelio Control | _79.0 | RM17JC00MW_79.0
1 | RM17JC00MW | Main | product or component type | Modular measurement and control relays | _0.0 | RM17JC00MW_0.0
2 | RM17JC00MW | Main | relay type | Current control relay | _80.0 | RM17JC00MW_80.0
3 | RM17JC00MW | Main | relay name | RM17JC | _72.0 | RM17JC00MW_72.0
4 | RM17JC00MW | Main | relay monitored parameters | Overcurrent detection | _81.0 | RM17JC00MW_81.0
5 | RM17JC00MW | Main | time delay | Without | _96.0 | RM17JC00MW_96.0
6 | RM17JC00MW | Main | switching capacity in VA | 1250 VA | _59.0 | RM17JC00MW_59.0
7 | RM17JC00MW | Main | minimum switching current | 10 mA at 5 V DC | _88.0 | RM17JC00MW_88.0
8 | RM17JC00MW | Main | maximum power consumption in VA | 3 VA | _67.0 | RM17JC00MW_67.0
9 | RM17JC00MW | Main | measurement range | 2...20 A current | _95.0 | RM17JC00MW_95.0
10 | RM17JC00MW | Main | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | _0.0 | RM17JC00MW_0.0
11 | RM17JC00MW | Complementary | maximum switching voltage | 250 V AC/DC | _87.0 | RM17JC00MW_87.0
12 | RM17JC00MW | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz +/- 10 % | _11.0 | RM17JC00MW_11.0
13 | RM17JC00MW | Complementary | supply voltage limits | 20.4…264 V AC/DC | _11.0 | RM17JC00MW_11.0
14 | RM17JC00MW | Complementary | operating voltage tolerance | - 15 % + 10 % Un | _0.0 | RM17JC00MW_0.0
15 | RM17JC00MW | Complementary | maximum power consumption in W | 1 W | _67.0 | RM17JC00MW_67.0
16 | RM17JC00MW | Complementary | control circuit frequency | 40...70 Hz sinusoidal | _25.0 | RM17JC00MW_25.0
17 | RM17JC00MW | Complementary | output contacts | 1 C/O | _0.0 | RM17JC00MW_0.0
18 | RM17JC00MW | Complementary | nominal output current | 5 A | _0.0 | RM17JC00MW_0.0
19 | RM17JC00MW | Complementary | maximum measuring cycle | 30 ms measurement cycle as true rms value | _58.0 | RM17JC00MW_58.0
20 | RM17JC00MW | Complementary | hysteresis | 15 % fixed of threshold setting | _24.0 | RM17JC00MW_24.0
21 | RM17JC00MW | Complementary | delay at power up | 0.5 s | _10.0 | RM17JC00MW_10.0
22 | RM17JC00MW | Complementary | measurement accuracy | +/- 10 % of the full scale value | _44.0 | RM17JC00MW_44.0
23 | RM17JC00MW | Complementary | repeat accuracy | +/- 0.5 % for input and measurement circuit | _46.0 | RM17JC00MW_46.0
24 | RM17JC00MW | Complementary | measurement error | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | _0.0 | RM17JC00MW_0.0
25 | RM17JC00MW | Complementary | response time | < 200 ms (in the event of a fault) | _35.0 | RM17JC00MW_35.0
26 | RM17JC00MW | Complementary | polarity | Yes DC | _64.0 | RM17JC00MW_64.0
27 | RM17JC00MW | Complementary | threshold setting | 10...100 % | _91.0 | RM17JC00MW_91.0
28 | RM17JC00MW | Complementary | input current | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | _0.0 | RM17JC00MW_0.0
29 | RM17JC00MW | Complementary | marking | CE : 73/23/EEC CE : EMC 89/336/EEC | _31.0 | RM17JC00MW_31.0
30 | RM17JC00MW | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RM17JC00MW_55.0
31 | RM17JC00MW | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RM17JC00MW_4.0
32 | RM17JC00MW | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | _8.0 | RM17JC00MW_8.0
33 | RM17JC00MW | Complementary | insulation | Between supply and measurement | _8.0 | RM17JC00MW_8.0
34 | RM17JC00MW | Complementary | operating position | Any position without derating | _50.0 | RM17JC00MW_50.0
35 | RM17JC00MW | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RM17JC00MW_17.0
36 | RM17JC00MW | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RM17JC00MW_42.0
37 | RM17JC00MW | Complementary | housing material | Self-extinguishing plastic | _0.0 | RM17JC00MW_0.0
38 | RM17JC00MW | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | _30.0 | RM17JC00MW_30.0
39 | RM17JC00MW | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | _51.0 | RM17JC00MW_51.0
40 | RM17JC00MW | Complementary | electrical durability | 100000 cycles | _6.0 | RM17JC00MW_6.0
41 | RM17JC00MW | Complementary | mechanical durability | 30000000 cycles | _9.0 | RM17JC00MW_9.0
42 | RM17JC00MW | Complementary | operating rate | <= 360 operations/hour full load | _0.0 | RM17JC00MW_0.0
43 | RM17JC00MW | Complementary | contacts material | Cadmium free | _18.0 | RM17JC00MW_18.0
44 | RM17JC00MW | Complementary | width | 17.5 mm | _3.0 | RM17JC00MW_3.0
45 | RM17JC00MW | Complementary | net weight | 0.13 kg | _298.0 | RM17JC00MW_298.0
46 | RM17JC00MW | Environment | immunity to microbreaks | 10 ms | _5.0 | RM17JC00MW_5.0
47 | RM17JC00MW | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | _23.0 | RM17JC00MW_23.0
48 | RM17JC00MW | Environment | standards | EN/IEC 60255-6 | _21.0 | RM17JC00MW_21.0
49 | RM17JC00MW | Environment | product certifications | GL C-Tick GOST UL CSA | _32.0 | RM17JC00MW_32.0
50 | RM17JC00MW | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RM17JC00MW_13.0
51 | RM17JC00MW | Environment | ambient air temperature for operation | -20…50 °C | _12.0 | RM17JC00MW_12.0
52 | RM17JC00MW | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | _33.0 | RM17JC00MW_33.0
53 | RM17JC00MW | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | _43.0 | RM17JC00MW_43.0
54 | RM17JC00MW | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | _37.0 | RM17JC00MW_37.0
55 | RM17JC00MW | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | _29.0 | RM17JC00MW_29.0
56 | RM17JC00MW | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RM17JC00MW_40.0
57 | RM17JC00MW | Environment | dielectric test voltage | 2 kV AC 50 Hz | _20.0 | RM17JC00MW_20.0
58 | RM17JC00MW | Environment | non-dissipating shock wave | 4 kV | _7.0 | RM17JC00MW_7.0
59 | RM17JC00MW | Packing Units | Package 1 Weight | 120 g | _298.0 | RM17JC00MW_298.0
60 | RM17JC00MW | Packing Units | Package 2 Weight | 4.295 kg | _299.0 | RM17JC00MW_299.0
61 | RM17JC00MW | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RM17JC00MW_295.0
62 | RM17JC00MW | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RM17JC00MW_292.0
63 | RM17JC00MW | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RM17JC00MW_21.0
64 | RM17JC00MW | Offer Sustainability | Mercury free | Yes | _291.0 | RM17JC00MW_291.0
65 | RM17JC00MW | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RM17JC00MW_294.0
66 | RM17JC00MW | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RM17JC00MW_288.0
67 | RM17JC00MW | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RM17JC00MW_290.0
68 | RM17JC00MW | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RM17JC00MW_289.0
69 | RM17JC00MW | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RM17JC00MW_297.0
70 | RM17JC00MW | Contractual warranty | Warranty | 18 months | _287.0 | RM17JC00MW_287.0
71 | RM17TA00 | Main | range of product | Zelio Control | _79.0 | RM17TA00_79.0
72 | RM17TA00 | Main | product or component type | Modular measurement and control relays | _0.0 | RM17TA00_0.0
73 | RM17TA00 | Main | relay type | Multifunction control relay | _80.0 | RM17TA00_80.0
74 | RM17TA00 | Main | product specific application | For 3-phase supply | _0.0 | RM17TA00_0.0
75 | RM17TA00 | Main | relay name | RM17TA | _72.0 | RM17TA00_72.0
76 | RM17TA00 | Main | relay monitored parameters | Asymmetry Phase sequence Phase failure detection | _81.0 | RM17TA00_81.0
77 | RM17TA00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | _96.0 | RM17TA00_96.0
78 | RM17TA00 | Main | switching capacity in VA | 1250 VA | _59.0 | RM17TA00_59.0
79 | RM17TA00 | Main | measurement range | 208...480 V voltage AC | _95.0 | RM17TA00_95.0
80 | RM17TA00 | Complementary | reset time | 1500 ms time delay | _34.0 | RM17TA00_34.0
81 | RM17TA00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | _87.0 | RM17TA00_87.0
82 | RM17TA00 | Complementary | minimum switching current | 10 mA at 5 V DC | _88.0 | RM17TA00_88.0
83 | RM17TA00 | Complementary | maximum switching current | 5 A AC 5 A DC | _86.0 | RM17TA00_86.0
84 | RM17TA00 | Complementary | supply voltage limits | 183…528 V AC | _11.0 | RM17TA00_11.0
85 | RM17TA00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | _0.0 | RM17TA00_0.0
86 | RM17TA00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | _67.0 | RM17TA00_67.0
87 | RM17TA00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | _25.0 | RM17TA00_25.0
88 | RM17TA00 | Complementary | output contacts | 1 C/O | _0.0 | RM17TA00_0.0
89 | RM17TA00 | Complementary | nominal output current | 5 A | _0.0 | RM17TA00_0.0
90 | RM17TA00 | Complementary | measurement voltage limits | 183…528 V AC | _0.0 | RM17TA00_0.0
91 | RM17TA00 | Complementary | hysteresis | 2 % | _24.0 | RM17TA00_24.0
92 | RM17TA00 | Complementary | delay at power up | 650 ms | _10.0 | RM17TA00_10.0
93 | RM17TA00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | _58.0 | RM17TA00_58.0
94 | RM17TA00 | Complementary | threshold adjustment voltage | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | _91.0 | RM17TA00_91.0
95 | RM17TA00 | Complementary | voltage range | 208...480 V phase to phase | _78.0 | RM17TA00_78.0
96 | RM17TA00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | _0.0 | RM17TA00_0.0
97 | RM17TA00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | _46.0 | RM17TA00_46.0
98 | RM17TA00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | _0.0 | RM17TA00_0.0
99 | RM17TA00 | Complementary | phase failure sensitivity | 0.7 Un | _0.0 | RM17TA00_0.0
100 | RM17TA00 | Complementary | response time | < 200 ms (in the event of a fault) | _35.0 | RM17TA00_35.0
101 | RM17TA00 | Complementary | marking | CE | _31.0 | RM17TA00_31.0
102 | RM17TA00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RM17TA00_55.0
103 | RM17TA00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RM17TA00_4.0
104 | RM17TA00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | _8.0 | RM17TA00_8.0
105 | RM17TA00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | _38.0 | RM17TA00_38.0
106 | RM17TA00 | Complementary | operating position | Any position without derating | _50.0 | RM17TA00_50.0
107 | RM17TA00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RM17TA00_17.0
108 | RM17TA00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RM17TA00_42.0
109 | RM17TA00 | Complementary | housing material | Self-extinguishing plastic | _0.0 | RM17TA00_0.0
110 | RM17TA00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | _30.0 | RM17TA00_30.0
111 | RM17TA00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | _51.0 | RM17TA00_51.0
112 | RM17TA00 | Complementary | electrical durability | 100000 cycles | _6.0 | RM17TA00_6.0
113 | RM17TA00 | Complementary | mechanical durability | 30000000 cycles | _9.0 | RM17TA00_9.0
114 | RM17TA00 | Complementary | operating rate | <= 360 operations/hour full load | _0.0 | RM17TA00_0.0
115 | RM17TA00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | _0.0 | RM17TA00_0.0
116 | RM17TA00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | _48.0 | RM17TA00_48.0
117 | RM17TA00 | Complementary | width | 17.5 mm | _3.0 | RM17TA00_3.0
118 | RM17TA00 | Complementary | net weight | 0.13 kg | _298.0 | RM17TA00_298.0
119 | RM17TA00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | _23.0 | RM17TA00_23.0
120 | RM17TA00 | Environment | standards | EN/IEC 60255-1 | _21.0 | RM17TA00_21.0
121 | RM17TA00 | Environment | product certifications | GOST CSA GL C-Tick UL | _32.0 | RM17TA00_32.0
122 | RM17TA00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | _21.0 | RM17TA00_21.0
123 | RM17TA00 | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RM17TA00_13.0
124 | RM17TA00 | Environment | ambient air temperature for operation | -20…50 °C | _12.0 | RM17TA00_12.0
125 | RM17TA00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | _33.0 | RM17TA00_33.0
126 | RM17TA00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | _43.0 | RM17TA00_43.0
127 | RM17TA00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | _37.0 | RM17TA00_37.0
128 | RM17TA00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | _29.0 | RM17TA00_29.0
129 | RM17TA00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RM17TA00_40.0
130 | RM17TA00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | _20.0 | RM17TA00_20.0
131 | RM17TA00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | _7.0 | RM17TA00_7.0
132 | RM17TA00 | Packing Units | Package 1 Weight | 89 g | _298.0 | RM17TA00_298.0
133 | RM17TA00 | Packing Units | Package 2 Weight | 4.685 kg | _299.0 | RM17TA00_299.0
134 | RM17TA00 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RM17TA00_295.0
135 | RM17TA00 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RM17TA00_292.0
136 | RM17TA00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RM17TA00_21.0
137 | RM17TA00 | Offer Sustainability | Mercury free | Yes | _291.0 | RM17TA00_291.0
138 | RM17TA00 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RM17TA00_294.0
139 | RM17TA00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RM17TA00_288.0
140 | RM17TA00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RM17TA00_290.0
141 | RM17TA00 | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RM17TA00_289.0
142 | RM17TA00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RM17TA00_297.0
143 | RM17TA00 | Contractual warranty | Warranty | 18 months | _287.0 | RM17TA00_287.0
144 | RM17TE00 | Main | range of product | Zelio Control | _79.0 | RM17TE00_79.0
145 | RM17TE00 | Main | product or component type | Modular measurement and control relays | _0.0 | RM17TE00_0.0
146 | RM17TE00 | Main | relay type | Multifunction control relay | _80.0 | RM17TE00_80.0
147 | RM17TE00 | Main | product specific application | For 3-phase supply | _0.0 | RM17TE00_0.0
148 | RM17TE00 | Main | relay name | RM17TE | _72.0 | RM17TE00_72.0
149 | RM17TE00 | Main | relay monitored parameters | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection | _81.0 | RM17TE00_81.0
150 | RM17TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | _96.0 | RM17TE00_96.0
151 | RM17TE00 | Main | switching capacity in VA | 1250 VA | _59.0 | RM17TE00_59.0
152 | RM17TE00 | Main | measurement range | 208...480 V voltage AC | _95.0 | RM17TE00_95.0
153 | RM17TE00 | Complementary | reset time | 1500 ms time delay | _34.0 | RM17TE00_34.0
154 | RM17TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | _87.0 | RM17TE00_87.0
155 | RM17TE00 | Complementary | minimum switching current | 10 mA at 5 V DC | _88.0 | RM17TE00_88.0
156 | RM17TE00 | Complementary | maximum switching current | 5 A AC 5 A DC | _86.0 | RM17TE00_86.0
157 | RM17TE00 | Complementary | supply voltage limits | 183…528 V AC | _11.0 | RM17TE00_11.0
158 | RM17TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | _0.0 | RM17TE00_0.0
159 | RM17TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | _67.0 | RM17TE00_67.0
160 | RM17TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | _25.0 | RM17TE00_25.0
161 | RM17TE00 | Complementary | output contacts | 1 C/O | _0.0 | RM17TE00_0.0
162 | RM17TE00 | Complementary | nominal output current | 5 A | _0.0 | RM17TE00_0.0
163 | RM17TE00 | Complementary | measurement voltage limits | 183…528 V AC | _0.0 | RM17TE00_0.0
164 | RM17TE00 | Complementary | hysteresis | 2 % | _24.0 | RM17TE00_24.0
165 | RM17TE00 | Complementary | delay at power up | 650 ms | _10.0 | RM17TE00_10.0
166 | RM17TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | _58.0 | RM17TE00_58.0
167 | RM17TE00 | Complementary | threshold adjustment voltage | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected | _91.0 | RM17TE00_91.0
168 | RM17TE00 | Complementary | voltage range | 208...480 V phase to phase | _78.0 | RM17TE00_78.0
169 | RM17TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | _0.0 | RM17TE00_0.0
170 | RM17TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | _46.0 | RM17TE00_46.0
171 | RM17TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | _0.0 | RM17TE00_0.0
172 | RM17TE00 | Complementary | phase failure sensitivity | 0.7 Un | _0.0 | RM17TE00_0.0
173 | RM17TE00 | Complementary | response time | < 200 ms (in the event of a fault) | _35.0 | RM17TE00_35.0
174 | RM17TE00 | Complementary | marking | CE | _31.0 | RM17TE00_31.0
175 | RM17TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RM17TE00_55.0
176 | RM17TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RM17TE00_4.0
177 | RM17TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | _8.0 | RM17TE00_8.0
178 | RM17TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | _38.0 | RM17TE00_38.0
179 | RM17TE00 | Complementary | operating position | Any position without derating | _50.0 | RM17TE00_50.0
180 | RM17TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RM17TE00_17.0
181 | RM17TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RM17TE00_42.0
182 | RM17TE00 | Complementary | housing material | Self-extinguishing plastic | _0.0 | RM17TE00_0.0
183 | RM17TE00 | Complementary | local signalling | LED (green) for power ON LED (yellow) for relay ON | _30.0 | RM17TE00_30.0
184 | RM17TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | _51.0 | RM17TE00_51.0
185 | RM17TE00 | Complementary | electrical durability | 100000 cycles | _6.0 | RM17TE00_6.0
186 | RM17TE00 | Complementary | mechanical durability | 30000000 cycles | _9.0 | RM17TE00_9.0
187 | RM17TE00 | Complementary | operating rate | <= 360 operations/hour full load | _0.0 | RM17TE00_0.0
188 | RM17TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | _0.0 | RM17TE00_0.0
189 | RM17TE00 | Complementary | safety reliability data | MTTFd = 502.2 years B10d = 470000 | _48.0 | RM17TE00_48.0
190 | RM17TE00 | Complementary | width | 17.5 mm | _3.0 | RM17TE00_3.0
191 | RM17TE00 | Complementary | net weight | 0.13 kg | _298.0 | RM17TE00_298.0
192 | RM17TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | _23.0 | RM17TE00_23.0
193 | RM17TE00 | Environment | standards | EN/IEC 60255-1 | _21.0 | RM17TE00_21.0
194 | RM17TE00 | Environment | product certifications | GOST C-Tick CSA UL GL | _32.0 | RM17TE00_32.0
195 | RM17TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | _21.0 | RM17TE00_21.0
196 | RM17TE00 | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RM17TE00_13.0
197 | RM17TE00 | Environment | ambient air temperature for operation | -20…50 °C | _12.0 | RM17TE00_12.0
198 | RM17TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | _33.0 | RM17TE00_33.0
199 | RM17TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | _43.0 | RM17TE00_43.0
200 | RM17TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | _37.0 | RM17TE00_37.0
201 | RM17TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | _29.0 | RM17TE00_29.0
202 | RM17TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RM17TE00_40.0
203 | RM17TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | _20.0 | RM17TE00_20.0
204 | RM17TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | _7.0 | RM17TE00_7.0
205 | RM17TE00 | Packing Units | Package 1 Weight | 89 g | _298.0 | RM17TE00_298.0
206 | RM17TE00 | Packing Units | Package 2 Weight | 5.017 kg | _299.0 | RM17TE00_299.0
207 | RM17TE00 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RM17TE00_295.0
208 | RM17TE00 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RM17TE00_292.0
209 | RM17TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RM17TE00_21.0
210 | RM17TE00 | Offer Sustainability | Mercury free | Yes | _291.0 | RM17TE00_291.0
211 | RM17TE00 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RM17TE00_294.0
212 | RM17TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RM17TE00_288.0
213 | RM17TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RM17TE00_290.0
214 | RM17TE00 | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RM17TE00_289.0
215 | RM17TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RM17TE00_297.0
216 | RM17TE00 | Contractual warranty | Warranty | 18 months | _287.0 | RM17TE00_287.0
217 | RM10TE00 | Main | range of product | Zelio Control | _79.0 | RM10TE00_79.0
218 | RM10TE00 | Main | product or component type | Modular measurement and control relays | _0.0 | RM10TE00_0.0
219 | RM10TE00 | Main | relay type | Multifunction control relay | _80.0 | RM10TE00_80.0
220 | RM10TE00 | Main | product specific application | For 3-phase supply | _0.0 | RM10TE00_0.0
221 | RM10TE00 | Main | relay name | RM10TE | _72.0 | RM10TE00_72.0
222 | RM10TE00 | Main | relay monitored parameters | Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | _81.0 | RM10TE00_81.0
223 | RM10TE00 | Main | time delay | Adjustable 0.1...10 s, +/- 10 % of the full scale value | _96.0 | RM10TE00_96.0
224 | RM10TE00 | Main | switching capacity in VA | 1250 VA | _59.0 | RM10TE00_59.0
225 | RM10TE00 | Main | measurement range | 183...528 V AC | _95.0 | RM10TE00_95.0
226 | RM10TE00 | Complementary | reset time | 1500 ms time delay | _34.0 | RM10TE00_34.0
227 | RM10TE00 | Complementary | maximum switching voltage | 250 V AC 250 V DC | _87.0 | RM10TE00_87.0
228 | RM10TE00 | Complementary | minimum switching current | 10 mA at 5 V DC | _88.0 | RM10TE00_88.0
229 | RM10TE00 | Complementary | maximum switching current | 5 A AC 5 A DC | _86.0 | RM10TE00_86.0
230 | RM10TE00 | Complementary | supply voltage limits | 183…528 V AC | _11.0 | RM10TE00_11.0
231 | RM10TE00 | Complementary | control circuit voltage limits | - 12 % + 10 % Un | _0.0 | RM10TE00_0.0
232 | RM10TE00 | Complementary | power consumption in VA | 0…22 VA at 400 V AC 50 Hz | _67.0 | RM10TE00_67.0
233 | RM10TE00 | Complementary | control circuit frequency | 50...60 Hz +/- 10 % | _25.0 | RM10TE00_25.0
234 | RM10TE00 | Complementary | output contacts | 1 C/O | _0.0 | RM10TE00_0.0
235 | RM10TE00 | Complementary | nominal output current | 5 A | _0.0 | RM10TE00_0.0
236 | RM10TE00 | Complementary | hysteresis | 2 % | _24.0 | RM10TE00_24.0
237 | RM10TE00 | Complementary | delay at power up | 650 ms | _10.0 | RM10TE00_10.0
238 | RM10TE00 | Complementary | maximum measuring cycle | 150 ms measurement cycle as true rms value | _58.0 | RM10TE00_58.0
239 | RM10TE00 | Complementary | threshold adjustment voltage | -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC | _91.0 | RM10TE00_91.0
240 | RM10TE00 | Complementary | voltage range | 208...480 V phase to phase | _78.0 | RM10TE00_78.0
241 | RM10TE00 | Complementary | adjustment of asymmetry threshold | 5...15 % of Un selected | _0.0 | RM10TE00_0.0
242 | RM10TE00 | Complementary | repeat accuracy | 0.5 % for input and measurement circuit 3 % for time delay | _46.0 | RM10TE00_46.0
243 | RM10TE00 | Complementary | measurement error | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | _0.0 | RM10TE00_0.0
244 | RM10TE00 | Complementary | phase failure sensitivity | 0.7 Un | _0.0 | RM10TE00_0.0
245 | RM10TE00 | Complementary | response time | < 200 ms (in the event of a fault) | _35.0 | RM10TE00_35.0
246 | RM10TE00 | Complementary | marking | CE | _31.0 | RM10TE00_31.0
247 | RM10TE00 | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RM10TE00_55.0
248 | RM10TE00 | Complementary | insulation resistance | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RM10TE00_4.0
249 | RM10TE00 | Complementary | [Ui] rated insulation voltage | 400 V conforming to IEC 60664-1 | _8.0 | RM10TE00_8.0
250 | RM10TE00 | Complementary | supply frequency | 50/60 Hz +/- 10 % | _38.0 | RM10TE00_38.0
251 | RM10TE00 | Complementary | operating position | Any position without derating | _50.0 | RM10TE00_50.0
252 | RM10TE00 | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RM10TE00_17.0
253 | RM10TE00 | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RM10TE00_42.0
254 | RM10TE00 | Complementary | housing material | Self-extinguishing plastic | _0.0 | RM10TE00_0.0
255 | RM10TE00 | Complementary | local signalling | LED (green)power ON: LED (yellow)relay ON: | _30.0 | RM10TE00_30.0
256 | RM10TE00 | Complementary | mounting support | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | _51.0 | RM10TE00_51.0
257 | RM10TE00 | Complementary | electrical durability | 100000 cycles | _6.0 | RM10TE00_6.0
258 | RM10TE00 | Complementary | mechanical durability | 30000000 cycles | _9.0 | RM10TE00_9.0
259 | RM10TE00 | Complementary | operating rate | <= 360 operations/hour full load | _0.0 | RM10TE00_0.0
260 | RM10TE00 | Complementary | utilisation category | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | _0.0 | RM10TE00_0.0
261 | RM10TE00 | Complementary | safety reliability data | B10d = 470000 MTTFd = 502.2 years | _48.0 | RM10TE00_48.0
262 | RM10TE00 | Complementary | width | 17.5 mm | _3.0 | RM10TE00_3.0
263 | RM10TE00 | Complementary | net weight | 0.13 kg | _298.0 | RM10TE00_298.0
264 | RM10TE00 | Environment | electromagnetic compatibility | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | _23.0 | RM10TE00_23.0
265 | RM10TE00 | Environment | standards | EN/IEC 60255-1 | _21.0 | RM10TE00_21.0
266 | RM10TE00 | Environment | product certifications | C-Tick UL GOST CSA GL | _32.0 | RM10TE00_32.0
267 | RM10TE00 | Environment | directives | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | _21.0 | RM10TE00_21.0
268 | RM10TE00 | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RM10TE00_13.0
269 | RM10TE00 | Environment | ambient air temperature for operation | -20…50 °C | _12.0 | RM10TE00_12.0
270 | RM10TE00 | Environment | relative humidity | 95 % at 55 °C conforming to IEC 60068-2-30 | _33.0 | RM10TE00_33.0
271 | RM10TE00 | Environment | vibration resistance | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | _43.0 | RM10TE00_43.0
272 | RM10TE00 | Environment | shock resistance | 15 gn for 11 ms conforming to IEC 60255-21-1 | _37.0 | RM10TE00_37.0
273 | RM10TE00 | Environment | IP degree of protection | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | _29.0 | RM10TE00_29.0
274 | RM10TE00 | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RM10TE00_40.0
275 | RM10TE00 | Environment | dielectric test voltage | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | _20.0 | RM10TE00_20.0
276 | RM10TE00 | Environment | non-dissipating shock wave | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | _7.0 | RM10TE00_7.0
277 | RM10TE00 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RM10TE00_295.0
278 | RM10TE00 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RM10TE00_292.0
279 | RM10TE00 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RM10TE00_21.0
280 | RM10TE00 | Offer Sustainability | Mercury free | Yes | _291.0 | RM10TE00_291.0
281 | RM10TE00 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RM10TE00_294.0
282 | RM10TE00 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RM10TE00_288.0
283 | RM10TE00 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RM10TE00_290.0
284 | RM10TE00 | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RM10TE00_289.0
285 | RM10TE00 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RM10TE00_297.0
286 | RE22R2AMR | Main | range of product | Zelio Time | _79.0 | RE22R2AMR_79.0
287 | RE22R2AMR | Main | product or component type | Modular timing relay | _0.0 | RE22R2AMR_0.0
288 | RE22R2AMR | Main | discrete output type | Relay | _0.0 | RE22R2AMR_0.0
289 | RE22R2AMR | Main | device short name | RE22 | _72.0 | RE22R2AMR_72.0
290 | RE22R2AMR | Main | nominal output current | 8 A | _0.0 | RE22R2AMR_0.0
291 | RE22R2AMR | Complementary | contacts type and composition | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | _18.0 | RE22R2AMR_18.0
292 | RE22R2AMR | Complementary | time delay type | Aw A | _68.0 | RE22R2AMR_68.0
293 | RE22R2AMR | Complementary | time delay range | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | _96.0 | RE22R2AMR_96.0
294 | RE22R2AMR | Complementary | control type | Rotary knob Diagnostic button Potentiometer external | _0.0 | RE22R2AMR_0.0
295 | RE22R2AMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | _11.0 | RE22R2AMR_11.0
296 | RE22R2AMR | Complementary | Release input voltage | <= 2.4 V | _65.0 | RE22R2AMR_65.0
297 | RE22R2AMR | Complementary | voltage range | 0.85...1.1 Us | _78.0 | RE22R2AMR_78.0
298 | RE22R2AMR | Complementary | supply frequency | 50...60 Hz +/- 5 % | _38.0 | RE22R2AMR_38.0
299 | RE22R2AMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RE22R2AMR_17.0
300 | RE22R2AMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RE22R2AMR_42.0
301 | RE22R2AMR | Complementary | housing material | Self-extinguishing | _0.0 | RE22R2AMR_0.0
302 | RE22R2AMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | _46.0 | RE22R2AMR_46.0
303 | RE22R2AMR | Complementary | temperature drift | +/- 0.05 %/°C | _90.0 | RE22R2AMR_90.0
304 | RE22R2AMR | Complementary | voltage drift | +/- 0.2 %/V | _71.0 | RE22R2AMR_71.0
305 | RE22R2AMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | _45.0 | RE22R2AMR_45.0
306 | RE22R2AMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms | _82.0 | RE22R2AMR_82.0
307 | RE22R2AMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RE22R2AMR_4.0
308 | RE22R2AMR | Complementary | Recovery time | 120 ms on de-energisation | _35.0 | RE22R2AMR_35.0
309 | RE22R2AMR | Complementary | immunity to microbreaks | 10 ms | _5.0 | RE22R2AMR_5.0
310 | RE22R2AMR | Complementary | power consumption in VA | 3 VA at 240 V AC | _67.0 | RE22R2AMR_67.0
311 | RE22R2AMR | Complementary | power consumption in W | 1.5 W at 240 V DC | _67.0 | RE22R2AMR_67.0
312 | RE22R2AMR | Complementary | switching capacity in VA | 2000 VA | _59.0 | RE22R2AMR_59.0
313 | RE22R2AMR | Complementary | minimum switching current | 10 mA at 5 V DC | _88.0 | RE22R2AMR_88.0
314 | RE22R2AMR | Complementary | maximum switching current | 8 A | _86.0 | RE22R2AMR_86.0
315 | RE22R2AMR | Complementary | maximum switching voltage | 250 V AC | _87.0 | RE22R2AMR_87.0
316 | RE22R2AMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | _6.0 | RE22R2AMR_6.0
317 | RE22R2AMR | Complementary | mechanical durability | 10000000 cycles | _9.0 | RE22R2AMR_9.0
318 | RE22R2AMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | _7.0 | RE22R2AMR_7.0
319 | RE22R2AMR | Complementary | Power on delay | 100 ms | _10.0 | RE22R2AMR_10.0
320 | RE22R2AMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1 | _0.0 | RE22R2AMR_0.0
321 | RE22R2AMR | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RE22R2AMR_55.0
322 | RE22R2AMR | Complementary | safety reliability data | B10d = 200000 MTTFd = 216.8 years | _48.0 | RE22R2AMR_48.0
323 | RE22R2AMR | Complementary | mounting position | Any position | _50.0 | RE22R2AMR_50.0
324 | RE22R2AMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | _51.0 | RE22R2AMR_51.0
325 | RE22R2AMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | _30.0 | RE22R2AMR_30.0
326 | RE22R2AMR | Complementary | width | 22.5 mm | _3.0 | RE22R2AMR_3.0
327 | RE22R2AMR | Complementary | net weight | 0.105 kg | _298.0 | RE22R2AMR_298.0
328 | RE22R2AMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | _20.0 | RE22R2AMR_20.0
329 | RE22R2AMR | Environment | standards | UL 508 IEC 61812-1 | _21.0 | RE22R2AMR_21.0
330 | RE22R2AMR | Environment | directives | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | _21.0 | RE22R2AMR_21.0
331 | RE22R2AMR | Environment | product certifications | CE CCC GL China RoHS UL RCM EAC CSA | _32.0 | RE22R2AMR_32.0
332 | RE22R2AMR | Environment | ambient air temperature for operation | -20…60 °C | _12.0 | RE22R2AMR_12.0
333 | RE22R2AMR | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RE22R2AMR_13.0
334 | RE22R2AMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | _29.0 | RE22R2AMR_29.0
335 | RE22R2AMR | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RE22R2AMR_40.0
336 | RE22R2AMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | _43.0 | RE22R2AMR_43.0
337 | RE22R2AMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | _37.0 | RE22R2AMR_37.0
338 | RE22R2AMR | Environment | relative humidity | 95 % at 25…55 °C | _33.0 | RE22R2AMR_33.0
339 | RE22R2AMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | _23.0 | RE22R2AMR_23.0
340 | RE22R2AMR | Packing Units | Package 1 Weight | 0.114 kg | _298.0 | RE22R2AMR_298.0
341 | RE22R2AMR | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RE22R2AMR_295.0
342 | RE22R2AMR | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RE22R2AMR_292.0
343 | RE22R2AMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RE22R2AMR_21.0
344 | RE22R2AMR | Offer Sustainability | Mercury free | Yes | _291.0 | RE22R2AMR_291.0
345 | RE22R2AMR | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RE22R2AMR_294.0
346 | RE22R2AMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RE22R2AMR_288.0
347 | RE22R2AMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RE22R2AMR_290.0
348 | RE22R2AMR | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RE22R2AMR_289.0
349 | RE22R2CMR | Main | range of product | Zelio Time | _79.0 | RE22R2CMR_79.0
350 | RE22R2CMR | Main | product or component type | Modular timing relay | _0.0 | RE22R2CMR_0.0
351 | RE22R2CMR | Main | discrete output type | Relay | _0.0 | RE22R2CMR_0.0
352 | RE22R2CMR | Main | device short name | RE22 | _72.0 | RE22R2CMR_72.0
353 | RE22R2CMR | Main | nominal output current | 8 A | _0.0 | RE22R2CMR_0.0
354 | RE22R2CMR | Complementary | contacts type and composition | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | _18.0 | RE22R2CMR_18.0
355 | RE22R2CMR | Complementary | time delay type | C | _68.0 | RE22R2CMR_68.0
356 | RE22R2CMR | Complementary | time delay range | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | _96.0 | RE22R2CMR_96.0
357 | RE22R2CMR | Complementary | control type | Rotary knob Diagnostic button | _0.0 | RE22R2CMR_0.0
358 | RE22R2CMR | Complementary | [Us] rated supply voltage | 24...240 V AC/DC 50/60 Hz | _11.0 | RE22R2CMR_11.0
359 | RE22R2CMR | Complementary | Release input voltage | <= 2.4 V | _65.0 | RE22R2CMR_65.0
360 | RE22R2CMR | Complementary | voltage range | 0.85...1.1 Us | _78.0 | RE22R2CMR_78.0
361 | RE22R2CMR | Complementary | supply frequency | 50...60 Hz +/- 5 % | _38.0 | RE22R2CMR_38.0
362 | RE22R2CMR | Complementary | connections - terminals | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | _17.0 | RE22R2CMR_17.0
363 | RE22R2CMR | Complementary | tightening torque | 0.6…1 N.m conforming to IEC 60947-1 | _42.0 | RE22R2CMR_42.0
364 | RE22R2CMR | Complementary | housing material | Self-extinguishing | _0.0 | RE22R2CMR_0.0
365 | RE22R2CMR | Complementary | repeat accuracy | +/- 0.5 % conforming to IEC 61812-1 | _46.0 | RE22R2CMR_46.0
366 | RE22R2CMR | Complementary | temperature drift | +/- 0.05 %/°C | _90.0 | RE22R2CMR_90.0
367 | RE22R2CMR | Complementary | voltage drift | +/- 0.2 %/V | _71.0 | RE22R2CMR_71.0
368 | RE22R2CMR | Complementary | setting accuracy of time delay | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | _45.0 | RE22R2CMR_45.0
369 | RE22R2CMR | Complementary | Control signal pulse width | 100 ms with load in parallel 30 ms | _82.0 | RE22R2CMR_82.0
370 | RE22R2CMR | Complementary | insulation resistance | 100 MOhm at 500 V DC conforming to IEC 60664-1 | _4.0 | RE22R2CMR_4.0
371 | RE22R2CMR | Complementary | Recovery time | 120 ms on de-energisation | _35.0 | RE22R2CMR_35.0
372 | RE22R2CMR | Complementary | immunity to microbreaks | 10 ms | _5.0 | RE22R2CMR_5.0
373 | RE22R2CMR | Complementary | power consumption in VA | 3 VA at 240 V AC | _67.0 | RE22R2CMR_67.0
374 | RE22R2CMR | Complementary | power consumption in W | 1.5 W at 240 V DC | _67.0 | RE22R2CMR_67.0
375 | RE22R2CMR | Complementary | switching capacity in VA | 2000 VA | _59.0 | RE22R2CMR_59.0
376 | RE22R2CMR | Complementary | minimum switching current | 10 mA at 5 V DC | _88.0 | RE22R2CMR_88.0
377 | RE22R2CMR | Complementary | maximum switching current | 8 A | _86.0 | RE22R2CMR_86.0
378 | RE22R2CMR | Complementary | maximum switching voltage | 250 V AC | _87.0 | RE22R2CMR_87.0
379 | RE22R2CMR | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | _6.0 | RE22R2CMR_6.0
380 | RE22R2CMR | Complementary | mechanical durability | 10000000 cycles | _9.0 | RE22R2CMR_9.0
381 | RE22R2CMR | Complementary | Rated impulse withstand voltage | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | _7.0 | RE22R2CMR_7.0
382 | RE22R2CMR | Complementary | Power on delay | 100 ms | _10.0 | RE22R2CMR_10.0
383 | RE22R2CMR | Complementary | creepage distance | 4 kV/3 conforming to IEC 60664-1 | _0.0 | RE22R2CMR_0.0
384 | RE22R2CMR | Complementary | overvoltage category | III conforming to IEC 60664-1 | _55.0 | RE22R2CMR_55.0
385 | RE22R2CMR | Complementary | safety reliability data | MTTFd = 251.1 years B10d = 230000 | _48.0 | RE22R2CMR_48.0
386 | RE22R2CMR | Complementary | mounting position | Any position | _50.0 | RE22R2CMR_50.0
387 | RE22R2CMR | Complementary | mounting support | 35 mm DIN rail conforming to EN/IEC 60715 | _51.0 | RE22R2CMR_51.0
388 | RE22R2CMR | Complementary | status LED | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | _30.0 | RE22R2CMR_30.0
389 | RE22R2CMR | Complementary | width | 22.5 mm | _3.0 | RE22R2CMR_3.0
390 | RE22R2CMR | Complementary | net weight | 0.105 kg | _298.0 | RE22R2CMR_298.0
391 | RE22R2CMR | Environment | dielectric strength | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | _20.0 | RE22R2CMR_20.0
392 | RE22R2CMR | Environment | standards | UL 508 IEC 61812-1 | _21.0 | RE22R2CMR_21.0
393 | RE22R2CMR | Environment | directives | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | _21.0 | RE22R2CMR_21.0
394 | RE22R2CMR | Environment | product certifications | CSA CCC RCM China RoHS CE GL UL EAC | _32.0 | RE22R2CMR_32.0
395 | RE22R2CMR | Environment | ambient air temperature for operation | -20…60 °C | _12.0 | RE22R2CMR_12.0
396 | RE22R2CMR | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RE22R2CMR_13.0
397 | RE22R2CMR | Environment | IP degree of protection | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | _29.0 | RE22R2CMR_29.0
398 | RE22R2CMR | Environment | pollution degree | 3 conforming to IEC 60664-1 | _40.0 | RE22R2CMR_40.0
399 | RE22R2CMR | Environment | vibration resistance | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | _43.0 | RE22R2CMR_43.0
400 | RE22R2CMR | Environment | shock resistance | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | _37.0 | RE22R2CMR_37.0
401 | RE22R2CMR | Environment | relative humidity | 95 % at 25…55 °C | _33.0 | RE22R2CMR_33.0
402 | RE22R2CMR | Environment | electromagnetic compatibility | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | _23.0 | RE22R2CMR_23.0
403 | RE22R2CMR | Packing Units | Package 1 Weight | 0.108 kg | _298.0 | RE22R2CMR_298.0
404 | RE22R2CMR | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RE22R2CMR_295.0
405 | RE22R2CMR | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RE22R2CMR_292.0
406 | RE22R2CMR | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RE22R2CMR_21.0
407 | RE22R2CMR | Offer Sustainability | Mercury free | Yes | _291.0 | RE22R2CMR_291.0
408 | RE22R2CMR | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RE22R2CMR_294.0
409 | RE22R2CMR | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RE22R2CMR_288.0
410 | RE22R2CMR | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RE22R2CMR_290.0
411 | RE22R2CMR | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RE22R2CMR_289.0
412 | RMTJ60BD | Main | range of product | Zelio Analog | _79.0 | RMTJ60BD_79.0
413 | RMTJ60BD | Main | product or component type | Converter for thermocouples | _0.0 | RMTJ60BD_0.0
414 | RMTJ60BD | Main | analogue input type | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | _0.0 | RMTJ60BD_0.0
415 | RMTJ60BD | Main | analogue output type | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | _0.0 | RMTJ60BD_0.0
416 | RMTJ60BD | Complementary | protection type | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | _57.0 | RMTJ60BD_57.0
417 | RMTJ60BD | Complementary | abnormal analogue output voltage | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | _0.0 | RMTJ60BD_0.0
418 | RMTJ60BD | Complementary | abnormal analogue output current | -30…0 mA when no input or input wire broken | _0.0 | RMTJ60BD_0.0
419 | RMTJ60BD | Complementary | [Us] rated supply voltage | 24 V DC +/- 20 %, non isolated | _11.0 | RMTJ60BD_11.0
420 | RMTJ60BD | Complementary | current consumption | <= 40 mA for voltage output <= 60 mA for current output | _67.0 | RMTJ60BD_67.0
421 | RMTJ60BD | Complementary | local signalling | LED (green) for power ON | _30.0 | RMTJ60BD_30.0
422 | RMTJ60BD | Complementary | measurement error | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | _0.0 | RMTJ60BD_0.0
423 | RMTJ60BD | Complementary | repeat accuracy | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C | _46.0 | RMTJ60BD_46.0
424 | RMTJ60BD | Complementary | temperature coefficient | 200 ppm/°C | _90.0 | RMTJ60BD_90.0
425 | RMTJ60BD | Complementary | cold junction compensation | Built-in, measurement: between 0 and 60 °C | _0.0 | RMTJ60BD_0.0
426 | RMTJ60BD | Complementary | clamping connection capacity | 2 x 1.5 mm² 1 x 2.5 mm² | _17.0 | RMTJ60BD_17.0
427 | RMTJ60BD | Complementary | tightening torque | 0.6…1.1 N.m | _42.0 | RMTJ60BD_42.0
428 | RMTJ60BD | Complementary | marking | CE | _31.0 | RMTJ60BD_31.0
429 | RMTJ60BD | Complementary | surge withstand | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | _23.0 | RMTJ60BD_23.0
430 | RMTJ60BD | Complementary | [Ui] rated insulation voltage | 2 kV | _8.0 | RMTJ60BD_8.0
431 | RMTJ60BD | Complementary | fixing mode | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | _51.0 | RMTJ60BD_51.0
432 | RMTJ60BD | Complementary | safety reliability data | B10d = 45447 MTTFd = 49.2 years | _48.0 | RMTJ60BD_48.0
433 | RMTJ60BD | Complementary | net weight | 0.12 kg | _298.0 | RMTJ60BD_298.0
434 | RMTJ60BD | Environment | standards | IEC 60584-1 IEC 60947-1 | _21.0 | RMTJ60BD_21.0
435 | RMTJ60BD | Environment | product certifications | CSA GL UL | _32.0 | RMTJ60BD_32.0
436 | RMTJ60BD | Environment | IP degree of protection | IP20 (terminal block) IP50 (housing) | _29.0 | RMTJ60BD_29.0
437 | RMTJ60BD | Environment | fire resistance | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | _0.0 | RMTJ60BD_0.0
438 | RMTJ60BD | Environment | shock resistance | 50 gn for 11 ms conforming to IEC 60068-2-27 | _37.0 | RMTJ60BD_37.0
439 | RMTJ60BD | Environment | vibration resistance | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | _43.0 | RMTJ60BD_43.0
440 | RMTJ60BD | Environment | resistance to electrostatic discharge | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | _23.0 | RMTJ60BD_23.0
441 | RMTJ60BD | Environment | resistance to fast transients | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | _23.0 | RMTJ60BD_23.0
442 | RMTJ60BD | Environment | disturbance radiated/conducted | CISPR 22 group 1 - class B CISPR 11 | _23.0 | RMTJ60BD_23.0
443 | RMTJ60BD | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RMTJ60BD_13.0
444 | RMTJ60BD | Environment | ambient air temperature for operation | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | _12.0 | RMTJ60BD_12.0
445 | RMTJ60BD | Environment | pollution degree | 2 conforming to IEC 60664-1 | _40.0 | RMTJ60BD_40.0
446 | RMTJ60BD | Packing Units | Package 1 Weight | 0.101 kg | _298.0 | RMTJ60BD_298.0
447 | RMTJ60BD | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RMTJ60BD_295.0
448 | RMTJ60BD | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RMTJ60BD_292.0
449 | RMTJ60BD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RMTJ60BD_21.0
450 | RMTJ60BD | Offer Sustainability | Mercury free | Yes | _291.0 | RMTJ60BD_291.0
451 | RMTJ60BD | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RMTJ60BD_294.0
452 | RMTJ60BD | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RMTJ60BD_288.0
453 | RMTJ60BD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RMTJ60BD_290.0
454 | RMTJ60BD | Offer Sustainability | Circularity Profile | End of Life Information | _289.0 | RMTJ60BD_289.0
455 | RMTJ60BD | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RMTJ60BD_297.0
456 | RMTJ60BD | Contractual warranty | Warranty | 18 months | _287.0 | RMTJ60BD_287.0
457 | XVDLS37 | Main | range of product | Harmony XVD Optimum | _79.0 | XVDLS37_79.0
458 | XVDLS37 | Main | product or component type | Complete miniature beacon | _0.0 | XVDLS37_0.0
459 | XVDLS37 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | _0.0 | XVDLS37_0.0
460 | XVDLS37 | Main | signalling type | Steady | _30.0 | XVDLS37_30.0
461 | XVDLS37 | Main | mounting diameter | 45 mm | _52.0 | XVDLS37_52.0
462 | XVDLS37 | Main | component name | XVDLS | _72.0 | XVDLS37_72.0
463 | XVDLS37 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | _0.0 | XVDLS37_0.0
464 | XVDLS37 | Main | light source | Bulb not included, clear | _0.0 | XVDLS37_0.0
465 | XVDLS37 | Main | bulb type | Incandescent with BA 15d base | _0.0 | XVDLS37_0.0
466 | XVDLS37 | Main | [Us] rated supply voltage | <= 230 V | _11.0 | XVDLS37_11.0
467 | XVDLS37 | Main | maximum power dissipation in W | 5 W | _67.0 | XVDLS37_67.0
468 | XVDLS37 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | _17.0 | XVDLS37_17.0
469 | XVDLS37 | Complementary | cable entry | 1 entry tapped for Pg 7 | _15.0 | XVDLS37_15.0
470 | XVDLS37 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | _8.0 | XVDLS37_8.0
471 | XVDLS37 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | _7.0 | XVDLS37_7.0
472 | XVDLS37 | Complementary | CAD overall width | 45 mm | _3.0 | XVDLS37_3.0
473 | XVDLS37 | Complementary | CAD overall height | 104 mm | _2.0 | XVDLS37_2.0
474 | XVDLS37 | Complementary | CAD overall depth | 45 mm | _1.0 | XVDLS37_1.0
475 | XVDLS37 | Complementary | terminals description ISO n°1 | (GND)GROUND (COM-1)PW | _0.0 | XVDLS37_0.0
476 | XVDLS37 | Complementary | net weight | 0.08 kg | _298.0 | XVDLS37_298.0
477 | XVDLS37 | Environment | product certifications | CSA UL | _32.0 | XVDLS37_32.0
478 | XVDLS37 | Environment | standards | EN/IEC 60947-5-1 | _21.0 | XVDLS37_21.0
479 | XVDLS37 | Environment | protective treatment | TC | _0.0 | XVDLS37_0.0
480 | XVDLS37 | Environment | ambient air temperature for operation | -25…70 °C | _12.0 | XVDLS37_12.0
481 | XVDLS37 | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | XVDLS37_13.0
482 | XVDLS37 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | _7.0 | XVDLS37_7.0
483 | XVDLS37 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | _29.0 | XVDLS37_29.0
484 | XVDLS37 | Packing Units | Package 1 Weight | 0.101 kg | _298.0 | XVDLS37_298.0
485 | XVDLS37 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | XVDLS37_295.0
486 | XVDLS37 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | XVDLS37_292.0
487 | XVDLS37 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | XVDLS37_21.0
488 | XVDLS37 | Offer Sustainability | Mercury free | Yes | _291.0 | XVDLS37_291.0
489 | XVDLS37 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | XVDLS37_294.0
490 | XVDLS37 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | XVDLS37_288.0
491 | XVDLS37 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | XVDLS37_290.0
492 | XVDLS37 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | XVDLS37_297.0
493 | XVDLS37 | Contractual warranty | Warranty | 18 months | _287.0 | XVDLS37_287.0
494 | XVDLS38 | Main | range of product | Harmony XVD Optimum | _79.0 | XVDLS38_79.0
495 | XVDLS38 | Main | product or component type | Complete miniature beacon | _0.0 | XVDLS38_0.0
496 | XVDLS38 | Main | beacon or indicator bank unit type | Base unit direct fixing Illuminated unit | _0.0 | XVDLS38_0.0
497 | XVDLS38 | Main | signalling type | Steady | _30.0 | XVDLS38_30.0
498 | XVDLS38 | Main | mounting diameter | 45 mm | _52.0 | XVDLS38_52.0
499 | XVDLS38 | Main | component name | XVDLS | _72.0 | XVDLS38_72.0
500 | XVDLS38 | Main | material | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | _0.0 | XVDLS38_0.0
501 | XVDLS38 | Main | light source | Bulb not included, yellow | _0.0 | XVDLS38_0.0
502 | XVDLS38 | Main | bulb type | Incandescent with BA 15d base | _0.0 | XVDLS38_0.0
503 | XVDLS38 | Main | [Us] rated supply voltage | <= 230 V | _11.0 | XVDLS38_11.0
504 | XVDLS38 | Main | maximum power dissipation in W | 5 W | _67.0 | XVDLS38_67.0
505 | XVDLS38 | Complementary | connections - terminals | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | _17.0 | XVDLS38_17.0
506 | XVDLS38 | Complementary | cable entry | 1 entry tapped for Pg 7 | _15.0 | XVDLS38_15.0
507 | XVDLS38 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 60947-1 | _8.0 | XVDLS38_8.0
508 | XVDLS38 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV IEC 60947-1 | _7.0 | XVDLS38_7.0
509 | XVDLS38 | Complementary | CAD overall width | 45 mm | _3.0 | XVDLS38_3.0
510 | XVDLS38 | Complementary | CAD overall height | 104 mm | _2.0 | XVDLS38_2.0
511 | XVDLS38 | Complementary | CAD overall depth | 45 mm | _1.0 | XVDLS38_1.0
512 | XVDLS38 | Complementary | terminals description ISO n°1 | (COM-1)PW (GND)GROUND | _0.0 | XVDLS38_0.0
513 | XVDLS38 | Complementary | net weight | 0.08 kg | _298.0 | XVDLS38_298.0
514 | XVDLS38 | Environment | product certifications | CSA UL | _32.0 | XVDLS38_32.0
515 | XVDLS38 | Environment | standards | EN/IEC 60947-5-1 | _21.0 | XVDLS38_21.0
516 | XVDLS38 | Environment | protective treatment | TC | _0.0 | XVDLS38_0.0
517 | XVDLS38 | Environment | ambient air temperature for operation | -25…70 °C | _12.0 | XVDLS38_12.0
518 | XVDLS38 | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | XVDLS38_13.0
519 | XVDLS38 | Environment | electrical shock protection class | Class II conforming to IEC 60536 | _7.0 | XVDLS38_7.0
520 | XVDLS38 | Environment | IP degree of protection | IP40 conforming to IEC 60529 | _29.0 | XVDLS38_29.0
521 | XVDLS38 | Packing Units | Package 1 Weight | 0.100 kg | _298.0 | XVDLS38_298.0
522 | XVDLS38 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | XVDLS38_295.0
523 | XVDLS38 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | XVDLS38_292.0
524 | XVDLS38 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | XVDLS38_21.0
525 | XVDLS38 | Offer Sustainability | Mercury free | Yes | _291.0 | XVDLS38_291.0
526 | XVDLS38 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | XVDLS38_294.0
527 | XVDLS38 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | XVDLS38_288.0
528 | XVDLS38 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | XVDLS38_290.0
529 | XVDLS38 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | XVDLS38_297.0
530 | XVDLS38 | Contractual warranty | Warranty | 18 months | _287.0 | XVDLS38_287.0
531 | RHT428B | Main | range of product | Zelio Relay | _79.0 | RHT428B_79.0
532 | RHT428B | Main | product or component type | Plug-in relay Timing relay | _0.0 | RHT428B_0.0
533 | RHT428B | Main | device short name | RHT | _72.0 | RHT428B_72.0
534 | RHT428B | Main | contacts type and composition | 4 C/O | _18.0 | RHT428B_18.0
535 | RHT428B | Main | contact operation | Low level | _0.0 | RHT428B_0.0
536 | RHT428B | Main | [Uc] control circuit voltage | 24 V AC/DC 50/60 Hz | _84.0 | RHT428B_84.0
537 | RHT428B | Main | time delay type | On-delay | _68.0 | RHT428B_68.0
538 | RHT428B | Main | time delay range | 15...300 s 0.2...3 s 1.5...30 s | _96.0 | RHT428B_96.0
539 | RHT428B | Main | [Ithe] conventional enclosed thermal current | 1 A 40 °C | _41.0 | RHT428B_41.0
540 | RHT428B | Main | status LED | With | _30.0 | RHT428B_30.0
541 | RHT428B | Main | control type | Selector switch | _0.0 | RHT428B_0.0
542 | RHT428B | Main | coil interference suppression | With | _0.0 | RHT428B_0.0
543 | RHT428B | Complementary | [Ui] rated insulation voltage | 250 V | _8.0 | RHT428B_8.0
544 | RHT428B | Complementary | operating position | Any position | _50.0 | RHT428B_50.0
545 | RHT428B | Complementary | minimum switching capacity | 50 mVA at 1 mA, 1 V | _60.0 | RHT428B_60.0
546 | RHT428B | Complementary | contact bounce time | <= 10 ms | _0.0 | RHT428B_0.0
547 | RHT428B | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | _93.0 | RHT428B_93.0
548 | RHT428B | Complementary | average resistance | 30 mOhm at 20 °C | _83.0 | RHT428B_83.0
549 | RHT428B | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | _35.0 | RHT428B_35.0
550 | RHT428B | Complementary | average coil consumption | 2.5 W at 20 °C | _85.0 | RHT428B_85.0
551 | RHT428B | Complementary | average coil consumption in VA | 2.9 at 20 °C | _85.0 | RHT428B_85.0
552 | RHT428B | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | _0.0 | RHT428B_0.0
553 | RHT428B | Complementary | mechanical durability | 20000000 cycles | _9.0 | RHT428B_9.0
554 | RHT428B | Complementary | repeat accuracy | +/- 1 % | _46.0 | RHT428B_46.0
555 | RHT428B | Complementary | setting accuracy of time delay | +/- 15 % of full scale | _45.0 | RHT428B_45.0
556 | RHT428B | Complementary | reset time | 100 ms | _34.0 | RHT428B_34.0
557 | RHT428B | Complementary | CAD overall width | 33 mm | _3.0 | RHT428B_3.0
558 | RHT428B | Complementary | CAD overall height | 43 mm | _2.0 | RHT428B_2.0
559 | RHT428B | Complementary | CAD overall depth | 108 mm | _1.0 | RHT428B_1.0
560 | RHT428B | Complementary | terminals description ISO n°1 | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | _0.0 | RHT428B_0.0
561 | RHT428B | Complementary | net weight | 0.13 kg | _298.0 | RHT428B_298.0
562 | RHT428B | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | _21.0 | RHT428B_21.0
563 | RHT428B | Environment | product certifications | USSR EDF ASE BV CSA | _32.0 | RHT428B_32.0
564 | RHT428B | Environment | protective treatment | TC | _0.0 | RHT428B_0.0
565 | RHT428B | Environment | dielectric strength | 2500 V | _20.0 | RHT428B_20.0
566 | RHT428B | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | _12.0 | RHT428B_12.0
567 | RHT428B | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RHT428B_13.0
568 | RHT428B | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | _43.0 | RHT428B_43.0
569 | RHT428B | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | _37.0 | RHT428B_37.0
570 | RHT428B | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | _5.0 | RHT428B_5.0
571 | RHT428B | Packing Units | Package 1 Weight | 0.135 kg | _298.0 | RHT428B_298.0
572 | RHT428B | Contractual warranty | Warranty | 18 months | _287.0 | RHT428B_287.0
573 | RHT418BE | Main | range of product | Zelio Relay | _79.0 | RHT418BE_79.0
574 | RHT418BE | Main | product or component type | Timing relay Plug-in relay | _0.0 | RHT418BE_0.0
575 | RHT418BE | Main | device short name | RHT | _72.0 | RHT418BE_72.0
576 | RHT418BE | Main | contacts type and composition | 4 C/O | _18.0 | RHT418BE_18.0
577 | RHT418BE | Main | contact operation | Standard | _0.0 | RHT418BE_0.0
578 | RHT418BE | Main | [Uc] control circuit voltage | 27 V AC/DC 50/60 Hz | _84.0 | RHT418BE_84.0
579 | RHT418BE | Main | time delay type | On-delay | _68.0 | RHT418BE_68.0
580 | RHT418BE | Main | time delay range | 0.2...3 s 15...300 s 1.5...30 s | _96.0 | RHT418BE_96.0
581 | RHT418BE | Main | [Ithe] conventional enclosed thermal current | 5 A 40 °C | _41.0 | RHT418BE_41.0
582 | RHT418BE | Main | status LED | With | _30.0 | RHT418BE_30.0
583 | RHT418BE | Main | control type | Selector switch | _0.0 | RHT418BE_0.0
584 | RHT418BE | Main | coil interference suppression | With | _0.0 | RHT418BE_0.0
585 | RHT418BE | Complementary | [Ui] rated insulation voltage | 250 V | _8.0 | RHT418BE_8.0
586 | RHT418BE | Complementary | operating position | Any position | _50.0 | RHT418BE_50.0
587 | RHT418BE | Complementary | minimum switching capacity | 150 mVA at 10 mA, 1 V | _60.0 | RHT418BE_60.0
588 | RHT418BE | Complementary | contact bounce time | <= 10 ms | _0.0 | RHT418BE_0.0
589 | RHT418BE | Complementary | maximum voltage drop | <100 V for 3 A at 24 V | _93.0 | RHT418BE_93.0
590 | RHT418BE | Complementary | average resistance | 30 mOhm at 20 °C | _83.0 | RHT418BE_83.0
591 | RHT418BE | Complementary | switching time | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | _35.0 | RHT418BE_35.0
592 | RHT418BE | Complementary | average coil consumption | 2.5 W at 20 °C | _85.0 | RHT418BE_85.0
593 | RHT418BE | Complementary | average coil consumption in VA | 2.9 at 20 °C | _85.0 | RHT418BE_85.0
594 | RHT418BE | Complementary | control circuit voltage limits | 0.8...1.1 Uc conforming to IEC 60255 | _0.0 | RHT418BE_0.0
595 | RHT418BE | Complementary | mechanical durability | 20000000 cycles | _9.0 | RHT418BE_9.0
596 | RHT418BE | Complementary | repeat accuracy | +/- 1 % | _46.0 | RHT418BE_46.0
597 | RHT418BE | Complementary | setting accuracy of time delay | +/- 15 % of full scale | _45.0 | RHT418BE_45.0
598 | RHT418BE | Complementary | reset time | 100 ms | _34.0 | RHT418BE_34.0
599 | RHT418BE | Complementary | CAD overall width | 33 mm | _3.0 | RHT418BE_3.0
600 | RHT418BE | Complementary | CAD overall height | 43 mm | _2.0 | RHT418BE_2.0
601 | RHT418BE | Complementary | CAD overall depth | 108 mm | _1.0 | RHT418BE_1.0
602 | RHT418BE | Complementary | terminals description ISO n°1 | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | _0.0 | RHT418BE_0.0
603 | RHT418BE | Complementary | net weight | 0.13 kg | _298.0 | RHT418BE_298.0
604 | RHT418BE | Environment | standards | IEC 60255 NF C 45-250 VDE 0435 | _21.0 | RHT418BE_21.0
605 | RHT418BE | Environment | product certifications | ASE EDF USSR BV CSA | _32.0 | RHT418BE_32.0
606 | RHT418BE | Environment | protective treatment | TC | _0.0 | RHT418BE_0.0
607 | RHT418BE | Environment | dielectric strength | 2500 V | _20.0 | RHT418BE_20.0
608 | RHT418BE | Environment | ambient air temperature for operation | -5…40 °C conforming to IEC 60255 | _12.0 | RHT418BE_12.0
609 | RHT418BE | Environment | ambient air temperature for storage | -40…70 °C | _13.0 | RHT418BE_13.0
610 | RHT418BE | Environment | vibration resistance | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | _43.0 | RHT418BE_43.0
611 | RHT418BE | Environment | shock resistance | 50 gn for 11 ms conforming to NF C 20-608 | _37.0 | RHT418BE_37.0
612 | RHT418BE | Environment | immunity to microbreaks | 10 ms during time delay 2 ms after time delay | _5.0 | RHT418BE_5.0
613 | RHT418BE | Packing Units | Package 1 Weight | 0.136 kg | _298.0 | RHT418BE_298.0
614 | RHT418BE | Contractual warranty | Warranty | 18 months | _287.0 | RHT418BE_287.0
615 | RSB1A160M7S | Main | range of product | Zelio Relay | _79.0 | RSB1A160M7S_79.0
616 | RSB1A160M7S | Main | series name | Interface relay | _80.0 | RSB1A160M7S_80.0
617 | RSB1A160M7S | Main | product or component type | Plug-in relay | _0.0 | RSB1A160M7S_0.0
618 | RSB1A160M7S | Main | device short name | RSB | _72.0 | RSB1A160M7S_72.0
619 | RSB1A160M7S | Main | contacts type and composition | 1 C/O | _18.0 | RSB1A160M7S_18.0
620 | RSB1A160M7S | Main | contact operation | Standard | _0.0 | RSB1A160M7S_0.0
621 | RSB1A160M7S | Main | [Uc] control circuit voltage | 220 V AC | _84.0 | RSB1A160M7S_84.0
622 | RSB1A160M7S | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | _41.0 | RSB1A160M7S_41.0
623 | RSB1A160M7S | Main | status LED | Without | _30.0 | RSB1A160M7S_30.0
624 | RSB1A160M7S | Complementary | shape of pin | Flat | _0.0 | RSB1A160M7S_0.0
625 | RSB1A160M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | _75.0 | RSB1A160M7S_75.0
626 | RSB1A160M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | _78.0 | RSB1A160M7S_78.0
627 | RSB1A160M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB1A160M7S_8.0
628 | RSB1A160M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | _7.0 | RSB1A160M7S_7.0
629 | RSB1A160M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB1A160M7S_18.0
630 | RSB1A160M7S | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | _77.0 | RSB1A160M7S_77.0
631 | RSB1A160M7S | Complementary | minimum switching current | 5 mA | _88.0 | RSB1A160M7S_88.0
632 | RSB1A160M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB1A160M7S_87.0
633 | RSB1A160M7S | Complementary | minimum switching voltage | 5 V | _89.0 | RSB1A160M7S_89.0
634 | RSB1A160M7S | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | _59.0 | RSB1A160M7S_59.0
635 | RSB1A160M7S | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | _6.0 | RSB1A160M7S_6.0
636 | RSB1A160M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB1A160M7S_60.0
637 | RSB1A160M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB1A160M7S_0.0
638 | RSB1A160M7S | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB1A160M7S_9.0
639 | RSB1A160M7S | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | _6.0 | RSB1A160M7S_6.0
640 | RSB1A160M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | _35.0 | RSB1A160M7S_35.0
641 | RSB1A160M7S | Complementary | marking | CE | _31.0 | RSB1A160M7S_31.0
642 | RSB1A160M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | _85.0 | RSB1A160M7S_85.0
643 | RSB1A160M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | _0.0 | RSB1A160M7S_0.0
644 | RSB1A160M7S | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB1A160M7S_48.0
645 | RSB1A160M7S | Complementary | protection category | RT I | _56.0 | RSB1A160M7S_56.0
646 | RSB1A160M7S | Complementary | operating position | Any position | _50.0 | RSB1A160M7S_50.0
647 | RSB1A160M7S | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB1A160M7S_0.0
648 | RSB1A160M7S | Complementary | device presentation | Complete product | _0.0 | RSB1A160M7S_0.0
649 | RSB1A160M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB1A160M7S_20.0
650 | RSB1A160M7S | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | _21.0 | RSB1A160M7S_21.0
651 | RSB1A160M7S | Environment | product certifications | CSA UL GOST | _32.0 | RSB1A160M7S_32.0
652 | RSB1A160M7S | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB1A160M7S_13.0
653 | RSB1A160M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB1A160M7S_43.0
654 | RSB1A160M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB1A160M7S_29.0
655 | RSB1A160M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB1A160M7S_37.0
656 | RSB1A160M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB1A160M7S_12.0
657 | RSB1A160M7S | Packing Units | Package 1 Weight | 0.001 kg | _298.0 | RSB1A160M7S_298.0
658 | RSB1A160M7S | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RSB1A160M7S_295.0
659 | RSB1A160M7S | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RSB1A160M7S_293.0
660 | RSB1A160M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RSB1A160M7S_21.0
661 | RSB1A160M7S | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RSB1A160M7S_296.0
662 | RSB1A160M7S | Offer Sustainability | Mercury free | Yes | _291.0 | RSB1A160M7S_291.0
663 | RSB1A160M7S | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RSB1A160M7S_294.0
664 | RSB1A160M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RSB1A160M7S_288.0
665 | RSB1A160M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RSB1A160M7S_290.0
666 | RSB1A160M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RSB1A160M7S_297.0
667 | RSB1A160M7S | Contractual warranty | Warranty | 18 months | _287.0 | RSB1A160M7S_287.0
668 | RSB1A160NDS | Main | range of product | Zelio Relay | _79.0 | RSB1A160NDS_79.0
669 | RSB1A160NDS | Main | series name | Interface relay | _80.0 | RSB1A160NDS_80.0
670 | RSB1A160NDS | Main | product or component type | Plug-in relay | _0.0 | RSB1A160NDS_0.0
671 | RSB1A160NDS | Main | device short name | RSB | _72.0 | RSB1A160NDS_72.0
672 | RSB1A160NDS | Main | contacts type and composition | 1 C/O | _18.0 | RSB1A160NDS_18.0
673 | RSB1A160NDS | Main | contact operation | Standard | _0.0 | RSB1A160NDS_0.0
674 | RSB1A160NDS | Main | [Uc] control circuit voltage | 60 V DC | _84.0 | RSB1A160NDS_84.0
675 | RSB1A160NDS | Main | [Ithe] conventional enclosed thermal current | 16 A at -40…40 °C | _41.0 | RSB1A160NDS_41.0
676 | RSB1A160NDS | Main | status LED | Without | _30.0 | RSB1A160NDS_30.0
677 | RSB1A160NDS | Complementary | shape of pin | Flat | _0.0 | RSB1A160NDS_0.0
678 | RSB1A160NDS | Complementary | average coil resistance | 7500 Ohm network: DC at 20 °C +/- 10 % | _75.0 | RSB1A160NDS_75.0
679 | RSB1A160NDS | Complementary | [Ue] rated operational voltage | 48...66 V DC | _78.0 | RSB1A160NDS_78.0
680 | RSB1A160NDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB1A160NDS_8.0
681 | RSB1A160NDS | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | _7.0 | RSB1A160NDS_7.0
682 | RSB1A160NDS | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB1A160NDS_18.0
683 | RSB1A160NDS | Complementary | [Ie] rated operational current | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | _77.0 | RSB1A160NDS_77.0
684 | RSB1A160NDS | Complementary | minimum switching current | 5 mA | _88.0 | RSB1A160NDS_88.0
685 | RSB1A160NDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB1A160NDS_87.0
686 | RSB1A160NDS | Complementary | minimum switching voltage | 5 V | _89.0 | RSB1A160NDS_89.0
687 | RSB1A160NDS | Complementary | maximum switching capacity | 4000 VA AC 448 W DC | _59.0 | RSB1A160NDS_59.0
688 | RSB1A160NDS | Complementary | resistive rated load | 16 A at 250 V AC 16 A at 28 V DC | _6.0 | RSB1A160NDS_6.0
689 | RSB1A160NDS | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB1A160NDS_60.0
690 | RSB1A160NDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB1A160NDS_0.0
691 | RSB1A160NDS | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB1A160NDS_9.0
692 | RSB1A160NDS | Complementary | electrical durability | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | _6.0 | RSB1A160NDS_6.0
693 | RSB1A160NDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | _35.0 | RSB1A160NDS_35.0
694 | RSB1A160NDS | Complementary | marking | CE | _31.0 | RSB1A160NDS_31.0
695 | RSB1A160NDS | Complementary | average coil consumption | 0.45 W DC | _85.0 | RSB1A160NDS_85.0
696 | RSB1A160NDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | _0.0 | RSB1A160NDS_0.0
697 | RSB1A160NDS | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB1A160NDS_48.0
698 | RSB1A160NDS | Complementary | protection category | RT I | _56.0 | RSB1A160NDS_56.0
699 | RSB1A160NDS | Complementary | operating position | Any position | _50.0 | RSB1A160NDS_50.0
700 | RSB1A160NDS | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB1A160NDS_0.0
701 | RSB1A160NDS | Complementary | device presentation | Complete product | _0.0 | RSB1A160NDS_0.0
702 | RSB1A160NDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB1A160NDS_20.0
703 | RSB1A160NDS | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | _21.0 | RSB1A160NDS_21.0
704 | RSB1A160NDS | Environment | product certifications | CSA UL GOST | _32.0 | RSB1A160NDS_32.0
705 | RSB1A160NDS | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB1A160NDS_13.0
706 | RSB1A160NDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB1A160NDS_43.0
707 | RSB1A160NDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB1A160NDS_29.0
708 | RSB1A160NDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB1A160NDS_37.0
709 | RSB1A160NDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB1A160NDS_12.0
710 | RSB1A160NDS | Packing Units | Package 1 Weight | 0.001 kg | _298.0 | RSB1A160NDS_298.0
711 | RSB1A160NDS | Contractual warranty | Warranty | 18 months | _287.0 | RSB1A160NDS_287.0
712 | RSB2A080P7S | Main | range of product | Zelio Relay | _79.0 | RSB2A080P7S_79.0
713 | RSB2A080P7S | Main | series name | Interface relay | _80.0 | RSB2A080P7S_80.0
714 | RSB2A080P7S | Main | product or component type | Plug-in relay | _0.0 | RSB2A080P7S_0.0
715 | RSB2A080P7S | Main | device short name | RSB | _72.0 | RSB2A080P7S_72.0
716 | RSB2A080P7S | Main | contacts type and composition | 2 C/O | _18.0 | RSB2A080P7S_18.0
717 | RSB2A080P7S | Main | contact operation | Standard | _0.0 | RSB2A080P7S_0.0
718 | RSB2A080P7S | Main | [Uc] control circuit voltage | 230 V AC | _84.0 | RSB2A080P7S_84.0
719 | RSB2A080P7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | _41.0 | RSB2A080P7S_41.0
720 | RSB2A080P7S | Main | status LED | Without | _30.0 | RSB2A080P7S_30.0
721 | RSB2A080P7S | Main | control type | Without push-button | _0.0 | RSB2A080P7S_0.0
722 | RSB2A080P7S | Complementary | shape of pin | Flat | _0.0 | RSB2A080P7S_0.0
723 | RSB2A080P7S | Complementary | average coil resistance | 38500 Ohm network: AC at 20 °C +/- 15 % | _75.0 | RSB2A080P7S_75.0
724 | RSB2A080P7S | Complementary | [Ue] rated operational voltage | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | _78.0 | RSB2A080P7S_78.0
725 | RSB2A080P7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB2A080P7S_8.0
726 | RSB2A080P7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | _7.0 | RSB2A080P7S_7.0
727 | RSB2A080P7S | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB2A080P7S_18.0
728 | RSB2A080P7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | _77.0 | RSB2A080P7S_77.0
729 | RSB2A080P7S | Complementary | minimum switching current | 5 mA | _88.0 | RSB2A080P7S_88.0
730 | RSB2A080P7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB2A080P7S_87.0
731 | RSB2A080P7S | Complementary | minimum switching voltage | 5 V | _89.0 | RSB2A080P7S_89.0
732 | RSB2A080P7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | _59.0 | RSB2A080P7S_59.0
733 | RSB2A080P7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | _6.0 | RSB2A080P7S_6.0
734 | RSB2A080P7S | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB2A080P7S_60.0
735 | RSB2A080P7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB2A080P7S_0.0
736 | RSB2A080P7S | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB2A080P7S_9.0
737 | RSB2A080P7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | _6.0 | RSB2A080P7S_6.0
738 | RSB2A080P7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | _35.0 | RSB2A080P7S_35.0
739 | RSB2A080P7S | Complementary | marking | CE | _31.0 | RSB2A080P7S_31.0
740 | RSB2A080P7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | _85.0 | RSB2A080P7S_85.0
741 | RSB2A080P7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | _0.0 | RSB2A080P7S_0.0
742 | RSB2A080P7S | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB2A080P7S_48.0
743 | RSB2A080P7S | Complementary | protection category | RT I | _56.0 | RSB2A080P7S_56.0
744 | RSB2A080P7S | Complementary | operating position | Any position | _50.0 | RSB2A080P7S_50.0
745 | RSB2A080P7S | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB2A080P7S_0.0
746 | RSB2A080P7S | Complementary | device presentation | Complete product | _0.0 | RSB2A080P7S_0.0
747 | RSB2A080P7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB2A080P7S_20.0
748 | RSB2A080P7S | Environment | standards | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | _21.0 | RSB2A080P7S_21.0
749 | RSB2A080P7S | Environment | product certifications | GOST CSA UL | _32.0 | RSB2A080P7S_32.0
750 | RSB2A080P7S | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB2A080P7S_13.0
751 | RSB2A080P7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB2A080P7S_43.0
752 | RSB2A080P7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB2A080P7S_29.0
753 | RSB2A080P7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB2A080P7S_37.0
754 | RSB2A080P7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB2A080P7S_12.0
755 | RSB2A080P7S | Packing Units | Package 1 Weight | 61 g | _298.0 | RSB2A080P7S_298.0
756 | RSB2A080P7S | Packing Units | Package 2 Weight | 1.23 kg | _299.0 | RSB2A080P7S_299.0
757 | RSB2A080P7S | Packing Units | Package 3 Weight | 7.876 kg | _300.0 | RSB2A080P7S_300.0
758 | RSB2A080P7S | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RSB2A080P7S_295.0
759 | RSB2A080P7S | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RSB2A080P7S_293.0
760 | RSB2A080P7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RSB2A080P7S_21.0
761 | RSB2A080P7S | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RSB2A080P7S_296.0
762 | RSB2A080P7S | Offer Sustainability | Mercury free | Yes | _291.0 | RSB2A080P7S_291.0
763 | RSB2A080P7S | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RSB2A080P7S_294.0
764 | RSB2A080P7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RSB2A080P7S_288.0
765 | RSB2A080P7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RSB2A080P7S_290.0
766 | RSB2A080P7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RSB2A080P7S_297.0
767 | RSB2A080P7S | Contractual warranty | Warranty | 18 months | _287.0 | RSB2A080P7S_287.0
768 | RSB2A080RDS | Main | range of product | Zelio Relay | _79.0 | RSB2A080RDS_79.0
769 | RSB2A080RDS | Main | series name | Interface relay | _80.0 | RSB2A080RDS_80.0
770 | RSB2A080RDS | Main | product or component type | Plug-in relay | _0.0 | RSB2A080RDS_0.0
771 | RSB2A080RDS | Main | device short name | RSB | _72.0 | RSB2A080RDS_72.0
772 | RSB2A080RDS | Main | contacts type and composition | 2 C/O | _18.0 | RSB2A080RDS_18.0
773 | RSB2A080RDS | Main | contact operation | Standard | _0.0 | RSB2A080RDS_0.0
774 | RSB2A080RDS | Main | [Uc] control circuit voltage | 6 V DC | _84.0 | RSB2A080RDS_84.0
775 | RSB2A080RDS | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | _41.0 | RSB2A080RDS_41.0
776 | RSB2A080RDS | Main | status LED | Without | _30.0 | RSB2A080RDS_30.0
777 | RSB2A080RDS | Complementary | shape of pin | Flat | _0.0 | RSB2A080RDS_0.0
778 | RSB2A080RDS | Complementary | average coil resistance | 90 Ohm network: DC at 20 °C +/- 10 % | _75.0 | RSB2A080RDS_75.0
779 | RSB2A080RDS | Complementary | [Ue] rated operational voltage | 4.8...6.6 V DC | _78.0 | RSB2A080RDS_78.0
780 | RSB2A080RDS | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB2A080RDS_8.0
781 | RSB2A080RDS | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | _7.0 | RSB2A080RDS_7.0
782 | RSB2A080RDS | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB2A080RDS_18.0
783 | RSB2A080RDS | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | _77.0 | RSB2A080RDS_77.0
784 | RSB2A080RDS | Complementary | minimum switching current | 5 mA | _88.0 | RSB2A080RDS_88.0
785 | RSB2A080RDS | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB2A080RDS_87.0
786 | RSB2A080RDS | Complementary | minimum switching voltage | 5 V | _89.0 | RSB2A080RDS_89.0
787 | RSB2A080RDS | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | _59.0 | RSB2A080RDS_59.0
788 | RSB2A080RDS | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | _6.0 | RSB2A080RDS_6.0
789 | RSB2A080RDS | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB2A080RDS_60.0
790 | RSB2A080RDS | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB2A080RDS_0.0
791 | RSB2A080RDS | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB2A080RDS_9.0
792 | RSB2A080RDS | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | _6.0 | RSB2A080RDS_6.0
793 | RSB2A080RDS | Complementary | operating time | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | _35.0 | RSB2A080RDS_35.0
794 | RSB2A080RDS | Complementary | marking | CE | _31.0 | RSB2A080RDS_31.0
795 | RSB2A080RDS | Complementary | average coil consumption | 0.45 W DC | _85.0 | RSB2A080RDS_85.0
796 | RSB2A080RDS | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | _0.0 | RSB2A080RDS_0.0
797 | RSB2A080RDS | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB2A080RDS_48.0
798 | RSB2A080RDS | Complementary | protection category | RT I | _56.0 | RSB2A080RDS_56.0
799 | RSB2A080RDS | Complementary | operating position | Any position | _50.0 | RSB2A080RDS_50.0
800 | RSB2A080RDS | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB2A080RDS_0.0
801 | RSB2A080RDS | Complementary | device presentation | Complete product | _0.0 | RSB2A080RDS_0.0
802 | RSB2A080RDS | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB2A080RDS_20.0
803 | RSB2A080RDS | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | _21.0 | RSB2A080RDS_21.0
804 | RSB2A080RDS | Environment | product certifications | CSA GOST UL | _32.0 | RSB2A080RDS_32.0
805 | RSB2A080RDS | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB2A080RDS_13.0
806 | RSB2A080RDS | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB2A080RDS_43.0
807 | RSB2A080RDS | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB2A080RDS_29.0
808 | RSB2A080RDS | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB2A080RDS_37.0
809 | RSB2A080RDS | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB2A080RDS_12.0
810 | RSB2A080RDS | Packing Units | Package 1 Weight | 0.001 kg | _298.0 | RSB2A080RDS_298.0
811 | RSB2A080RDS | Contractual warranty | Warranty | 18 months | _287.0 | RSB2A080RDS_287.0
812 | RSB2A080U7S | Main | range of product | Zelio Relay | _79.0 | RSB2A080U7S_79.0
813 | RSB2A080U7S | Main | series name | Interface relay | _80.0 | RSB2A080U7S_80.0
814 | RSB2A080U7S | Main | product or component type | Plug-in relay | _0.0 | RSB2A080U7S_0.0
815 | RSB2A080U7S | Main | device short name | RSB | _72.0 | RSB2A080U7S_72.0
816 | RSB2A080U7S | Main | contacts type and composition | 2 C/O | _18.0 | RSB2A080U7S_18.0
817 | RSB2A080U7S | Main | contact operation | Standard | _0.0 | RSB2A080U7S_0.0
818 | RSB2A080U7S | Main | [Uc] control circuit voltage | 240 V AC | _84.0 | RSB2A080U7S_84.0
819 | RSB2A080U7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | _41.0 | RSB2A080U7S_41.0
820 | RSB2A080U7S | Main | status LED | Without | _30.0 | RSB2A080U7S_30.0
821 | RSB2A080U7S | Complementary | shape of pin | Flat | _0.0 | RSB2A080U7S_0.0
822 | RSB2A080U7S | Complementary | average coil resistance | 42500 Ohm network: AC at 20 °C +/- 15 % | _75.0 | RSB2A080U7S_75.0
823 | RSB2A080U7S | Complementary | [Ue] rated operational voltage | 192...288 V AC 50 Hz 204...288 V AC 60 Hz | _78.0 | RSB2A080U7S_78.0
824 | RSB2A080U7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB2A080U7S_8.0
825 | RSB2A080U7S | Complementary | [Uimp] rated impulse withstand voltage | 3.6 kV IEC 61000-4-5 | _7.0 | RSB2A080U7S_7.0
826 | RSB2A080U7S | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB2A080U7S_18.0
827 | RSB2A080U7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | _77.0 | RSB2A080U7S_77.0
828 | RSB2A080U7S | Complementary | minimum switching current | 5 mA | _88.0 | RSB2A080U7S_88.0
829 | RSB2A080U7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB2A080U7S_87.0
830 | RSB2A080U7S | Complementary | minimum switching voltage | 5 V | _89.0 | RSB2A080U7S_89.0
831 | RSB2A080U7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | _59.0 | RSB2A080U7S_59.0
832 | RSB2A080U7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | _6.0 | RSB2A080U7S_6.0
833 | RSB2A080U7S | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB2A080U7S_60.0
834 | RSB2A080U7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB2A080U7S_0.0
835 | RSB2A080U7S | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB2A080U7S_9.0
836 | RSB2A080U7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | _6.0 | RSB2A080U7S_6.0
837 | RSB2A080U7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | _35.0 | RSB2A080U7S_35.0
838 | RSB2A080U7S | Complementary | marking | CE | _31.0 | RSB2A080U7S_31.0
839 | RSB2A080U7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | _85.0 | RSB2A080U7S_85.0
840 | RSB2A080U7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | _0.0 | RSB2A080U7S_0.0
841 | RSB2A080U7S | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB2A080U7S_48.0
842 | RSB2A080U7S | Complementary | protection category | RT I | _56.0 | RSB2A080U7S_56.0
843 | RSB2A080U7S | Complementary | operating position | Any position | _50.0 | RSB2A080U7S_50.0
844 | RSB2A080U7S | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB2A080U7S_0.0
845 | RSB2A080U7S | Complementary | device presentation | Complete product | _0.0 | RSB2A080U7S_0.0
846 | RSB2A080U7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB2A080U7S_20.0
847 | RSB2A080U7S | Environment | standards | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | _21.0 | RSB2A080U7S_21.0
848 | RSB2A080U7S | Environment | product certifications | UL CSA GOST | _32.0 | RSB2A080U7S_32.0
849 | RSB2A080U7S | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB2A080U7S_13.0
850 | RSB2A080U7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB2A080U7S_43.0
851 | RSB2A080U7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB2A080U7S_29.0
852 | RSB2A080U7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB2A080U7S_37.0
853 | RSB2A080U7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB2A080U7S_12.0
854 | RSB2A080U7S | Packing Units | Package 1 Weight | 0.001 kg | _298.0 | RSB2A080U7S_298.0
855 | RSB2A080U7S | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RSB2A080U7S_295.0
856 | RSB2A080U7S | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RSB2A080U7S_293.0
857 | RSB2A080U7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RSB2A080U7S_21.0
858 | RSB2A080U7S | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RSB2A080U7S_296.0
859 | RSB2A080U7S | Offer Sustainability | Mercury free | Yes | _291.0 | RSB2A080U7S_291.0
860 | RSB2A080U7S | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RSB2A080U7S_294.0
861 | RSB2A080U7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RSB2A080U7S_288.0
862 | RSB2A080U7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RSB2A080U7S_290.0
863 | RSB2A080U7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RSB2A080U7S_297.0
864 | RSB2A080U7S | Contractual warranty | Warranty | 18 months | _287.0 | RSB2A080U7S_287.0
865 | RSB2A080M7S | Main | range of product | Zelio Relay | _79.0 | RSB2A080M7S_79.0
866 | RSB2A080M7S | Main | series name | Interface relay | _80.0 | RSB2A080M7S_80.0
867 | RSB2A080M7S | Main | product or component type | Plug-in relay | _0.0 | RSB2A080M7S_0.0
868 | RSB2A080M7S | Main | device short name | RSB | _72.0 | RSB2A080M7S_72.0
869 | RSB2A080M7S | Main | contacts type and composition | 2 C/O | _18.0 | RSB2A080M7S_18.0
870 | RSB2A080M7S | Main | contact operation | Standard | _0.0 | RSB2A080M7S_0.0
871 | RSB2A080M7S | Main | [Uc] control circuit voltage | 220 V AC | _84.0 | RSB2A080M7S_84.0
872 | RSB2A080M7S | Main | [Ithe] conventional enclosed thermal current | 8 A at -40…40 °C | _41.0 | RSB2A080M7S_41.0
873 | RSB2A080M7S | Main | status LED | Without | _30.0 | RSB2A080M7S_30.0
874 | RSB2A080M7S | Complementary | shape of pin | Flat | _0.0 | RSB2A080M7S_0.0
875 | RSB2A080M7S | Complementary | average coil resistance | 35500 Ohm network: AC at 20 °C +/- 15 % | _75.0 | RSB2A080M7S_75.0
876 | RSB2A080M7S | Complementary | [Ue] rated operational voltage | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | _78.0 | RSB2A080M7S_78.0
877 | RSB2A080M7S | Complementary | [Ui] rated insulation voltage | 400 V conforming to EN/IEC 60947 | _8.0 | RSB2A080M7S_8.0
878 | RSB2A080M7S | Complementary | [Uimp] rated impulse withstand voltage | IEC 61000-4-5 3.6 kV | _7.0 | RSB2A080M7S_7.0
879 | RSB2A080M7S | Complementary | contacts material | Silver alloy (Ag/Ni) | _18.0 | RSB2A080M7S_18.0
880 | RSB2A080M7S | Complementary | [Ie] rated operational current | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | _77.0 | RSB2A080M7S_77.0
881 | RSB2A080M7S | Complementary | minimum switching current | 5 mA | _88.0 | RSB2A080M7S_88.0
882 | RSB2A080M7S | Complementary | maximum switching voltage | 300 V DC 400 V AC | _87.0 | RSB2A080M7S_87.0
883 | RSB2A080M7S | Complementary | minimum switching voltage | 5 V | _89.0 | RSB2A080M7S_89.0
884 | RSB2A080M7S | Complementary | maximum switching capacity | 2000 VA AC 224 W DC | _59.0 | RSB2A080M7S_59.0
885 | RSB2A080M7S | Complementary | resistive rated load | 8 A at 250 V AC 8 A at 28 V DC | _6.0 | RSB2A080M7S_6.0
886 | RSB2A080M7S | Complementary | minimum switching capacity | 300 mW at 5 mA | _60.0 | RSB2A080M7S_60.0
887 | RSB2A080M7S | Complementary | operating rate | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | _0.0 | RSB2A080M7S_0.0
888 | RSB2A080M7S | Complementary | mechanical durability | 30000000 cycles | _9.0 | RSB2A080M7S_9.0
889 | RSB2A080M7S | Complementary | electrical durability | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | _6.0 | RSB2A080M7S_6.0
890 | RSB2A080M7S | Complementary | operating time | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | _35.0 | RSB2A080M7S_35.0
891 | RSB2A080M7S | Complementary | marking | CE | _31.0 | RSB2A080M7S_31.0
892 | RSB2A080M7S | Complementary | average coil consumption | 0.75 VA AC 60 Hz | _85.0 | RSB2A080M7S_85.0
893 | RSB2A080M7S | Complementary | drop-out voltage threshold | >= 0.15 Uc AC | _0.0 | RSB2A080M7S_0.0
894 | RSB2A080M7S | Complementary | safety reliability data | B10d = 100000 | _48.0 | RSB2A080M7S_48.0
895 | RSB2A080M7S | Complementary | protection category | RT I | _56.0 | RSB2A080M7S_56.0
896 | RSB2A080M7S | Complementary | operating position | Any position | _50.0 | RSB2A080M7S_50.0
897 | RSB2A080M7S | Complementary | sale per indivisible quantity | 10 | _0.0 | RSB2A080M7S_0.0
898 | RSB2A080M7S | Complementary | device presentation | Complete product | _0.0 | RSB2A080M7S_0.0
899 | RSB2A080M7S | Environment | dielectric strength | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | _20.0 | RSB2A080M7S_20.0
900 | RSB2A080M7S | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | _21.0 | RSB2A080M7S_21.0
901 | RSB2A080M7S | Environment | product certifications | GOST UL CSA | _32.0 | RSB2A080M7S_32.0
902 | RSB2A080M7S | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RSB2A080M7S_13.0
903 | RSB2A080M7S | Environment | vibration resistance | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | _43.0 | RSB2A080M7S_43.0
904 | RSB2A080M7S | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RSB2A080M7S_29.0
905 | RSB2A080M7S | Environment | shock resistance | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | _37.0 | RSB2A080M7S_37.0
906 | RSB2A080M7S | Environment | ambient air temperature for operation | -40…70 °C (AC) -40…85 °C (DC) | _12.0 | RSB2A080M7S_12.0
907 | RSB2A080M7S | Packing Units | Package 1 Weight | 0.001 kg | _298.0 | RSB2A080M7S_298.0
908 | RSB2A080M7S | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RSB2A080M7S_295.0
909 | RSB2A080M7S | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RSB2A080M7S_293.0
910 | RSB2A080M7S | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RSB2A080M7S_21.0
911 | RSB2A080M7S | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RSB2A080M7S_296.0
912 | RSB2A080M7S | Offer Sustainability | Mercury free | Yes | _291.0 | RSB2A080M7S_291.0
913 | RSB2A080M7S | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RSB2A080M7S_294.0
914 | RSB2A080M7S | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RSB2A080M7S_288.0
915 | RSB2A080M7S | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RSB2A080M7S_290.0
916 | RSB2A080M7S | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RSB2A080M7S_297.0
917 | RSB2A080M7S | Contractual warranty | Warranty | 18 months | _287.0 | RSB2A080M7S_287.0
918 | RXG11RD | Main | range of product | Harmony Relay | _79.0 | RXG11RD_79.0
919 | RXG11RD | Main | series name | Interface relay | _80.0 | RXG11RD_80.0
920 | RXG11RD | Main | product or component type | Plug-in relay | _0.0 | RXG11RD_0.0
921 | RXG11RD | Main | device short name | RXG | _72.0 | RXG11RD_72.0
922 | RXG11RD | Main | contacts type and composition | 1 C/O | _18.0 | RXG11RD_18.0
923 | RXG11RD | Complementary | status LED | Without | _30.0 | RXG11RD_30.0
924 | RXG11RD | Complementary | contacts material | Silver alloy (AgSnO2In2O3) | _18.0 | RXG11RD_18.0
925 | RXG11RD | Complementary | Maximum contact resistance | 100 mOhm | _83.0 | RXG11RD_83.0
926 | RXG11RD | Complementary | [Ithe] conventional enclosed thermal current | 10 A at -40…55 °C | _41.0 | RXG11RD_41.0
927 | RXG11RD | Complementary | [Ie] rated operational current | 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL | _77.0 | RXG11RD_77.0
928 | RXG11RD | Complementary | maximum switching voltage | 250 V AC 30 V DC | _87.0 | RXG11RD_87.0
929 | RXG11RD | Complementary | load current | 10 A at 250 V AC | _0.0 | RXG11RD_0.0
930 | RXG11RD | Complementary | maximum switching capacity | 2500 VA | _59.0 | RXG11RD_59.0
931 | RXG11RD | Complementary | minimum switching capacity | 500 mW at 100 mA, 5 V DC | _60.0 | RXG11RD_60.0
932 | RXG11RD | Complementary | operating rate | <= 1800 cycles/hour under load <= 18000 cycles/hour no-load | _0.0 | RXG11RD_0.0
933 | RXG11RD | Complementary | utilisation coefficient | 20 % | _97.0 | RXG11RD_97.0
934 | RXG11RD | Complementary | mechanical durability | 10000000 cycles | _9.0 | RXG11RD_9.0
935 | RXG11RD | Complementary | electrical durability | 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C | _6.0 | RXG11RD_6.0
936 | RXG11RD | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | _8.0 | RXG11RD_8.0
937 | RXG11RD | Complementary | [Uimp] rated impulse withstand voltage | 6 kV 1.2/50 µs | _7.0 | RXG11RD_7.0
938 | RXG11RD | Complementary | dielectric strength | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation | _20.0 | RXG11RD_20.0
939 | RXG11RD | Complementary | Coil resistance | 68 Ohm +/- 10 % | _75.0 | RXG11RD_75.0
940 | RXG11RD | Complementary | insulation resistance | 1000 MOhm at 500 V DC | _4.0 | RXG11RD_4.0
941 | RXG11RD | Complementary | test levels | Level A group mounting | _98.0 | RXG11RD_98.0
942 | RXG11RD | Complementary | mounting position | Any position | _50.0 | RXG11RD_50.0
943 | RXG11RD | Complementary | drop-out voltage threshold | >= 0.1 Uc DC | _0.0 | RXG11RD_0.0
944 | RXG11RD | Complementary | Coil insulation class | Class F | _76.0 | RXG11RD_76.0
945 | RXG11RD | Complementary | Operate time | 20 ms | _73.0 | RXG11RD_73.0
946 | RXG11RD | Complementary | Release time | 20 ms | _74.0 | RXG11RD_74.0
947 | RXG11RD | Complementary | [Uc] control circuit voltage | 6 V DC | _84.0 | RXG11RD_84.0
948 | RXG11RD | Complementary | safety reliability data | B10d = 100000 | _48.0 | RXG11RD_48.0
949 | RXG11RD | Complementary | colour of cover | Standard | _0.0 | RXG11RD_0.0
950 | RXG11RD | Complementary | control type | Lockable test button | _0.0 | RXG11RD_0.0
951 | RXG11RD | Complementary | local signalling | Flag | _30.0 | RXG11RD_30.0
952 | RXG11RD | Complementary | torque value | 0.8 N.m | _42.0 | RXG11RD_42.0
953 | RXG11RD | Complementary | net weight | 0.02 kg | _298.0 | RXG11RD_298.0
954 | RXG11RD | Complementary | device presentation | Complete product | _0.0 | RXG11RD_0.0
955 | RXG11RD | Environment | vibration resistance | 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation | _43.0 | RXG11RD_43.0
956 | RXG11RD | Environment | IP degree of protection | IP40 | _29.0 | RXG11RD_29.0
957 | RXG11RD | Environment | shock resistance | 20 gn in operation 100 gn not in operation | _37.0 | RXG11RD_37.0
958 | RXG11RD | Environment | protection category | RT I | _56.0 | RXG11RD_56.0
959 | RXG11RD | Environment | standards | UL 508 IEC 61810-1 CSA C22.2 No 14 | _21.0 | RXG11RD_21.0
960 | RXG11RD | Environment | product certifications | UL China RoHS CSA EAC REACH CE RoHS | _32.0 | RXG11RD_32.0
961 | RXG11RD | Environment | pollution degree | 2 | _40.0 | RXG11RD_40.0
962 | RXG11RD | Environment | overvoltage category | III | _55.0 | RXG11RD_55.0
963 | RXG11RD | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RXG11RD_13.0
964 | RXG11RD | Environment | ambient air temperature for operation | -40…70 °C | _12.0 | RXG11RD_12.0
965 | RXG11RD | Environment | relative humidity | 10…85 % | _33.0 | RXG11RD_33.0
966 | RXG11RD | Packing Units | Package 1 Weight | 20.200 g | _298.0 | RXG11RD_298.0
967 | RXG11RD | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RXG11RD_295.0
968 | RXG11RD | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RXG11RD_292.0
969 | RXG11RD | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RXG11RD_293.0
970 | RXG11RD | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RXG11RD_21.0
971 | RXG11RD | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RXG11RD_296.0
972 | RXG11RD | Offer Sustainability | Mercury free | Yes | _291.0 | RXG11RD_291.0
973 | RXG11RD | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RXG11RD_294.0
974 | RXG11RD | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RXG11RD_288.0
975 | RXG11RD | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RXG11RD_290.0
976 | RXM2AB1B7 | Main | range of product | Zelio Relay | _79.0 | RXM2AB1B7_79.0
977 | RXM2AB1B7 | Main | series name | Miniature | _80.0 | RXM2AB1B7_80.0
978 | RXM2AB1B7 | Main | product or component type | Plug-in relay | _0.0 | RXM2AB1B7_0.0
979 | RXM2AB1B7 | Main | device short name | RXM | _72.0 | RXM2AB1B7_72.0
980 | RXM2AB1B7 | Main | contacts type and composition | 2 C/O | _18.0 | RXM2AB1B7_18.0
981 | RXM2AB1B7 | Main | [Uc] control circuit voltage | 24 V AC 50/60 Hz | _84.0 | RXM2AB1B7_84.0
982 | RXM2AB1B7 | Main | [Ithe] conventional enclosed thermal current | 12 A at -40…55 °C | _41.0 | RXM2AB1B7_41.0
983 | RXM2AB1B7 | Main | status LED | Without | _30.0 | RXM2AB1B7_30.0
984 | RXM2AB1B7 | Main | control type | Lockable test button | _0.0 | RXM2AB1B7_0.0
985 | RXM2AB1B7 | Main | utilisation coefficient | 20 % | _97.0 | RXM2AB1B7_97.0
986 | RXM2AB1B7 | Complementary | shape of pin | Flat | _0.0 | RXM2AB1B7_0.0
987 | RXM2AB1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | _8.0 | RXM2AB1B7_8.0
988 | RXM2AB1B7 | Complementary | [Uimp] rated impulse withstand voltage | 4 kV during 1.2/50 µs | _7.0 | RXM2AB1B7_7.0
989 | RXM2AB1B7 | Complementary | contacts material | AgNi | _18.0 | RXM2AB1B7_18.0
990 | RXM2AB1B7 | Complementary | [Ie] rated operational current | 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL | _77.0 | RXM2AB1B7_77.0
991 | RXM2AB1B7 | Complementary | maximum switching voltage | 250 V conforming to IEC | _87.0 | RXM2AB1B7_87.0
992 | RXM2AB1B7 | Complementary | resistive rated load | 12 A at 250 V AC 12 A at 28 V DC | _6.0 | RXM2AB1B7_6.0
993 | RXM2AB1B7 | Complementary | maximum switching capacity | 3000 VA/336 W | _59.0 | RXM2AB1B7_59.0
994 | RXM2AB1B7 | Complementary | minimum switching capacity | 170 mW at 10 mA, 17 V | _60.0 | RXM2AB1B7_60.0
995 | RXM2AB1B7 | Complementary | operating rate | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | _0.0 | RXM2AB1B7_0.0
996 | RXM2AB1B7 | Complementary | mechanical durability | 10000000 cycles | _9.0 | RXM2AB1B7_9.0
997 | RXM2AB1B7 | Complementary | electrical durability | 100000 cycles for resistive load | _6.0 | RXM2AB1B7_6.0
998 | RXM2AB1B7 | Complementary | average coil consumption in VA | 1.2 at 60 Hz | _85.0 | RXM2AB1B7_85.0
999 | RXM2AB1B7 | Complementary | average consumption | 1.2 VA at 60 Hz | _85.0 | RXM2AB1B7_85.0
1000 | RXM2AB1B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc | _0.0 | RXM2AB1B7_0.0
1001 | RXM2AB1B7 | Complementary | operate time | 20 ms | operate time | RXM2AB1B7operate time
1002 | RXM2AB1B7 | Complementary | release time | 20 ms | release time | RXM2AB1B7release time
1003 | RXM2AB1B7 | Complementary | average coil resistance | 180 Ohm at 20 °C +/- 15 % | _75.0 | RXM2AB1B7_75.0
1004 | RXM2AB1B7 | Complementary | rated operational voltage limits | 19.2...26.4 V AC | _11.0 | RXM2AB1B7_11.0
1005 | RXM2AB1B7 | Complementary | safety reliability data | B10d = 100000 | _48.0 | RXM2AB1B7_48.0
1006 | RXM2AB1B7 | Complementary | protection category | RT I | _56.0 | RXM2AB1B7_56.0
1007 | RXM2AB1B7 | Complementary | test levels | Level A group mounting | _98.0 | RXM2AB1B7_98.0
1008 | RXM2AB1B7 | Complementary | operating position | Any position | _50.0 | RXM2AB1B7_50.0
1009 | RXM2AB1B7 | Complementary | net weight | 0.037 kg | _298.0 | RXM2AB1B7_298.0
1010 | RXM2AB1B7 | Complementary | device presentation | Complete product | _0.0 | RXM2AB1B7_0.0
1011 | RXM2AB1B7 | Environment | dielectric strength | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | _20.0 | RXM2AB1B7_20.0
1012 | RXM2AB1B7 | Environment | product certifications | UL Lloyd's RoHS CE CSA GOST REACH | _32.0 | RXM2AB1B7_32.0
1013 | RXM2AB1B7 | Environment | standards | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | _21.0 | RXM2AB1B7_21.0
1014 | RXM2AB1B7 | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RXM2AB1B7_13.0
1015 | RXM2AB1B7 | Environment | ambient air temperature for operation | -40…55 °C | _12.0 | RXM2AB1B7_12.0
1016 | RXM2AB1B7 | Environment | vibration resistance | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | _43.0 | RXM2AB1B7_43.0
1017 | RXM2AB1B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RXM2AB1B7_29.0
1018 | RXM2AB1B7 | Environment | shock resistance | 10 gn for in operation 30 gn for not operating | _37.0 | RXM2AB1B7_37.0
1019 | RXM2AB1B7 | Environment | pollution degree | 3 | _40.0 | RXM2AB1B7_40.0
1020 | RXM2AB1B7 | Packing Units | Package 1 Weight | 0.035 kg | _298.0 | RXM2AB1B7_298.0
1021 | RXM2AB1B7 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RXM2AB1B7_295.0
1022 | RXM2AB1B7 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RXM2AB1B7_292.0
1023 | RXM2AB1B7 | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RXM2AB1B7_293.0
1024 | RXM2AB1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RXM2AB1B7_21.0
1025 | RXM2AB1B7 | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RXM2AB1B7_296.0
1026 | RXM2AB1B7 | Offer Sustainability | Mercury free | Yes | _291.0 | RXM2AB1B7_291.0
1027 | RXM2AB1B7 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RXM2AB1B7_294.0
1028 | RXM2AB1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RXM2AB1B7_288.0
1029 | RXM2AB1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RXM2AB1B7_290.0
1030 | RXM2AB1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RXM2AB1B7_297.0
1031 | RXM2AB1B7 | Contractual warranty | Warranty | 18 months | _287.0 | RXM2AB1B7_287.0
1032 | RXM4AB1B7 | Main | range of product | Zelio Relay | _79.0 | RXM4AB1B7_79.0
1033 | RXM4AB1B7 | Main | series name | Miniature | _80.0 | RXM4AB1B7_80.0
1034 | RXM4AB1B7 | Main | product or component type | Plug-in relay | _0.0 | RXM4AB1B7_0.0
1035 | RXM4AB1B7 | Main | device short name | RXM | _72.0 | RXM4AB1B7_72.0
1036 | RXM4AB1B7 | Main | contacts type and composition | 4 C/O | _18.0 | RXM4AB1B7_18.0
1037 | RXM4AB1B7 | Main | [Uc] control circuit voltage | 24 V AC 50/60 Hz | _84.0 | RXM4AB1B7_84.0
1038 | RXM4AB1B7 | Main | [Ithe] conventional enclosed thermal current | 6 A at -40…55 °C | _41.0 | RXM4AB1B7_41.0
1039 | RXM4AB1B7 | Main | status LED | Without | _30.0 | RXM4AB1B7_30.0
1040 | RXM4AB1B7 | Main | control type | Lockable test button | _0.0 | RXM4AB1B7_0.0
1041 | RXM4AB1B7 | Main | utilisation coefficient | 20 % | _97.0 | RXM4AB1B7_97.0
1042 | RXM4AB1B7 | Complementary | shape of pin | Flat | _0.0 | RXM4AB1B7_0.0
1043 | RXM4AB1B7 | Complementary | [Ui] rated insulation voltage | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | _8.0 | RXM4AB1B7_8.0
1044 | RXM4AB1B7 | Complementary | [Uimp] rated impulse withstand voltage | 2.5 kV during 1.2/50 µs | _7.0 | RXM4AB1B7_7.0
1045 | RXM4AB1B7 | Complementary | contacts material | AgNi | _18.0 | RXM4AB1B7_18.0
1046 | RXM4AB1B7 | Complementary | [Ie] rated operational current | 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL | _77.0 | RXM4AB1B7_77.0
1047 | RXM4AB1B7 | Complementary | maximum switching voltage | 250 V conforming to IEC | _87.0 | RXM4AB1B7_87.0
1048 | RXM4AB1B7 | Complementary | resistive rated load | 6 A at 250 V AC 6 A at 28 V DC | _6.0 | RXM4AB1B7_6.0
1049 | RXM4AB1B7 | Complementary | maximum switching capacity | 1500 VA/168 W | _59.0 | RXM4AB1B7_59.0
1050 | RXM4AB1B7 | Complementary | minimum switching capacity | 170 mW at 10 mA, 17 V | _60.0 | RXM4AB1B7_60.0
1051 | RXM4AB1B7 | Complementary | operating rate | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | _0.0 | RXM4AB1B7_0.0
1052 | RXM4AB1B7 | Complementary | mechanical durability | 10000000 cycles | _9.0 | RXM4AB1B7_9.0
1053 | RXM4AB1B7 | Complementary | electrical durability | 100000 cycles for resistive load | _6.0 | RXM4AB1B7_6.0
1054 | RXM4AB1B7 | Complementary | average coil consumption in VA | 1.2 at 60 Hz | _85.0 | RXM4AB1B7_85.0
1055 | RXM4AB1B7 | Complementary | average consumption | 1.2 VA at 60 Hz | _85.0 | RXM4AB1B7_85.0
1056 | RXM4AB1B7 | Complementary | drop-out voltage threshold | >= 0.15 Uc | _0.0 | RXM4AB1B7_0.0
1057 | RXM4AB1B7 | Complementary | operate time | 20 ms | operate time | RXM4AB1B7operate time
1058 | RXM4AB1B7 | Complementary | release time | 20 ms | release time | RXM4AB1B7release time
1059 | RXM4AB1B7 | Complementary | average coil resistance | 180 Ohm at 20 °C +/- 15 % | _75.0 | RXM4AB1B7_75.0
1060 | RXM4AB1B7 | Complementary | rated operational voltage limits | 19.2...26.4 V AC | _11.0 | RXM4AB1B7_11.0
1061 | RXM4AB1B7 | Complementary | safety reliability data | B10d = 100000 | _48.0 | RXM4AB1B7_48.0
1062 | RXM4AB1B7 | Complementary | protection category | RT I | _56.0 | RXM4AB1B7_56.0
1063 | RXM4AB1B7 | Complementary | test levels | Level A group mounting | _98.0 | RXM4AB1B7_98.0
1064 | RXM4AB1B7 | Complementary | operating position | Any position | _50.0 | RXM4AB1B7_50.0
1065 | RXM4AB1B7 | Complementary | CAD overall height | 79 mm | _2.0 | RXM4AB1B7_2.0
1066 | RXM4AB1B7 | Complementary | CAD overall depth | 78.45 mm | _1.0 | RXM4AB1B7_1.0
1067 | RXM4AB1B7 | Complementary | net weight | 0.037 kg | _298.0 | RXM4AB1B7_298.0
1068 | RXM4AB1B7 | Complementary | device presentation | Complete product | _0.0 | RXM4AB1B7_0.0
1069 | RXM4AB1B7 | Environment | dielectric strength | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | _20.0 | RXM4AB1B7_20.0
1070 | RXM4AB1B7 | Environment | product certifications | RoHS CSA Lloyd's CE UL REACH GOST | _32.0 | RXM4AB1B7_32.0
1071 | RXM4AB1B7 | Environment | standards | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | _21.0 | RXM4AB1B7_21.0
1072 | RXM4AB1B7 | Environment | ambient air temperature for storage | -40…85 °C | _13.0 | RXM4AB1B7_13.0
1073 | RXM4AB1B7 | Environment | ambient air temperature for operation | -40…55 °C | _12.0 | RXM4AB1B7_12.0
1074 | RXM4AB1B7 | Environment | vibration resistance | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | _43.0 | RXM4AB1B7_43.0
1075 | RXM4AB1B7 | Environment | IP degree of protection | IP40 conforming to EN/IEC 60529 | _29.0 | RXM4AB1B7_29.0
1076 | RXM4AB1B7 | Environment | shock resistance | 10 gn for in operation 30 gn for not operating | _37.0 | RXM4AB1B7_37.0
1077 | RXM4AB1B7 | Environment | pollution degree | 2 | _40.0 | RXM4AB1B7_40.0
1078 | RXM4AB1B7 | Packing Units | Package 1 Weight | 0.036 kg | _298.0 | RXM4AB1B7_298.0
1079 | RXM4AB1B7 | Offer Sustainability | Sustainable offer status | Green Premium product | _295.0 | RXM4AB1B7_295.0
1080 | RXM4AB1B7 | Offer Sustainability | REACh Regulation | REACh Declaration | _292.0 | RXM4AB1B7_292.0
1081 | RXM4AB1B7 | Offer Sustainability | REACh free of SVHC | Yes | _293.0 | RXM4AB1B7_293.0
1082 | RXM4AB1B7 | Offer Sustainability | EU RoHS Directive | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | _21.0 | RXM4AB1B7_21.0
1083 | RXM4AB1B7 | Offer Sustainability | Toxic heavy metal free | Yes | _296.0 | RXM4AB1B7_296.0
1084 | RXM4AB1B7 | Offer Sustainability | Mercury free | Yes | _291.0 | RXM4AB1B7_291.0
1085 | RXM4AB1B7 | Offer Sustainability | RoHS exemption information | Yes | _294.0 | RXM4AB1B7_294.0
1086 | RXM4AB1B7 | Offer Sustainability | China RoHS Regulation | China RoHS declaration | _288.0 | RXM4AB1B7_288.0
1087 | RXM4AB1B7 | Offer Sustainability | Environmental Disclosure | Product Environmental Profile | _290.0 | RXM4AB1B7_290.0
1088 | RXM4AB1B7 | Offer Sustainability | WEEE | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | _297.0 | RXM4AB1B7_297.0
1089 | RXM4AB1B7 | Contractual warranty | Warranty | 18 months | _287.0 | RXM4AB1B7_287.0

## pivot_datasheet
| Reference | All_Cnt | Uniq_Cnt | Most_Cnt | Most_Freq_Val | RE22R2AMR | RE22R2CMR | RHT418BE | RHT428B | RM10TE00 | RM17JC00MW | RM17TA00 | RM17TE00 | RMTJ60BD | RSB1A160M7S | RSB1A160NDS | RSB2A080M7S | RSB2A080P7S | RSB2A080RDS | RSB2A080U7S | RXG11RD | RXM2AB1B7 | RXM4AB1B7 | XVDLS37 | XVDLS38
[6 empty] | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value | Value
Section | Parameters
Complementary | CAD overall depth | 5 | 3 | 2 | 45 mm |  |  | 108 mm | 108 mm | [13 empty] | 78.45 mm | 45 mm | 45 mm
| CAD overall height | 5 | 3 | 2 | 104 mm |  |  | 43 mm | 43 mm | [13 empty] | 79 mm | 104 mm | 104 mm
| CAD overall width | 4 | 2 | 2 | 45 mm |  |  | 33 mm | 33 mm | [14 empty] | 45 mm | 45 mm
| Coil insulation class | 1 | 1 | 1 | Class F | [15 empty] | Class F
| Coil resistance | 1 | 1 | 1 | 68 Ohm +/- 10 % | [15 empty] | 68 Ohm +/- 10 %
| Control signal pulse width | 2 | 1 | 2 | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms
| Maximum contact resistance | 1 | 1 | 1 | 100 mOhm | [15 empty] | 100 mOhm
| Operate time | 1 | 1 | 1 | 20 ms | [15 empty] | 20 ms
| Power on delay | 2 | 1 | 2 | 100 ms | 100 ms | 100 ms
| Rated impulse withstand voltage | 2 | 1 | 2 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 2 | 1 | 2 | 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation
| Release input voltage | 2 | 1 | 2 | <= 2.4 V | <= 2.4 V | <= 2.4 V
| Release time | 1 | 1 | 1 | 20 ms | [15 empty] | 20 ms
| [Ie] rated operational current | 9 | 5 | 4 | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | [9 empty] | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC | 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL | 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL | 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL
| [Ithe] conventional enclosed thermal current | 1 | 1 | 1 | 10 A at -40…55 °C | [15 empty] | 10 A at -40…55 °C
| [Uc] control circuit voltage | 1 | 1 | 1 | 6 V DC | [15 empty] | 6 V DC
| [Ue] rated operational voltage | 6 | 5 | 2 | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | [9 empty] | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 48...66 V DC | 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz | 4.8...6.6 V DC | 192...288 V AC 50 Hz 204...288 V AC 60 Hz
| [Ui] rated insulation voltage | 18 | 6 | 6 | 400 V conforming to EN/IEC 60947 |  |  | 250 V | 250 V | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 400 V conforming to IEC 60664-1 | 2 kV | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 400 V conforming to EN/IEC 60947 | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 250 V conforming to IEC 60947-1 | 250 V conforming to IEC 60947-1
| [Uimp] rated impulse withstand voltage | 11 | 6 | 3 | IEC 61000-4-5 3.6 kV | [9 empty] | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | IEC 61000-4-5 3.6 kV | 3.6 kV IEC 61000-4-5 | 6 kV 1.2/50 µs | 4 kV during 1.2/50 µs | 2.5 kV during 1.2/50 µs | 4 kV IEC 60947-1 | 4 kV IEC 60947-1
| [Us] rated supply voltage | 4 | 3 | 2 | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz | 24...240 V AC/DC 50/60 Hz |  |  |  | 24...240 V AC/DC 50/60 Hz +/- 10 % |  |  | 24 V DC +/- 20 %, non isolated
| abnormal analogue output current | 1 | 1 | 1 | -30…0 mA when no input or input wire broken | [8 empty] | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | 1 | 1 | 1 | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | [8 empty] | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold | 3 | 1 | 3 | 5...15 % of Un selected |  |  |  |  | 5...15 % of Un selected |  | 5...15 % of Un selected | 5...15 % of Un selected
| average coil consumption | 8 | 3 | 4 | 0.75 VA AC 60 Hz |  |  | 2.5 W at 20 °C | 2.5 W at 20 °C | [5 empty] | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz | 0.75 VA AC 60 Hz | 0.45 W DC | 0.75 VA AC 60 Hz
| average coil consumption in VA | 4 | 2 | 2 | 2.9 at 20 °C |  |  | 2.9 at 20 °C | 2.9 at 20 °C | [12 empty] | 1.2 at 60 Hz | 1.2 at 60 Hz
| average coil resistance | 8 | 6 | 2 | 35500 Ohm network: AC at 20 °C +/- 15 % | [9 empty] | 35500 Ohm network: AC at 20 °C +/- 15 % | 7500 Ohm network: DC at 20 °C +/- 10 % | 35500 Ohm network: AC at 20 °C +/- 15 % | 38500 Ohm network: AC at 20 °C +/- 15 % | 90 Ohm network: DC at 20 °C +/- 10 % | 42500 Ohm network: AC at 20 °C +/- 15 % |  | 180 Ohm at 20 °C +/- 15 % | 180 Ohm at 20 °C +/- 15 %
| average consumption | 2 | 1 | 2 | 1.2 VA at 60 Hz | [16 empty] | 1.2 VA at 60 Hz | 1.2 VA at 60 Hz
| average resistance | 2 | 1 | 2 | 30 mOhm at 20 °C |  |  | 30 mOhm at 20 °C | 30 mOhm at 20 °C
| cable entry | 2 | 1 | 2 | 1 entry tapped for Pg 7 | [18 empty] | 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7
| clamping connection capacity | 1 | 1 | 1 | 2 x 1.5 mm² 1 x 2.5 mm² | [8 empty] | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | 1 | 1 | 1 | Built-in, measurement: between 0 and 60 °C | [8 empty] | Built-in, measurement: between 0 and 60 °C
| colour of cover | 1 | 1 | 1 | Standard | [15 empty] | Standard
| connections - terminals | 8 | 3 | 4 | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end |  |  | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end | [10 empty] | Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw clamp terminals, <= 1 x 1.5 mm² with cable end
| contact bounce time | 2 | 1 | 2 | <= 10 ms |  |  | <= 10 ms | <= 10 ms
| contacts material | 10 | 4 | 6 | Silver alloy (Ag/Ni) | [5 empty] | Cadmium free |  |  |  | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (Ag/Ni) | Silver alloy (AgSnO2In2O3) | AgNi | AgNi
| contacts type and composition | 2 | 2 | 1 | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free | 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free
| control circuit frequency | 4 | 2 | 3 | 50...60 Hz +/- 10 % |  |  |  |  | 50...60 Hz +/- 10 % | 40...70 Hz sinusoidal | 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 %
| control circuit voltage limits | 5 | 2 | 3 | - 12 % + 10 % Un |  |  | 0.8...1.1 Uc conforming to IEC 60255 | 0.8...1.1 Uc conforming to IEC 60255 | - 12 % + 10 % Un |  | - 12 % + 10 % Un | - 12 % + 10 % Un
| control type | 3 | 3 | 1 | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button Potentiometer external | Rotary knob Diagnostic button | [13 empty] | Lockable test button
| creepage distance | 2 | 1 | 2 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1
| current consumption | 1 | 1 | 1 | <= 40 mA for voltage output <= 60 mA for current output | [8 empty] | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up | 4 | 2 | 3 | 650 ms |  |  |  |  | 650 ms | 0.5 s | 650 ms | 650 ms
| device presentation | 9 | 1 | 9 | Complete product | [9 empty] | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product | Complete product
| dielectric strength | 1 | 1 | 1 | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation | [15 empty] | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation
| drop-out voltage threshold | 9 | 3 | 4 | >= 0.15 Uc AC | [9 empty] | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc AC | >= 0.1 Uc DC | >= 0.15 Uc | >= 0.15 Uc
| electrical durability | 15 | 6 | 4 | 100000 cycles | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 | 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 |  |  | 100000 cycles | 100000 cycles | 100000 cycles | 100000 cycles |  | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC | 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C | 100000 cycles for resistive load | 100000 cycles for resistive load
| fixing mode | 1 | 1 | 1 | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | [8 empty] | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | 6 | 2 | 4 | Self-extinguishing plastic | Self-extinguishing | Self-extinguishing |  |  | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic | Self-extinguishing plastic
| hysteresis | 4 | 2 | 3 | 2 % |  |  |  |  | 2 % | 15 % fixed of threshold setting | 2 % | 2 %
| immunity to microbreaks | 2 | 1 | 2 | 10 ms | 10 ms | 10 ms
| input current | 1 | 1 | 1 | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | [5 empty] | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | 1 | 1 | 1 | Between supply and measurement | [5 empty] | Between supply and measurement
| insulation resistance | 7 | 3 | 4 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 | 100 MOhm at 500 V DC conforming to IEC 60664-1 |  |  | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 | [7 empty] | 1000 MOhm at 500 V DC
| load current | 1 | 1 | 1 | 10 A at 250 V AC | [15 empty] | 10 A at 250 V AC
| local signalling | 6 | 4 | 3 | LED (green) for power ON LED (yellow) for relay ON |  |  |  |  | LED (green)power ON: LED (yellow)relay ON: | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON LED (yellow) for relay ON | LED (green) for power ON | [6 empty] | Flag
| marking | 11 | 2 | 10 | CE |  |  |  |  | CE | CE : 73/23/EEC CE : EMC 89/336/EEC | CE | CE | CE | CE | CE | CE | CE | CE | CE
| maximum measuring cycle | 4 | 2 | 3 | 150 ms measurement cycle as true rms value |  |  |  |  | 150 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value
| maximum power consumption in W | 1 | 1 | 1 | 1 W | [5 empty] | 1 W
| maximum switching capacity | 9 | 5 | 4 | 2000 VA AC 224 W DC | [9 empty] | 4000 VA AC 448 W DC | 4000 VA AC 448 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2000 VA AC 224 W DC | 2500 VA | 3000 VA/336 W | 1500 VA/168 W
| maximum switching current | 5 | 2 | 3 | 5 A AC 5 A DC | 8 A | 8 A |  |  | 5 A AC 5 A DC |  | 5 A AC 5 A DC | 5 A AC 5 A DC
| maximum switching voltage | 15 | 6 | 6 | 300 V DC 400 V AC | 250 V AC | 250 V AC |  |  | 250 V AC 250 V DC | 250 V AC/DC | 250 V AC 250 V DC | 250 V AC 250 V DC |  | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 300 V DC 400 V AC | 250 V AC 30 V DC | 250 V conforming to IEC | 250 V conforming to IEC
| maximum voltage drop | 2 | 1 | 2 | <100 V for 3 A at 24 V |  |  | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V
| measurement accuracy | 1 | 1 | 1 | +/- 10 % of the full scale value | [5 empty] | +/- 10 % of the full scale value
| measurement error | 5 | 3 | 3 | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation |  |  |  |  | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation | +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C
| measurement voltage limits | 2 | 1 | 2 | 183…528 V AC | [6 empty] | 183…528 V AC | 183…528 V AC
| mechanical durability | 17 | 3 | 10 | 30000000 cycles | 10000000 cycles | 10000000 cycles | 20000000 cycles | 20000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles |  | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 30000000 cycles | 10000000 cycles | 10000000 cycles | 10000000 cycles
| minimum switching capacity | 11 | 5 | 6 | 300 mW at 5 mA |  |  | 150 mVA at 10 mA, 1 V | 50 mVA at 1 mA, 1 V | [5 empty] | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 300 mW at 5 mA | 500 mW at 100 mA, 5 V DC | 170 mW at 10 mA, 17 V | 170 mW at 10 mA, 17 V
| minimum switching current | 11 | 2 | 6 | 5 mA | 10 mA at 5 V DC | 10 mA at 5 V DC |  |  | 10 mA at 5 V DC |  | 10 mA at 5 V DC | 10 mA at 5 V DC |  | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA | 5 mA
| minimum switching voltage | 6 | 1 | 6 | 5 V | [9 empty] | 5 V | 5 V | 5 V | 5 V | 5 V | 5 V
| mounting position | 3 | 1 | 3 | Any position | Any position | Any position | [13 empty] | Any position
| mounting support | 6 | 2 | 4 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm DIN rail conforming to EN/IEC 60715 |  |  | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
| net weight | 14 | 6 | 6 | 0.13 kg | 0.105 kg | 0.105 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.13 kg | 0.12 kg | [6 empty] | 0.02 kg | 0.037 kg | 0.037 kg | 0.08 kg | 0.08 kg
| nominal output current | 4 | 1 | 4 | 5 A |  |  |  |  | 5 A | 5 A | 5 A | 5 A
| operate time | 2 | 1 | 2 | 20 ms | [16 empty] | 20 ms | 20 ms
| operating position | 14 | 2 | 10 | Any position |  |  | Any position | Any position | Any position without derating | Any position without derating | Any position without derating | Any position without derating |  | Any position | Any position | Any position | Any position | Any position | Any position |  | Any position | Any position
| operating rate | 13 | 4 | 6 | <= 600 cycles/hour under load <= 72000 cycles/hour no-load |  |  |  |  | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load | <= 360 operations/hour full load |  | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load | <= 1800 cycles/hour under load <= 18000 cycles/hour no-load | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | <= 1200 cycles/hour under load <= 18000 cycles/hour no-load
| operating time | 6 | 2 | 4 | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | [9 empty] | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | 1 | 1 | 1 | - 15 % + 10 % Un | [5 empty] | - 15 % + 10 % Un
| output contacts | 4 | 1 | 4 | 1 C/O |  |  |  |  | 1 C/O | 1 C/O | 1 C/O | 1 C/O
| overvoltage category | 6 | 1 | 6 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 |  |  | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1
| phase failure sensitivity | 3 | 1 | 3 | 0.7 Un |  |  |  |  | 0.7 Un |  | 0.7 Un | 0.7 Un
| polarity | 1 | 1 | 1 | Yes DC | [5 empty] | Yes DC
| power consumption in VA | 5 | 2 | 3 | 0…22 VA at 400 V AC 50 Hz | 3 VA at 240 V AC | 3 VA at 240 V AC |  |  | 0…22 VA at 400 V AC 50 Hz |  | 0…22 VA at 400 V AC 50 Hz | 0…22 VA at 400 V AC 50 Hz
| power consumption in W | 2 | 1 | 2 | 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC
| protection category | 8 | 1 | 8 | RT I | [9 empty] | RT I | RT I | RT I | RT I | RT I | RT I |  | RT I | RT I
| protection type | 1 | 1 | 1 | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | [8 empty] | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| rated operational voltage limits | 2 | 1 | 2 | 19.2...26.4 V AC | [16 empty] | 19.2...26.4 V AC | 19.2...26.4 V AC
| release time | 2 | 1 | 2 | 20 ms | [16 empty] | 20 ms | 20 ms
| repeat accuracy | 9 | 5 | 3 | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.5 % conforming to IEC 61812-1 | +/- 0.5 % conforming to IEC 61812-1 | +/- 1 % | +/- 1 % | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.5 % for input and measurement circuit | 0.5 % for input and measurement circuit 3 % for time delay | 0.5 % for input and measurement circuit 3 % for time delay | +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C
| reset time | 5 | 2 | 3 | 1500 ms time delay |  |  | 100 ms | 100 ms | 1500 ms time delay |  | 1500 ms time delay | 1500 ms time delay
| resistive rated load | 8 | 4 | 4 | 8 A at 250 V AC 8 A at 28 V DC | [9 empty] | 16 A at 250 V AC 16 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC |  | 12 A at 250 V AC 12 A at 28 V DC | 6 A at 250 V AC 6 A at 28 V DC
| response time | 4 | 1 | 4 | < 200 ms (in the event of a fault) |  |  |  |  | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault)
| safety reliability data | 15 | 6 | 9 | B10d = 100000 | B10d = 200000 MTTFd = 216.8 years | MTTFd = 251.1 years B10d = 230000 |  |  | B10d = 470000 MTTFd = 502.2 years |  | MTTFd = 502.2 years B10d = 470000 | MTTFd = 502.2 years B10d = 470000 | B10d = 45447 MTTFd = 49.2 years | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000 | B10d = 100000
| sale per indivisible quantity | 6 | 1 | 6 | 10 | [9 empty] | 10 | 10 | 10 | 10 | 10 | 10
| setting accuracy of time delay | 4 | 2 | 2 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 | +/- 15 % of full scale | +/- 15 % of full scale
| shape of pin | 8 | 1 | 8 | Flat | [9 empty] | Flat | Flat | Flat | Flat | Flat | Flat |  | Flat | Flat
| status LED | 3 | 2 | 2 | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised | [13 empty] | Without
| supply frequency | 5 | 2 | 3 | 50/60 Hz +/- 10 % | 50...60 Hz +/- 5 % | 50...60 Hz +/- 5 % |  |  | 50/60 Hz +/- 10 % |  | 50/60 Hz +/- 10 % | 50/60 Hz +/- 10 %
| supply voltage limits | 4 | 2 | 3 | 183…528 V AC |  |  |  |  | 183…528 V AC | 20.4…264 V AC/DC | 183…528 V AC | 183…528 V AC
| surge withstand | 1 | 1 | 1 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | [8 empty] | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2 | 1 | 2 | 2000 VA | 2000 VA | 2000 VA
| switching time | 2 | 1 | 2 | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation |  |  | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | 1 | 1 | 1 | 200 ppm/°C | [8 empty] | 200 ppm/°C
| temperature drift | 2 | 1 | 2 | +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C
| terminals description ISO n°1 | 4 | 4 | 1 | (GND)GROUND (COM-1)PW |  |  | (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC | [14 empty] | (GND)GROUND (COM-1)PW | (COM-1)PW (GND)GROUND
| test levels | 3 | 1 | 3 | Level A group mounting | [15 empty] | Level A group mounting | Level A group mounting | Level A group mounting
| threshold adjustment voltage | 3 | 3 | 1 | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC |  |  |  |  | -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC |  | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC | -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected
| threshold setting | 1 | 1 | 1 | 10...100 % | [5 empty] | 10...100 %
| tightening torque | 7 | 2 | 6 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 |  |  | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1 N.m conforming to IEC 60947-1 | 0.6…1.1 N.m
| time delay range | 2 | 2 | 1 | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min | 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min
| time delay type | 2 | 2 | 1 | Aw A | Aw A | C
| torque value | 1 | 1 | 1 | 0.8 N.m | [15 empty] | 0.8 N.m
| utilisation category | 3 | 1 | 3 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 |  |  |  |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 |  | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| utilisation coefficient | 1 | 1 | 1 | 20 % | [15 empty] | 20 %
| voltage drift | 2 | 1 | 2 | +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V
| voltage range | 5 | 2 | 3 | 208...480 V phase to phase | 0.85...1.1 Us | 0.85...1.1 Us |  |  | 208...480 V phase to phase |  | 208...480 V phase to phase | 208...480 V phase to phase
| width | 6 | 2 | 4 | 17.5 mm | 22.5 mm | 22.5 mm |  |  | 17.5 mm | 17.5 mm | 17.5 mm | 17.5 mm
Contractual warranty | Warranty | 16 | 1 | 16 | 18 months |  |  | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months | 18 months |  | 18 months | 18 months | 18 months | 18 months
Environment | IP degree of protection | 18 | 6 | 8 | IP40 conforming to EN/IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 | IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 |  |  | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 | IP20 (terminal block) IP50 (housing) | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 | IP40 conforming to EN/IEC 60529 | IP40 conforming to EN/IEC 60529 | IP40 conforming to IEC 60529 | IP40 conforming to IEC 60529
| ambient air temperature for operation | 20 | 8 | 6 | -40…70 °C (AC) -40…85 °C (DC) | -20…60 °C | -20…60 °C | -5…40 °C conforming to IEC 60255 | -5…40 °C conforming to IEC 60255 | -20…50 °C | -20…50 °C | -20…50 °C | -20…50 °C | 0…50 °C mounting side by side 0…60 °C 2 cm spacing | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C (AC) -40…85 °C (DC) | -40…70 °C | -40…55 °C | -40…55 °C | -25…70 °C | -25…70 °C
| ambient air temperature for storage | 20 | 2 | 10 | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…70 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…85 °C | -40…70 °C | -40…70 °C
| dielectric strength | 12 | 4 | 6 | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 | 2500 V | 2500 V | [5 empty] | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact |  | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles
| dielectric test voltage | 4 | 2 | 3 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 |  |  |  |  | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV AC 50 Hz | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 5 | 3 | 3 | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive | 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility |  |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive |  | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
| disturbance radiated/conducted | 1 | 1 | 1 | CISPR 22 group 1 - class B CISPR 11 | [8 empty] | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | 2 | 1 | 2 | Class II conforming to IEC 60536 | [18 empty] | Class II conforming to IEC 60536 | Class II conforming to IEC 60536
| electromagnetic compatibility | 6 | 3 | 3 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 |  |  | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
| fire resistance | 1 | 1 | 1 | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | [8 empty] | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks | 3 | 2 | 2 | 10 ms during time delay 2 ms after time delay |  |  | 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay |  | 10 ms
| non-dissipating shock wave | 4 | 2 | 3 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 |  |  |  |  | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| overvoltage category | 1 | 1 | 1 | III | [15 empty] | III
| pollution degree | 10 | 4 | 6 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 |  |  | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 3 conforming to IEC 60664-1 | 2 conforming to IEC 60664-1 | [6 empty] | 2 | 3 | 2
| product certifications | 20 | 18 | 2 | CSA UL | CE CCC GL China RoHS UL RCM EAC CSA | CSA CCC RCM China RoHS CE GL UL EAC | ASE EDF USSR BV CSA | USSR EDF ASE BV CSA | C-Tick UL GOST CSA GL | GL C-Tick GOST UL CSA | GOST CSA GL C-Tick UL | GOST C-Tick CSA UL GL | CSA GL UL | CSA UL GOST | CSA UL GOST | GOST UL CSA | GOST CSA UL | CSA GOST UL | UL CSA GOST | UL China RoHS CSA EAC REACH CE RoHS | UL Lloyd's RoHS CE CSA GOST REACH | RoHS CSA Lloyd's CE UL REACH GOST | CSA UL | CSA UL
| protection category | 1 | 1 | 1 | RT I | [15 empty] | RT I
| protective treatment | 4 | 1 | 4 | TC |  |  | TC | TC | [14 empty] | TC | TC
| relative humidity | 7 | 3 | 4 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 25…55 °C | 95 % at 25…55 °C |  |  | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | 95 % at 55 °C conforming to IEC 60068-2-30 | [7 empty] | 10…85 %
| resistance to electrostatic discharge | 1 | 1 | 1 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | [8 empty] | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | 1 | 1 | 1 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | [8 empty] | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 18 | 7 | 6 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 | 50 gn for 11 ms conforming to NF C 20-608 | 50 gn for 11 ms conforming to NF C 20-608 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 15 gn for 11 ms conforming to IEC 60255-21-1 | 50 gn for 11 ms conforming to IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 | 20 gn in operation 100 gn not in operation | 10 gn for in operation 30 gn for not operating | 10 gn for in operation 30 gn for not operating
| standards | 20 | 11 | 3 | EN/IEC 60255-1 | UL 508 IEC 61812-1 | UL 508 IEC 61812-1 | IEC 60255 NF C 45-250 VDE 0435 | IEC 60255 NF C 45-250 VDE 0435 | EN/IEC 60255-1 | EN/IEC 60255-6 | EN/IEC 60255-1 | EN/IEC 60255-1 | IEC 60584-1 IEC 60947-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | UL 508 CSA C22.2 No 14 EN/IEC 61810-1 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | CSA C22.2 No 14 EN/IEC 61810-1 UL 508 | UL 508 IEC 61810-1 CSA C22.2 No 14 | EN/IEC 61810-1 CSA C22.2 No 14 UL 508 | CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | EN/IEC 60947-5-1 | EN/IEC 60947-5-1
| vibration resistance | 18 | 7 | 6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 | 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 | 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating
Main | [Ithe] conventional enclosed thermal current | 10 | 6 | 4 | 8 A at -40…40 °C |  |  | 5 A 40 °C | 1 A 40 °C | [5 empty] | 16 A at -40…40 °C | 16 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C | 8 A at -40…40 °C |  | 12 A at -40…55 °C | 6 A at -40…55 °C
| [Uc] control circuit voltage | 10 | 8 | 2 | 220 V AC |  |  | 27 V AC/DC 50/60 Hz | 24 V AC/DC 50/60 Hz | [5 empty] | 220 V AC | 60 V DC | 220 V AC | 230 V AC | 6 V DC | 240 V AC |  | 24 V AC 50/60 Hz | 24 V AC 50/60 Hz
| [Us] rated supply voltage | 2 | 1 | 2 | <= 230 V | [18 empty] | <= 230 V | <= 230 V
| analogue input type | 1 | 1 | 1 | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | [8 empty] | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | 1 | 1 | 1 | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | [8 empty] | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | 2 | 1 | 2 | Base unit direct fixing Illuminated unit | [18 empty] | Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit
| bulb type | 2 | 1 | 2 | Incandescent with BA 15d base | [18 empty] | Incandescent with BA 15d base | Incandescent with BA 15d base
| coil interference suppression | 2 | 1 | 2 | With |  |  | With | With
| component name | 2 | 1 | 2 | XVDLS | [18 empty] | XVDLS | XVDLS
| contact operation | 8 | 2 | 7 | Standard |  |  | Standard | Low level | [5 empty] | Standard | Standard | Standard | Standard | Standard | Standard
| contacts type and composition | 11 | 3 | 5 | 2 C/O |  |  | 4 C/O | 4 C/O | [5 empty] | 1 C/O | 1 C/O | 2 C/O | 2 C/O | 2 C/O | 2 C/O | 1 C/O | 2 C/O | 4 C/O
| control type | 5 | 3 | 2 | Selector switch |  |  | Selector switch | Selector switch | [8 empty] | Without push-button |  |  |  | Lockable test button | Lockable test button
| device short name | 13 | 5 | 6 | RSB | RE22 | RE22 | RHT | RHT | [5 empty] | RSB | RSB | RSB | RSB | RSB | RSB | RXG | RXM | RXM
| discrete output type | 2 | 1 | 2 | Relay | Relay | Relay
| light source | 2 | 2 | 1 | Bulb not included, clear | [18 empty] | Bulb not included, clear | Bulb not included, yellow
| material | 2 | 1 | 2 | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | [18 empty] | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | 1 | 1 | 1 | 3 VA | [5 empty] | 3 VA
| maximum power dissipation in W | 2 | 1 | 2 | 5 W | [18 empty] | 5 W | 5 W
| measurement range | 4 | 3 | 2 | 208...480 V voltage AC |  |  |  |  | 183...528 V AC | 2...20 A current | 208...480 V voltage AC | 208...480 V voltage AC
| minimum switching current | 1 | 1 | 1 | 10 mA at 5 V DC | [5 empty] | 10 mA at 5 V DC
| mounting diameter | 2 | 1 | 2 | 45 mm | [18 empty] | 45 mm | 45 mm
| nominal output current | 2 | 1 | 2 | 8 A | 8 A | 8 A
| product or component type | 20 | 7 | 9 | Plug-in relay | Modular timing relay | Modular timing relay | Timing relay Plug-in relay | Plug-in relay Timing relay | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Modular measurement and control relays | Converter for thermocouples | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Plug-in relay | Complete miniature beacon | Complete miniature beacon
| product specific application | 3 | 1 | 3 | For 3-phase supply |  |  |  |  | For 3-phase supply |  | For 3-phase supply | For 3-phase supply
| range of product | 20 | 6 | 10 | Zelio Relay | Zelio Time | Zelio Time | Zelio Relay | Zelio Relay | Zelio Control | Zelio Control | Zelio Control | Zelio Control | Zelio Analog | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Zelio Relay | Harmony Relay | Zelio Relay | Zelio Relay | Harmony XVD Optimum | Harmony XVD Optimum
| relay monitored parameters | 4 | 4 | 1 | Overcurrent detection |  |  |  |  | Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | Overcurrent detection | Asymmetry Phase sequence Phase failure detection | Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection
| relay name | 4 | 4 | 1 | RM17JC |  |  |  |  | RM10TE | RM17JC | RM17TA | RM17TE
| relay type | 4 | 2 | 3 | Multifunction control relay |  |  |  |  | Multifunction control relay | Current control relay | Multifunction control relay | Multifunction control relay
| series name | 9 | 2 | 7 | Interface relay | [9 empty] | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Interface relay | Miniature | Miniature
| signalling type | 2 | 1 | 2 | Steady | [18 empty] | Steady | Steady
| status LED | 10 | 2 | 8 | Without |  |  | With | With | [5 empty] | Without | Without | Without | Without | Without | Without |  | Without | Without
| switching capacity in VA | 4 | 1 | 4 | 1250 VA |  |  |  |  | 1250 VA | 1250 VA | 1250 VA | 1250 VA
| time delay | 4 | 2 | 3 | Adjustable 0.1...10 s, +/- 10 % of the full scale value |  |  |  |  | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Without | Adjustable 0.1...10 s, +/- 10 % of the full scale value | Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range | 2 | 2 | 1 | 15...300 s 0.2...3 s 1.5...30 s |  |  | 0.2...3 s 15...300 s 1.5...30 s | 15...300 s 0.2...3 s 1.5...30 s
| time delay type | 2 | 1 | 2 | On-delay |  |  | On-delay | On-delay
| utilisation category | 1 | 1 | 1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | [5 empty] | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
| utilisation coefficient | 2 | 1 | 2 | 20 % | [16 empty] | 20 % | 20 %
Offer Sustainability | China RoHS Regulation | 16 | 1 | 16 | China RoHS declaration | China RoHS declaration | China RoHS declaration |  |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration |  | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration | China RoHS declaration
| Circularity Profile | 7 | 1 | 7 | End of Life Information | End of Life Information | End of Life Information |  |  | End of Life Information | End of Life Information | End of Life Information | End of Life Information | End of Life Information
| EU RoHS Directive | 16 | 1 | 16 | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration |  | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | 16 | 1 | 16 | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile |  |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile |  | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile | Product Environmental Profile
| Mercury free | 16 | 1 | 16 | Yes | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes
| REACh Regulation | 12 | 1 | 12 | REACh Declaration | REACh Declaration | REACh Declaration |  |  | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | [6 empty] | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration | REACh Declaration
| REACh free of SVHC | 7 | 1 | 7 | Yes | [9 empty] | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes
| RoHS exemption information | 16 | 1 | 16 | Yes | Yes | Yes |  |  | Yes | Yes | Yes | Yes | Yes | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes | Yes | Yes
| Sustainable offer status | 16 | 1 | 16 | Green Premium product | Green Premium product | Green Premium product |  |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product |  | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product | Green Premium product
| Toxic heavy metal free | 7 | 1 | 7 | Yes | [9 empty] | Yes |  | Yes | Yes |  | Yes | Yes | Yes | Yes
| WEEE | 13 | 1 | 13 | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  |  |  |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins |  | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Weight | 19 | 13 | 5 | 0.001 kg | 0.114 kg | 0.108 kg | 0.136 kg | 0.135 kg |  | 120 g | 89 g | 89 g | 0.101 kg | 0.001 kg | 0.001 kg | 0.001 kg | 61 g | 0.001 kg | 0.001 kg | 20.200 g | 0.035 kg | 0.036 kg | 0.101 kg | 0.100 kg
| Package 2 Weight | 4 | 4 | 1 | 4.295 kg | [5 empty] | 4.295 kg | 4.685 kg | 5.017 kg |  |  |  |  | 1.23 kg
| Package 3 Weight | 1 | 1 | 1 | 7.876 kg | [12 empty] | 7.876 kg

## pivot1_datasheet
|  | all_item_count | unique_item_count | most_freq_item_count | all_item_list | all_unique_item_list | most_freq_item
|  | Value | Value | Value | Value | Value | Value
Section | Parameters
Complementary | CAD overall depth | 5 | 3 | 2 | 45 mm 45 mm 108 mm 108 mm 78.45 mm | 45 mm¦ 108 mm¦ 78.45 mm | 45 mm
| CAD overall height | 5 | 3 | 2 | 104 mm 104 mm 43 mm 43 mm 79 mm | 104 mm¦ 43 mm¦ 79 mm | 104 mm
| CAD overall width | 4 | 2 | 2 | 45 mm 45 mm 33 mm 33 mm | 45 mm¦ 33 mm | 45 mm
| Coil insulation class | 1 | 1 | 1 | Class F | Class F | Class F
| Coil resistance | 1 | 1 | 1 | 68 Ohm +/- 10 % | 68 Ohm +/- 10 % | 68 Ohm +/- 10 %
| Control signal pulse width | 2 | 1 | 2 | 100 ms with load in parallel 30 ms 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms | 100 ms with load in parallel 30 ms
| Maximum contact resistance | 1 | 1 | 1 | 100 mOhm | 100 mOhm | 100 mOhm
| Operate time | 1 | 1 | 1 | 20 ms | 20 ms | 20 ms
| Power on delay | 2 | 1 | 2 | 100 ms 100 ms | 100 ms | 100 ms
| Rated impulse withstand voltage | 2 | 1 | 2 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1 | 5 kV for 1.2…50 µs conforming to IEC 60664-1
| Recovery time | 2 | 1 | 2 | 120 ms on de-energisation 120 ms on de-energisation | 120 ms on de-energisation | 120 ms on de-energisation
| Release input voltage | 2 | 1 | 2 | <= 2.4 V <= 2.4 V | <= 2.4 V | <= 2.4 V
| Release time | 1 | 1 | 1 | 20 ms | 20 ms | 20 ms
| [Ie] rated operational current | 9 | 5 | 4 | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL | 16 A (AC-1/DC-1) NO conforming to IEC 8 A (AC-1/DC-1) NC conforming to IEC¦ 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC¦ 10 A at 30 V (DC) conforming to UL 10 A at 30 V (DC) conforming to IEC 10 A at 250 V (AC) conforming to IEC 10 A at 250 V (AC) conforming to UL¦ 12 A at 28 V (DC) NO conforming to IEC 12 A at 250 V (AC) NO conforming to IEC 6 A at 28 V (DC) NC conforming to IEC 6 A at 250 V (AC) NC conforming to IEC 12 A at 28 V (DC) conforming to UL 12 A at 277 V (AC) conforming to UL¦ 3 A at 28 V (DC) NC conforming to IEC 3 A at 250 V (AC) NC conforming to IEC 6 A at 28 V (DC) NO conforming to IEC 6 A at 250 V (AC) NO conforming to IEC 6 A at 277 V (AC) conforming to UL 8 A at 30 V (DC) conforming to UL | 4 A (AC-1/DC-1) NC conforming to IEC 8 A (AC-1/DC-1) NO conforming to IEC
| [Ithe] conventional enclosed thermal current | 1 | 1 | 1 | 10 A at -40…55 °C | 10 A at -40…55 °C | 10 A at -40…55 °C
| [Uc] control circuit voltage | 1 | 1 | 1 | 6 V DC | 6 V DC | 6 V DC
| [Ue] rated operational voltage | 6 | 5 | 2 | 176...264 V AC 50 Hz 187...264 V AC 60 Hz 48...66 V DC 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz 4.8...6.6 V DC 192...288 V AC 50 Hz 204...288 V AC 60 Hz 176...264 V AC 50 Hz 187...264 V AC 60 Hz | 176...264 V AC 50 Hz 187...264 V AC 60 Hz¦ 48...66 V DC¦ 184...276 V AC 50 Hz 195.5...276 V AC 60 Hz¦ 4.8...6.6 V DC¦ 192...288 V AC 50 Hz 204...288 V AC 60 Hz | 176...264 V AC 50 Hz 187...264 V AC 60 Hz
| [Ui] rated insulation voltage | 18 | 6 | 6 | 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 400 V conforming to IEC 60664-1 2 kV 250 V conforming to IEC 60947-1 250 V conforming to IEC 60947-1 250 V 250 V 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 400 V conforming to EN/IEC 60947 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 400 V conforming to IEC 60664-1¦ 2 kV¦ 250 V conforming to IEC 60947-1¦ 250 V¦ 400 V conforming to EN/IEC 60947¦ 250 V conforming to IEC 300 V conforming to CSA 300 V conforming to UL | 400 V conforming to EN/IEC 60947
| [Uimp] rated impulse withstand voltage | 11 | 6 | 3 | 4 kV IEC 60947-1 4 kV IEC 60947-1 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV 3.6 kV IEC 61000-4-5 IEC 61000-4-5 3.6 kV 6 kV 1.2/50 µs 4 kV during 1.2/50 µs 2.5 kV during 1.2/50 µs | 4 kV IEC 60947-1¦ IEC 61000-4-5 3.6 kV¦ 3.6 kV IEC 61000-4-5¦ 6 kV 1.2/50 µs¦ 4 kV during 1.2/50 µs¦ 2.5 kV during 1.2/50 µs | IEC 61000-4-5 3.6 kV
| [Us] rated supply voltage | 4 | 3 | 2 | 24...240 V AC/DC 50/60 Hz +/- 10 % 24...240 V AC/DC 50/60 Hz 24...240 V AC/DC 50/60 Hz 24 V DC +/- 20 %, non isolated | 24...240 V AC/DC 50/60 Hz +/- 10 %¦ 24...240 V AC/DC 50/60 Hz¦ 24 V DC +/- 20 %, non isolated | 24...240 V AC/DC 50/60 Hz
| abnormal analogue output current | 1 | 1 | 1 | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken | -30…0 mA when no input or input wire broken
| abnormal analogue output voltage | 1 | 1 | 1 | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken | -15...-11 V when no input or input wire broken 11...15 V when no input or input wire broken
| adjustment of asymmetry threshold | 3 | 1 | 3 | 5...15 % of Un selected 5...15 % of Un selected 5...15 % of Un selected | 5...15 % of Un selected | 5...15 % of Un selected
| average coil consumption | 8 | 3 | 4 | 2.5 W at 20 °C 2.5 W at 20 °C 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.45 W DC 0.75 VA AC 60 Hz 0.75 VA AC 60 Hz | 2.5 W at 20 °C¦ 0.75 VA AC 60 Hz¦ 0.45 W DC | 0.75 VA AC 60 Hz
| average coil consumption in VA | 4 | 2 | 2 | 2.9 at 20 °C 2.9 at 20 °C 1.2 at 60 Hz 1.2 at 60 Hz | 2.9 at 20 °C¦ 1.2 at 60 Hz | 2.9 at 20 °C
| average coil resistance | 8 | 6 | 2 | 35500 Ohm network: AC at 20 °C +/- 15 % 7500 Ohm network: DC at 20 °C +/- 10 % 38500 Ohm network: AC at 20 °C +/- 15 % 90 Ohm network: DC at 20 °C +/- 10 % 42500 Ohm network: AC at 20 °C +/- 15 % 35500 Ohm network: AC at 20 °C +/- 15 % 180 Ohm at 20 °C +/- 15 % 180 Ohm at 20 °C +/- 15 % | 35500 Ohm network: AC at 20 °C +/- 15 %¦ 7500 Ohm network: DC at 20 °C +/- 10 %¦ 38500 Ohm network: AC at 20 °C +/- 15 %¦ 90 Ohm network: DC at 20 °C +/- 10 %¦ 42500 Ohm network: AC at 20 °C +/- 15 %¦ 180 Ohm at 20 °C +/- 15 % | 35500 Ohm network: AC at 20 °C +/- 15 %
| average consumption | 2 | 1 | 2 | 1.2 VA at 60 Hz 1.2 VA at 60 Hz | 1.2 VA at 60 Hz | 1.2 VA at 60 Hz
| average resistance | 2 | 1 | 2 | 30 mOhm at 20 °C 30 mOhm at 20 °C | 30 mOhm at 20 °C | 30 mOhm at 20 °C
| cable entry | 2 | 1 | 2 | 1 entry tapped for Pg 7 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7 | 1 entry tapped for Pg 7
| clamping connection capacity | 1 | 1 | 1 | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm² | 2 x 1.5 mm² 1 x 2.5 mm²
| cold junction compensation | 1 | 1 | 1 | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C | Built-in, measurement: between 0 and 60 °C
| colour of cover | 1 | 1 | 1 | Standard | Standard | Standard
| connections - terminals | 8 | 3 | 4 | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end¦ Screw terminals, 1 x 0.5...1 x 3.3 mm² (AWG 20...AWG 12) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 14) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end¦ Screw clamp terminals, <= 1 x 1.5 mm² with cable end | Screw terminals, 1 x 0.5...1 x 4 mm² (AWG 20...AWG 11) solid without cable end Screw terminals, 2 x 0.5...2 x 2.5 mm² (AWG 20...AWG 14) solid without cable end Screw terminals, 1 x 0.2...1 x 2.5 mm² (AWG 24...AWG 12) flexible with cable end Screw terminals, 2 x 0.2...2 x 1.5 mm² (AWG 24...AWG 16) flexible with cable end
| contact bounce time | 2 | 1 | 2 | <= 10 ms <= 10 ms | <= 10 ms | <= 10 ms
| contacts material | 10 | 4 | 6 | Cadmium free Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (Ag/Ni) Silver alloy (AgSnO2In2O3) AgNi AgNi | Cadmium free¦ Silver alloy (Ag/Ni)¦ Silver alloy (AgSnO2In2O3)¦ AgNi | Silver alloy (Ag/Ni)
| contacts type and composition | 2 | 2 | 1 | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free¦ 1 C/O timed or instantaneous contact, cadmium free 2 C/O timed contact, cadmium free | 1 C/O timed contact, cadmium free 1 C/O timed or instantaneous contact, cadmium free
| control circuit frequency | 4 | 2 | 3 | 40...70 Hz sinusoidal 50...60 Hz +/- 10 % 50...60 Hz +/- 10 % 50...60 Hz +/- 10 % | 40...70 Hz sinusoidal¦ 50...60 Hz +/- 10 % | 50...60 Hz +/- 10 %
| control circuit voltage limits | 5 | 2 | 3 | - 12 % + 10 % Un - 12 % + 10 % Un - 12 % + 10 % Un 0.8...1.1 Uc conforming to IEC 60255 0.8...1.1 Uc conforming to IEC 60255 | - 12 % + 10 % Un¦ 0.8...1.1 Uc conforming to IEC 60255 | - 12 % + 10 % Un
| control type | 3 | 3 | 1 | Rotary knob Diagnostic button Potentiometer external Rotary knob Diagnostic button Lockable test button | Rotary knob Diagnostic button Potentiometer external¦ Rotary knob Diagnostic button¦ Lockable test button | Rotary knob Diagnostic button Potentiometer external
| creepage distance | 2 | 1 | 2 | 4 kV/3 conforming to IEC 60664-1 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1 | 4 kV/3 conforming to IEC 60664-1
| current consumption | 1 | 1 | 1 | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output | <= 40 mA for voltage output <= 60 mA for current output
| delay at power up | 4 | 2 | 3 | 0.5 s 650 ms 650 ms 650 ms | 0.5 s¦ 650 ms | 650 ms
| device presentation | 9 | 1 | 9 | Complete product Complete product Complete product Complete product Complete product Complete product Complete product Complete product Complete product | Complete product | Complete product
| dielectric strength | 1 | 1 | 1 | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation | 1000 V AC between contacts with micro disconnection 5000 V AC between coil and contact with reinforced insulation
| drop-out voltage threshold | 9 | 3 | 4 | >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc AC >= 0.15 Uc AC >= 0.1 Uc DC >= 0.15 Uc >= 0.15 Uc | >= 0.15 Uc AC¦ >= 0.1 Uc DC¦ >= 0.15 Uc | >= 0.15 Uc AC
| electrical durability | 15 | 6 | 4 | 100000 cycles 100000 cycles 100000 cycles 100000 cycles 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C 100000 cycles for resistive load 100000 cycles for resistive load | 100000 cycles¦ 100000 cycles, 8 A at 250 V, AC-1 100000 cycles, 2 A at 24 V, DC-1¦ 100000 cycles, 16 A at 250 V, AC-1 NO 100000 cycles, 8 A at 250 V, AC-1 NC¦ 100000 cycles, 8 A at 250 V, AC-1 NO 100000 cycles, 4 A at 250 V, AC-1 NC¦ 100000 cycles for NO resistive load at 55 °C 100000 cycles for NC resistive load at 55 °C¦ 100000 cycles for resistive load | 100000 cycles
| fixing mode | 1 | 1 | 1 | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail) | By screws (mounting plate) Clip-on (35 mm symmetrical DIN rail)
| housing material | 6 | 2 | 4 | Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing plastic Self-extinguishing Self-extinguishing | Self-extinguishing plastic¦ Self-extinguishing | Self-extinguishing plastic
| hysteresis | 4 | 2 | 3 | 15 % fixed of threshold setting 2 % 2 % 2 % | 15 % fixed of threshold setting¦ 2 % | 2 %
| immunity to microbreaks | 2 | 1 | 2 | 10 ms 10 ms | 10 ms | 10 ms
| input current | 1 | 1 | 1 | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C | 100000 mA permanent at 25 °C 300000 mA non repetitive < 3 s at 25 °C
| insulation | 1 | 1 | 1 | Between supply and measurement | Between supply and measurement | Between supply and measurement
| insulation resistance | 7 | 3 | 4 | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 100 MOhm at 500 V DC conforming to IEC 60664-1 1000 MOhm at 500 V DC | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1¦ 100 MOhm at 500 V DC conforming to IEC 60664-1¦ 1000 MOhm at 500 V DC | > 500 MOhm at 500 V DC conforming to IEC 60255-5 > 500 MOhm at 500 V DC conforming to IEC 60664-1
| load current | 1 | 1 | 1 | 10 A at 250 V AC | 10 A at 250 V AC | 10 A at 250 V AC
| local signalling | 6 | 4 | 3 | LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green) for power ON LED (yellow) for relay ON LED (green)power ON: LED (yellow)relay ON: LED (green) for power ON Flag | LED (green) for power ON LED (yellow) for relay ON¦ LED (green)power ON: LED (yellow)relay ON:¦ LED (green) for power ON¦ Flag | LED (green) for power ON LED (yellow) for relay ON
| marking | 11 | 2 | 10 | CE : 73/23/EEC CE : EMC 89/336/EEC CE CE CE CE CE CE CE CE CE CE | CE : 73/23/EEC CE : EMC 89/336/EEC¦ CE | CE
| maximum measuring cycle | 4 | 2 | 3 | 30 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value 150 ms measurement cycle as true rms value | 30 ms measurement cycle as true rms value¦ 150 ms measurement cycle as true rms value | 150 ms measurement cycle as true rms value
| maximum power consumption in W | 1 | 1 | 1 | 1 W | 1 W | 1 W
| maximum switching capacity | 9 | 5 | 4 | 4000 VA AC 448 W DC 4000 VA AC 448 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2000 VA AC 224 W DC 2500 VA 3000 VA/336 W 1500 VA/168 W | 4000 VA AC 448 W DC¦ 2000 VA AC 224 W DC¦ 2500 VA¦ 3000 VA/336 W¦ 1500 VA/168 W | 2000 VA AC 224 W DC
| maximum switching current | 5 | 2 | 3 | 5 A AC 5 A DC 5 A AC 5 A DC 5 A AC 5 A DC 8 A 8 A | 5 A AC 5 A DC¦ 8 A | 5 A AC 5 A DC
| maximum switching voltage | 15 | 6 | 6 | 250 V AC/DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 250 V DC 250 V AC 250 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 300 V DC 400 V AC 250 V AC 30 V DC 250 V conforming to IEC 250 V conforming to IEC | 250 V AC/DC¦ 250 V AC 250 V DC¦ 250 V AC¦ 300 V DC 400 V AC¦ 250 V AC 30 V DC¦ 250 V conforming to IEC | 300 V DC 400 V AC
| maximum voltage drop | 2 | 1 | 2 | <100 V for 3 A at 24 V <100 V for 3 A at 24 V | <100 V for 3 A at 24 V | <100 V for 3 A at 24 V
| measurement accuracy | 1 | 1 | 1 | +/- 10 % of the full scale value | +/- 10 % of the full scale value | +/- 10 % of the full scale value
| measurement error | 5 | 3 | 3 | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | +/- 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation¦ < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation¦ +/- 10 % of full scale at 20 °C (electromagnetic interference of 10 V/m) +/- 1 % of full scale at 20 °C | < 0.05 %/°C with temperature variation < 1 % over the whole range with voltage variation
| measurement voltage limits | 2 | 1 | 2 | 183…528 V AC 183…528 V AC | 183…528 V AC | 183…528 V AC
| mechanical durability | 17 | 3 | 10 | 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 10000000 cycles 20000000 cycles 20000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 30000000 cycles 10000000 cycles 10000000 cycles 10000000 cycles | 30000000 cycles¦ 10000000 cycles¦ 20000000 cycles | 30000000 cycles
| minimum switching capacity | 11 | 5 | 6 | 50 mVA at 1 mA, 1 V 150 mVA at 10 mA, 1 V 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 300 mW at 5 mA 500 mW at 100 mA, 5 V DC 170 mW at 10 mA, 17 V 170 mW at 10 mA, 17 V | 50 mVA at 1 mA, 1 V¦ 150 mVA at 10 mA, 1 V¦ 300 mW at 5 mA¦ 500 mW at 100 mA, 5 V DC¦ 170 mW at 10 mA, 17 V | 300 mW at 5 mA
| minimum switching current | 11 | 2 | 6 | 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 10 mA at 5 V DC 5 mA 5 mA 5 mA 5 mA 5 mA 5 mA | 10 mA at 5 V DC¦ 5 mA | 5 mA
| minimum switching voltage | 6 | 1 | 6 | 5 V 5 V 5 V 5 V 5 V 5 V | 5 V | 5 V
| mounting position | 3 | 1 | 3 | Any position Any position Any position | Any position | Any position
| mounting support | 6 | 2 | 4 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm symmetrical DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715¦ 35 mm DIN rail conforming to EN/IEC 60715 | 35 mm symmetrical DIN rail conforming to EN/IEC 60715
| net weight | 14 | 6 | 6 | 0.13 kg 0.13 kg 0.13 kg 0.13 kg 0.105 kg 0.105 kg 0.12 kg 0.08 kg 0.08 kg 0.13 kg 0.13 kg 0.02 kg 0.037 kg 0.037 kg | 0.13 kg¦ 0.105 kg¦ 0.12 kg¦ 0.08 kg¦ 0.02 kg¦ 0.037 kg | 0.13 kg
| nominal output current | 4 | 1 | 4 | 5 A 5 A 5 A 5 A | 5 A | 5 A
| operate time | 2 | 1 | 2 | 20 ms 20 ms | 20 ms | 20 ms
| operating position | 14 | 2 | 10 | Any position without derating Any position without derating Any position without derating Any position without derating Any position Any position Any position Any position Any position Any position Any position Any position Any position Any position | Any position without derating¦ Any position | Any position
| operating rate | 13 | 4 | 6 | <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 360 operations/hour full load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 600 cycles/hour under load <= 72000 cycles/hour no-load <= 1800 cycles/hour under load <= 18000 cycles/hour no-load <= 1200 cycles/hour under load <= 18000 cycles/hour no-load <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | <= 360 operations/hour full load¦ <= 600 cycles/hour under load <= 72000 cycles/hour no-load¦ <= 1800 cycles/hour under load <= 18000 cycles/hour no-load¦ <= 1200 cycles/hour under load <= 18000 cycles/hour no-load | <= 600 cycles/hour under load <= 72000 cycles/hour no-load
| operating time | 6 | 2 | 4 | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact¦ 4 ms between coil de-energisation and making of the Off-delay contact 9 ms between coil energisation and making of the On-delay contact | 10 ms between coil de-energisation and making of the Off-delay contact 12 ms between coil energisation and making of the On-delay contact
| operating voltage tolerance | 1 | 1 | 1 | - 15 % + 10 % Un | - 15 % + 10 % Un | - 15 % + 10 % Un
| output contacts | 4 | 1 | 4 | 1 C/O 1 C/O 1 C/O 1 C/O | 1 C/O | 1 C/O
| overvoltage category | 6 | 1 | 6 | III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 III conforming to IEC 60664-1 | III conforming to IEC 60664-1 | III conforming to IEC 60664-1
| phase failure sensitivity | 3 | 1 | 3 | 0.7 Un 0.7 Un 0.7 Un | 0.7 Un | 0.7 Un
| polarity | 1 | 1 | 1 | Yes DC | Yes DC | Yes DC
| power consumption in VA | 5 | 2 | 3 | 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 0…22 VA at 400 V AC 50 Hz 3 VA at 240 V AC 3 VA at 240 V AC | 0…22 VA at 400 V AC 50 Hz¦ 3 VA at 240 V AC | 0…22 VA at 400 V AC 50 Hz
| power consumption in W | 2 | 1 | 2 | 1.5 W at 240 V DC 1.5 W at 240 V DC | 1.5 W at 240 V DC | 1.5 W at 240 V DC
| protection category | 8 | 1 | 8 | RT I RT I RT I RT I RT I RT I RT I RT I | RT I | RT I
| protection type | 1 | 1 | 1 | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output | Overvoltage protection on output (+/- 30 V) Reverse polarity protection on output Short-circuit protection on output
| rated operational voltage limits | 2 | 1 | 2 | 19.2...26.4 V AC 19.2...26.4 V AC | 19.2...26.4 V AC | 19.2...26.4 V AC
| release time | 2 | 1 | 2 | 20 ms 20 ms | 20 ms | 20 ms
| repeat accuracy | 9 | 5 | 3 | +/- 0.5 % for input and measurement circuit 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay 0.5 % for input and measurement circuit 3 % for time delay +/- 0.5 % conforming to IEC 61812-1 +/- 0.5 % conforming to IEC 61812-1 +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C +/- 1 % +/- 1 % | +/- 0.5 % for input and measurement circuit¦ 0.5 % for input and measurement circuit 3 % for time delay¦ +/- 0.5 % conforming to IEC 61812-1¦ +/- 0.25 % full scale at 20 °C +/- 0.8 % full scale at 60 °C¦ +/- 1 % | 0.5 % for input and measurement circuit 3 % for time delay
| reset time | 5 | 2 | 3 | 1500 ms time delay 1500 ms time delay 1500 ms time delay 100 ms 100 ms | 1500 ms time delay¦ 100 ms | 1500 ms time delay
| resistive rated load | 8 | 4 | 4 | 16 A at 250 V AC 16 A at 28 V DC 16 A at 250 V AC 16 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 8 A at 250 V AC 8 A at 28 V DC 12 A at 250 V AC 12 A at 28 V DC 6 A at 250 V AC 6 A at 28 V DC | 16 A at 250 V AC 16 A at 28 V DC¦ 8 A at 250 V AC 8 A at 28 V DC¦ 12 A at 250 V AC 12 A at 28 V DC¦ 6 A at 250 V AC 6 A at 28 V DC | 8 A at 250 V AC 8 A at 28 V DC
| response time | 4 | 1 | 4 | < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault) | < 200 ms (in the event of a fault)
| safety reliability data | 15 | 6 | 9 | MTTFd = 502.2 years B10d = 470000 MTTFd = 502.2 years B10d = 470000 B10d = 470000 MTTFd = 502.2 years B10d = 200000 MTTFd = 216.8 years MTTFd = 251.1 years B10d = 230000 B10d = 45447 MTTFd = 49.2 years B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 B10d = 100000 | MTTFd = 502.2 years B10d = 470000¦ B10d = 470000 MTTFd = 502.2 years¦ B10d = 200000 MTTFd = 216.8 years¦ MTTFd = 251.1 years B10d = 230000¦ B10d = 45447 MTTFd = 49.2 years¦ B10d = 100000 | B10d = 100000
| sale per indivisible quantity | 6 | 1 | 6 | 10 10 10 10 10 10 | 10 | 10
| setting accuracy of time delay | 4 | 2 | 2 | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 10 % of full scale at 25 °C conforming to IEC 61812-1 +/- 15 % of full scale +/- 15 % of full scale | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1¦ +/- 15 % of full scale | +/- 10 % of full scale at 25 °C conforming to IEC 61812-1
| shape of pin | 8 | 1 | 8 | Flat Flat Flat Flat Flat Flat Flat Flat | Flat | Flat
| status LED | 3 | 2 | 2 | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised Without | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised¦ Without | LED backlight green (steady) for dial pointer indication LED yellow (steady) for output relay energised LED yellow (fast flashing) for timing in progress and output relay de-energised LED yellow (slow flashing) for timing in progress and output relay energised
| supply frequency | 5 | 2 | 3 | 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50/60 Hz +/- 10 % 50...60 Hz +/- 5 % 50...60 Hz +/- 5 % | 50/60 Hz +/- 10 %¦ 50...60 Hz +/- 5 % | 50/60 Hz +/- 10 %
| supply voltage limits | 4 | 2 | 3 | 20.4…264 V AC/DC 183…528 V AC 183…528 V AC 183…528 V AC | 20.4…264 V AC/DC¦ 183…528 V AC | 183…528 V AC
| surge withstand | 1 | 1 | 1 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5 | 0.5 kV during 1.2/50 µs conforming to IEC 61000-4-5
| switching capacity in VA | 2 | 1 | 2 | 2000 VA 2000 VA | 2000 VA | 2000 VA
| switching time | 2 | 1 | 2 | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation | 1...3 ms AC for energisation/de-energisation 0.5...6 ms AC for de-energisation/energisation 1...4 ms DC for energisation/de-energisation 1.2...4 ms DC for de-energisation/energisation
| temperature coefficient | 1 | 1 | 1 | 200 ppm/°C | 200 ppm/°C | 200 ppm/°C
| temperature drift | 2 | 1 | 2 | +/- 0.05 %/°C +/- 0.05 %/°C | +/- 0.05 %/°C | +/- 0.05 %/°C
| terminals description ISO n°1 | 4 | 4 | 1 | (GND)GROUND (COM-1)PW (COM-1)PW (GND)GROUND (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (GND)GROUND (COM-1)PW¦ (COM-1)PW (GND)GROUND¦ (A1-A2)CO (41-42-44)OC (21-22-24)OC (31-32-34)OC (11-12-14)OC¦ (31-32-34)OC (41-42-44)OC (11-12-14)OC (21-22-24)OC (A1-A2)CO | (GND)GROUND (COM-1)PW
| test levels | 3 | 1 | 3 | Level A group mounting Level A group mounting Level A group mounting | Level A group mounting | Level A group mounting
| threshold adjustment voltage | 3 | 3 | 1 | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC¦ -2...-17 % in the range 220 V AC +2...+17 % in the range 480 V AC -2...-12 % in the range 208 V AC 2...20 % of Un selected¦ -2...-12 % in the range 208 V AC 2...20 % of Un selected +2...+17 % in the range 480 V AC -2...-17 % in the range 220 V AC | +2...+17 % in the range 480 V AC 2...20 % of Un selected -2...-17 % in the range 220 V AC -2...-12 % in the range 208 V AC
| threshold setting | 1 | 1 | 1 | 10...100 % | 10...100 % | 10...100 %
| tightening torque | 7 | 2 | 6 | 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1 N.m conforming to IEC 60947-1 0.6…1.1 N.m | 0.6…1 N.m conforming to IEC 60947-1¦ 0.6…1.1 N.m | 0.6…1 N.m conforming to IEC 60947-1
| time delay range | 2 | 2 | 1 | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min¦ 10...100 s 3...30 h 1...10 s 3...30 s 30...300 h 0.3...3 s 0.05...1 s 30...300 min 30...300 s 3...30 min | 0.05...1 s 0.3...3 s 3...30 h 30...300 min 10...100 s 30...300 s 3...30 s 30...300 h 1...10 s 3...30 min
| time delay type | 2 | 2 | 1 | Aw A C | Aw A¦ C | Aw A
| torque value | 1 | 1 | 1 | 0.8 N.m | 0.8 N.m | 0.8 N.m
| utilisation category | 3 | 1 | 3 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1
| utilisation coefficient | 1 | 1 | 1 | 20 % | 20 % | 20 %
| voltage drift | 2 | 1 | 2 | +/- 0.2 %/V +/- 0.2 %/V | +/- 0.2 %/V | +/- 0.2 %/V
| voltage range | 5 | 2 | 3 | 208...480 V phase to phase 208...480 V phase to phase 208...480 V phase to phase 0.85...1.1 Us 0.85...1.1 Us | 208...480 V phase to phase¦ 0.85...1.1 Us | 208...480 V phase to phase
| width | 6 | 2 | 4 | 17.5 mm 17.5 mm 17.5 mm 17.5 mm 22.5 mm 22.5 mm | 17.5 mm¦ 22.5 mm | 17.5 mm
Contractual warranty | Warranty | 16 | 1 | 16 | 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months 18 months | 18 months | 18 months
Environment | IP degree of protection | 18 | 6 | 8 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529 IP20 (terminal block) IP50 (housing) IP40 conforming to IEC 60529 IP40 conforming to IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 IP40 IP40 conforming to EN/IEC 60529 IP40 conforming to EN/IEC 60529 | IP20 (terminals) conforming to IEC 60529 IP30 (casing) conforming to IEC 60529¦ IP40 housing: conforming to IEC 60529 IP20 terminals: conforming to IEC 60529 IP50 front panel: conforming to IEC 60529¦ IP20 (terminal block) IP50 (housing)¦ IP40 conforming to IEC 60529¦ IP40 conforming to EN/IEC 60529¦ IP40 | IP40 conforming to EN/IEC 60529
| ambient air temperature for operation | 20 | 8 | 6 | -20…50 °C -20…50 °C -20…50 °C -20…50 °C -20…60 °C -20…60 °C 0…50 °C mounting side by side 0…60 °C 2 cm spacing -25…70 °C -25…70 °C -5…40 °C conforming to IEC 60255 -5…40 °C conforming to IEC 60255 -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C (AC) -40…85 °C (DC) -40…70 °C -40…55 °C -40…55 °C | -20…50 °C¦ -20…60 °C¦ 0…50 °C mounting side by side 0…60 °C 2 cm spacing¦ -25…70 °C¦ -5…40 °C conforming to IEC 60255¦ -40…70 °C (AC) -40…85 °C (DC)¦ -40…70 °C¦ -40…55 °C | -40…70 °C (AC) -40…85 °C (DC)
| ambient air temperature for storage | 20 | 2 | 10 | -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…70 °C -40…70 °C -40…70 °C -40…70 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C -40…85 °C | -40…70 °C¦ -40…85 °C | -40…70 °C
| dielectric strength | 12 | 4 | 6 | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1 2500 V 2500 V 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | 2.5 kV for 1 mA/1 minute at 50 Hz between relay output and power supply with basic insulation conforming to IEC 61812-1¦ 2500 V¦ 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact¦ 1300 V AC between contacts with micro disconnection 2000 V AC between coil and contact 2000 V AC between poles | 1000 V AC between contacts 2500 V AC between poles 5000 V AC between coil and contact
| dielectric test voltage | 4 | 2 | 3 | 2 kV AC 50 Hz 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV AC 50 Hz¦ 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1 | 2 kV, 1 min AC 50 Hz conforming to IEC 60255-5 2 kV, 1 min AC 50 Hz conforming to IEC 60664-1
| directives | 5 | 3 | 3 | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive¦ 2004/108/EC - electromagnetic compatibility 2006/95/EC - low voltage directive¦ 2006/95/EC - low voltage directive 2004/108/EC - electromagnetic compatibility | 89/336/EEC - electromagnetic compatibility 73/23/EEC - low voltage directive
| disturbance radiated/conducted | 1 | 1 | 1 | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11 | CISPR 22 group 1 - class B CISPR 11
| electrical shock protection class | 2 | 1 | 2 | Class II conforming to IEC 60536 Class II conforming to IEC 60536 | Class II conforming to IEC 60536 | Class II conforming to IEC 60536
| electromagnetic compatibility | 6 | 3 | 3 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to NF EN/IEC 61000-6-2¦ Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2¦ Fast transients immunity test - test level: 1 kV level 3 (capacitive connecting clip) conforming to IEC 61000-4-4 Surge immunity test - test level: 1 kV level 3 (differential mode) conforming to IEC 61000-4-5 Surge immunity test - test level: 2 kV level 3 (common mode) conforming to IEC 61000-4-5 Electrostatic discharge - test level: 6 kV level 3 (contact discharge) conforming to IEC 61000-4-2 Electrostatic discharge - test level: 8 kV level 3 (air discharge) conforming to IEC 61000-4-2 Radiated radio-frequency electromagnetic field immunity test - test level: 10 V/m level 3 (80 MHz...1 GHz) conforming to IEC 61000-4-3 Conducted RF disturbances - test level: 10 V level 3 (0.15...80 MHz) conforming to IEC 61000-4-6 Fast transient bursts - test level: 2 kV level 3 (direct contact) conforming to IEC 61000-4-4 Immunity to microbreaks and voltage drops - test level: 30 % (500 ms) conforming to IEC 61000-4-11 Immunity to microbreaks and voltage drops - test level: 100 % (20 ms) conforming to IEC 61000-4-11 | Emission standard for industrial environments conforming to EN/IEC 61000-6-4 Emission standard for residential, commercial and light-industrial environments conforming to EN/IEC 61000-6-3 Immunity for industrial environments conforming to EN/IEC 61000-6-2
| fire resistance | 1 | 1 | 1 | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL | 850 °C conforming to IEC 60695-2-1 850 °C conforming to UL
| immunity to microbreaks | 3 | 2 | 2 | 10 ms 10 ms during time delay 2 ms after time delay 10 ms during time delay 2 ms after time delay | 10 ms¦ 10 ms during time delay 2 ms after time delay | 10 ms during time delay 2 ms after time delay
| non-dissipating shock wave | 4 | 2 | 3 | 4 kV 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV¦ 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5 | 4 kV conforming to IEC 60255-5 4 kV conforming to IEC 60664-1 4 kV conforming to IEC 61000-4-5
| overvoltage category | 1 | 1 | 1 | III | III | III
| pollution degree | 10 | 4 | 6 | 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 3 conforming to IEC 60664-1 2 conforming to IEC 60664-1 2 3 2 | 3 conforming to IEC 60664-1¦ 2 conforming to IEC 60664-1¦ 2¦ 3 | 3 conforming to IEC 60664-1
| product certifications | 20 | 18 | 2 | GL C-Tick GOST UL CSA GOST CSA GL C-Tick UL GOST C-Tick CSA UL GL C-Tick UL GOST CSA GL CE CCC GL China RoHS UL RCM EAC CSA CSA CCC RCM China RoHS CE GL UL EAC CSA GL UL CSA UL CSA UL USSR EDF ASE BV CSA ASE EDF USSR BV CSA CSA UL GOST CSA UL GOST GOST CSA UL CSA GOST UL UL CSA GOST GOST UL CSA UL China RoHS CSA EAC REACH CE RoHS UL Lloyd's RoHS CE CSA GOST REACH RoHS CSA Lloyd's CE UL REACH GOST | GL C-Tick GOST UL CSA¦ GOST CSA GL C-Tick UL¦ GOST C-Tick CSA UL GL¦ C-Tick UL GOST CSA GL¦ CE CCC GL China RoHS UL RCM EAC CSA¦ CSA CCC RCM China RoHS CE GL UL EAC¦ CSA GL UL¦ CSA UL¦ USSR EDF ASE BV CSA¦ ASE EDF USSR BV CSA¦ CSA UL GOST¦ GOST CSA UL¦ CSA GOST UL¦ UL CSA GOST¦ GOST UL CSA¦ UL China RoHS CSA EAC REACH CE RoHS¦ UL Lloyd's RoHS CE CSA GOST REACH¦ RoHS CSA Lloyd's CE UL REACH GOST | CSA UL
| protection category | 1 | 1 | 1 | RT I | RT I | RT I
| protective treatment | 4 | 1 | 4 | TC TC TC TC | TC | TC
| relative humidity | 7 | 3 | 4 | 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 55 °C conforming to IEC 60068-2-30 95 % at 25…55 °C 95 % at 25…55 °C 10…85 % | 95 % at 55 °C conforming to IEC 60068-2-30¦ 95 % at 25…55 °C¦ 10…85 % | 95 % at 55 °C conforming to IEC 60068-2-30
| resistance to electrostatic discharge | 1 | 1 | 1 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3 | 6 kV (in contact) conforming to IEC 61000-4-2 level 3 8 kV (in air) conforming to IEC 61000-4-2 level 3
| resistance to fast transients | 1 | 1 | 1 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4 | 1 kV (on input-output) conforming to IEC 61000-4-4 2 kV (on power supply) conforming to IEC 61000-4-4
| shock resistance | 18 | 7 | 6 | 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn for 11 ms conforming to IEC 60255-21-1 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to IEC 60068-2-27 50 gn for 11 ms conforming to NF C 20-608 50 gn for 11 ms conforming to NF C 20-608 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27 20 gn in operation 100 gn not in operation 10 gn for in operation 30 gn for not operating 10 gn for in operation 30 gn for not operating | 15 gn for 11 ms conforming to IEC 60255-21-1¦ 15 gn not operating for 11 ms conforming to IEC 60068-2-27 5 gn in operation for 11 ms conforming to IEC 60068-2-27¦ 50 gn for 11 ms conforming to IEC 60068-2-27¦ 50 gn for 11 ms conforming to NF C 20-608¦ 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27¦ 20 gn in operation 100 gn not in operation¦ 10 gn for in operation 30 gn for not operating | 10 gn (duration = 11 ms) for not operating conforming to EN/IEC 60068-2-27 5 gn (duration = 11 ms) for in operation conforming to EN/IEC 60068-2-27
| standards | 20 | 11 | 3 | EN/IEC 60255-6 EN/IEC 60255-1 EN/IEC 60255-1 EN/IEC 60255-1 UL 508 IEC 61812-1 UL 508 IEC 61812-1 IEC 60584-1 IEC 60947-1 EN/IEC 60947-5-1 EN/IEC 60947-5-1 IEC 60255 NF C 45-250 VDE 0435 IEC 60255 NF C 45-250 VDE 0435 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 UL 508 CSA C22.2 No 14 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 UL 508 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 UL 508 IEC 61810-1 CSA C22.2 No 14 EN/IEC 61810-1 CSA C22.2 No 14 UL 508 CSA C22.2 No 14 UL 508 EN/IEC 61810-1 | EN/IEC 60255-6¦ EN/IEC 60255-1¦ UL 508 IEC 61812-1¦ IEC 60584-1 IEC 60947-1¦ EN/IEC 60947-5-1¦ IEC 60255 NF C 45-250 VDE 0435¦ CSA C22.2 No 14 UL 508 EN/IEC 61810-1¦ CSA C22.2 No 14 EN/IEC 61810-1 UL 508¦ UL 508 CSA C22.2 No 14 EN/IEC 61810-1¦ EN/IEC 61810-1 CSA C22.2 No 14 UL 508¦ UL 508 IEC 61810-1 CSA C22.2 No 14 | EN/IEC 60255-1
| vibration resistance | 18 | 7 | 6 | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | 0.35 mm (f= 5…57.6 Hz) conforming to IEC 60068-2-6 1 gn (f= 57.6…150 Hz) conforming to IEC 60255-21-1¦ 20 m/s² (f= 10…150 Hz) conforming to IEC 60068-2-6¦ 5 gn (f= 10…100 Hz) conforming to IEC 60068-2-6¦ 6 gn (f= 10…55 Hz) conforming to IEC 60068-2-6 6 gn (f= 10…55 Hz) conforming to NF C 20-616¦ +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6¦ 3 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)in operation 5 gn, amplitude = +/- 0.75 mm (f = 10…150 Hz)not in operation¦ 3 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles in operation 5 gn, amplitude = +/- 1 mm (f = 10…150 Hz)5 cycles not operating | +/- 1 mm (f= 10…55 Hz) conforming to EN/IEC 60068-2-6
Main | [Ithe] conventional enclosed thermal current | 10 | 6 | 4 | 1 A 40 °C 5 A 40 °C 16 A at -40…40 °C 16 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 8 A at -40…40 °C 12 A at -40…55 °C 6 A at -40…55 °C | 1 A 40 °C¦ 5 A 40 °C¦ 16 A at -40…40 °C¦ 8 A at -40…40 °C¦ 12 A at -40…55 °C¦ 6 A at -40…55 °C | 8 A at -40…40 °C
| [Uc] control circuit voltage | 10 | 8 | 2 | 24 V AC/DC 50/60 Hz 27 V AC/DC 50/60 Hz 220 V AC 60 V DC 230 V AC 6 V DC 240 V AC 220 V AC 24 V AC 50/60 Hz 24 V AC 50/60 Hz | 24 V AC/DC 50/60 Hz¦ 27 V AC/DC 50/60 Hz¦ 220 V AC¦ 60 V DC¦ 230 V AC¦ 6 V DC¦ 240 V AC¦ 24 V AC 50/60 Hz | 220 V AC
| [Us] rated supply voltage | 2 | 1 | 2 | <= 230 V <= 230 V | <= 230 V | <= 230 V
| analogue input type | 1 | 1 | 1 | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584 | Thermocouple 0...300 °C/32...572 °F thermocouple J conforming to IEC 60584
| analogue output type | 1 | 1 | 1 | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm | Current 0...20 mA <= 500 Ohm Current 4...20 mA <= 500 Ohm Voltage 0...10 V >= 100 kOhm
| beacon or indicator bank unit type | 2 | 1 | 2 | Base unit direct fixing Illuminated unit Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit | Base unit direct fixing Illuminated unit
| bulb type | 2 | 1 | 2 | Incandescent with BA 15d base Incandescent with BA 15d base | Incandescent with BA 15d base | Incandescent with BA 15d base
| coil interference suppression | 2 | 1 | 2 | With With | With | With
| component name | 2 | 1 | 2 | XVDLS XVDLS | XVDLS | XVDLS
| contact operation | 8 | 2 | 7 | Low level Standard Standard Standard Standard Standard Standard Standard | Low level¦ Standard | Standard
| contacts type and composition | 11 | 3 | 5 | 4 C/O 4 C/O 1 C/O 1 C/O 2 C/O 2 C/O 2 C/O 2 C/O 1 C/O 2 C/O 4 C/O | 4 C/O¦ 1 C/O¦ 2 C/O | 2 C/O
| control type | 5 | 3 | 2 | Selector switch Selector switch Without push-button Lockable test button Lockable test button | Selector switch¦ Without push-button¦ Lockable test button | Selector switch
| device short name | 13 | 5 | 6 | RE22 RE22 RHT RHT RSB RSB RSB RSB RSB RSB RXG RXM RXM | RE22¦ RHT¦ RSB¦ RXG¦ RXM | RSB
| discrete output type | 2 | 1 | 2 | Relay Relay | Relay | Relay
| light source | 2 | 2 | 1 | Bulb not included, clear Bulb not included, yellow | Bulb not included, clear¦ Bulb not included, yellow | Bulb not included, clear
| material | 2 | 1 | 2 | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit | Glass reinforced polyamide: base unit Polycarbonate: illuminated unit
| maximum power consumption in VA | 1 | 1 | 1 | 3 VA | 3 VA | 3 VA
| maximum power dissipation in W | 2 | 1 | 2 | 5 W 5 W | 5 W | 5 W
| measurement range | 4 | 3 | 2 | 2...20 A current 208...480 V voltage AC 208...480 V voltage AC 183...528 V AC | 2...20 A current¦ 208...480 V voltage AC¦ 183...528 V AC | 208...480 V voltage AC
| minimum switching current | 1 | 1 | 1 | 10 mA at 5 V DC | 10 mA at 5 V DC | 10 mA at 5 V DC
| mounting diameter | 2 | 1 | 2 | 45 mm 45 mm | 45 mm | 45 mm
| nominal output current | 2 | 1 | 2 | 8 A 8 A | 8 A | 8 A
| product or component type | 20 | 7 | 9 | Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular measurement and control relays Modular timing relay Modular timing relay Converter for thermocouples Complete miniature beacon Complete miniature beacon Plug-in relay Timing relay Timing relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay Plug-in relay | Modular measurement and control relays¦ Modular timing relay¦ Converter for thermocouples¦ Complete miniature beacon¦ Plug-in relay Timing relay¦ Timing relay Plug-in relay¦ Plug-in relay | Plug-in relay
| product specific application | 3 | 1 | 3 | For 3-phase supply For 3-phase supply For 3-phase supply | For 3-phase supply | For 3-phase supply
| range of product | 20 | 6 | 10 | Zelio Control Zelio Control Zelio Control Zelio Control Zelio Time Zelio Time Zelio Analog Harmony XVD Optimum Harmony XVD Optimum Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Zelio Relay Harmony Relay Zelio Relay Zelio Relay | Zelio Control¦ Zelio Time¦ Zelio Analog¦ Harmony XVD Optimum¦ Zelio Relay¦ Harmony Relay | Zelio Relay
| relay monitored parameters | 4 | 4 | 1 | Overcurrent detection Asymmetry Phase sequence Phase failure detection Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | Overcurrent detection¦ Asymmetry Phase sequence Phase failure detection¦ Undervoltage and overvoltage in window mode Asymmetry Phase sequence Phase failure detection¦ Phase sequence Asymmetry Undervoltage and overvoltage in window mode Phase failure detection | Overcurrent detection
| relay name | 4 | 4 | 1 | RM17JC RM17TA RM17TE RM10TE | RM17JC¦ RM17TA¦ RM17TE¦ RM10TE | RM17JC
| relay type | 4 | 2 | 3 | Current control relay Multifunction control relay Multifunction control relay Multifunction control relay | Current control relay¦ Multifunction control relay | Multifunction control relay
| series name | 9 | 2 | 7 | Interface relay Interface relay Interface relay Interface relay Interface relay Interface relay Interface relay Miniature Miniature | Interface relay¦ Miniature | Interface relay
| signalling type | 2 | 1 | 2 | Steady Steady | Steady | Steady
| status LED | 10 | 2 | 8 | With With Without Without Without Without Without Without Without Without | With¦ Without | Without
| switching capacity in VA | 4 | 1 | 4 | 1250 VA 1250 VA 1250 VA 1250 VA | 1250 VA | 1250 VA
| time delay | 4 | 2 | 3 | Without Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value Adjustable 0.1...10 s, +/- 10 % of the full scale value | Without¦ Adjustable 0.1...10 s, +/- 10 % of the full scale value | Adjustable 0.1...10 s, +/- 10 % of the full scale value
| time delay range | 2 | 2 | 1 | 15...300 s 0.2...3 s 1.5...30 s 0.2...3 s 15...300 s 1.5...30 s | 15...300 s 0.2...3 s 1.5...30 s¦ 0.2...3 s 15...300 s 1.5...30 s | 15...300 s 0.2...3 s 1.5...30 s
| time delay type | 2 | 1 | 2 | On-delay On-delay | On-delay | On-delay
| utilisation category | 1 | 1 | 1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1 | AC-12 conforming to IEC 60947-5-1 AC-13 conforming to IEC 60947-5-1 AC-14 conforming to IEC 60947-5-1 AC-15 conforming to IEC 60947-5-1 DC-12 conforming to IEC 60947-5-1 DC-13 conforming to IEC 60947-5-1 DC-14 conforming to IEC 60947-5-1
| utilisation coefficient | 2 | 1 | 2 | 20 % 20 % | 20 % | 20 %
Offer Sustainability | China RoHS Regulation | 16 | 1 | 16 | China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration China RoHS declaration | China RoHS declaration | China RoHS declaration
| Circularity Profile | 7 | 1 | 7 | End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information End of Life Information | End of Life Information | End of Life Information
| EU RoHS Directive | 16 | 1 | 16 | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration | Pro-active compliance (Product out of EU RoHS legal scope) EU RoHS Declaration
| Environmental Disclosure | 16 | 1 | 16 | Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile Product Environmental Profile | Product Environmental Profile | Product Environmental Profile
| Mercury free | 16 | 1 | 16 | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes | Yes | Yes
| REACh Regulation | 12 | 1 | 12 | REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration REACh Declaration | REACh Declaration | REACh Declaration
| REACh free of SVHC | 7 | 1 | 7 | Yes Yes Yes Yes Yes Yes Yes | Yes | Yes
| RoHS exemption information | 16 | 1 | 16 | Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes Yes | Yes | Yes
| Sustainable offer status | 16 | 1 | 16 | Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product Green Premium product | Green Premium product | Green Premium product
| Toxic heavy metal free | 7 | 1 | 7 | Yes Yes Yes Yes Yes Yes Yes | Yes | Yes
| WEEE | 13 | 1 | 13 | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins | The product must be disposed on European Union markets following specific waste collection and never end up in rubbish bins
Packing Units | Package 1 Weight | 19 | 13 | 5 | 120 g 89 g 89 g 0.114 kg 0.108 kg 0.101 kg 0.101 kg 0.100 kg 0.135 kg 0.136 kg 0.001 kg 0.001 kg 61 g 0.001 kg 0.001 kg 0.001 kg 20.200 g 0.035 kg 0.036 kg | 120 g¦ 89 g¦ 0.114 kg¦ 0.108 kg¦ 0.101 kg¦ 0.100 kg¦ 0.135 kg¦ 0.136 kg¦ 0.001 kg¦ 61 g¦ 20.200 g¦ 0.035 kg¦ 0.036 kg | 0.001 kg
| Package 2 Weight | 4 | 4 | 1 | 4.295 kg 4.685 kg 5.017 kg 1.23 kg | 4.295 kg¦ 4.685 kg¦ 5.017 kg¦ 1.23 kg | 4.295 kg
| Package 3 Weight | 1 | 1 | 1 | 7.876 kg | 7.876 kg | 7.876 kg